## Introduction
Cost-Effectiveness of ASHRAE Standard 90.1-2019 Compared to ASHRAE Standard 90.1-2016
The report providing documentation for this spreadsheet can be found at:
https://www.energycodes.gov/sites/default/files/documents/90.1-2019_National_Cost_Effectiveness.pdf
This workbook accompanies the report National Cost-Effectiveness of ANSI/ASHRAE/IES Standard 90.1-2019 available at the same location as this spreadsheet at the URL shown at the right. The report provides the full description of this project and the cost estimate methodology as well as additional details on the cost estimate items.
Pacific Northwest National Laboratory (PNNL) conducted this study in support of the U.S. Department of Energy (DOE) Building Energy Codes Program (BECP). BECP was founded in 1993 in response to the Energy Policy Act of 1992, which mandated that DOE participate in the development process for national model codes and that DOE help states adopt and implement progressive energy codes. DOE has supported the development and implementation of more stringent building energy codes since the 1970s, but the BECP was the first DOE program assigned with specific mandates in regard to energy codes.
Building energy codes set baseline minimum requirements for energy-efficient design and construction for new and renovated buildings, and impact energy use and emissions for the life of the buildings. Energy codes are part of the greater collection of regulations that govern the design, construction, and operation of buildings for the health and life safety of occupants. Improving these regulations generates consistent and long-lasting energy savings.
For this project, BECP directed PNNL to analyze the cost-effectiveness of the changes in Standard 90.1 from 90.1-2016 to 90.1-2019 (ANSI/ASHRAE/IESNA 2016, ANSI/ASHRAE/IESNA 2019) applied in the United States. The first task was to define the building elements that need to change for compliance with these two standards. The second task was to develop costs for the required changes in buildings. The third task was to analyze the cost-effectiveness of the changes. This workbook includes the descriptions of the cost items and the cost estimates.
Changes to Standard 90.1-2016 were implemented through addenda, and Standard 90.1-2019 is simply Standard 90.1-2016 with all approved addenda. Previous work by PNNL assessed the energy savings due to the addenda. The addenda are the cost estimate items in most cases and are listed with brief descriptions in the cost spreadsheets.
A suite of prototype building models were used to quantify the energy impacts of the addenda. The development of the prototype models and the energy savings analysis are documented in the quantitative analysis report completed as part of the DOE determination process. For this cost effectiveness project, PNNL used six prototype buildings and five climate locations. For comparison, the quantitative analysis used 16 prototypes and 17 climate locations. Cost estimate and cost effectiveness results are developed for all 30 combinations of the selected six prototypes and five climate locations:
Selected Prototypes Selected Climate Locations
Small Office 2A Tampa, FL
Large Office 3A Atlanta, GA
Standalone Retail 3B El Paso, TX
Primary School 4A New York, NY
Small Hotel 5A Buffalo, NY
Mid-rise Apartment
This cost estimate spreadsheet is organized in sections, some with multiple worksheets, with each section or sub-section highlighted with a different colored tab:
1) Introduction (white)
2) HVAC (blue)
3) Lighting (red)
4) Envelope, Power, and Other (orange)
5) Cost Estimate Summaries (olive)
Within the three cost estimate sections, there are several types of cost worksheets. Component costs (labeled with “comp” in the worksheet name) are the individual cost items not assigned to the particular prototype, such as the cost for a 33 W linear LED lamp and fixture. Prototype costs (labeled with “proto” in the worksheet name) are the assignment of component costs to the applicable prototypes and climate zones. For HVAC costs, there is one cost worksheet for each prototype. The Interior Lighting LPD section includes an additional worksheet that assigns costs by lighting space types and these are then assigned to the prototypes. The Envelope, Power and Other workhseet combines component and prototype costs. Summary results for new construction, maintenance and replacement over 40 years are shown for each prototype and climate zone in the Summary worksheets.
There is also a Cost Estimate Summary sheet. It has costs with replacements for 29 years with the residual value of items with useful lives that extend beyond 30 years shown in year 30. It also shows a scenario that extends the replacements for 39 years and includes residual values in year 40. Residual values are discussed in Section 5.1.1 of the main report.
The cost estimates include material, labor, construction equipment, incremental commissioning and maintenance where significant, and overhead and profit (OH&P). These costs were estimated for both the initial project, and for replacement, which required defining the useful life of the cost items before replacement.
A variety of sources were used to produce the cost estimate and are identified in the various worksheets. For mechanical costs, two consulting firms were used for prior versions of this study, Faithful+Gould a cost estimating firm, and Solarc a mechanical, electrical and plumbing engineering consulting firm. For lighting costs and a couple of mechanical items, PNNL in house expertise was applied supported by online resources. Any older costs were adjusted for inflation.
Several general parameters apply to all of the cost estimates as shown in the worksheet General Cost Parameters. These items include overhead and profit, identified separately for first cost, and for replacement costs. Also included is a general method for adjusting labor costs for replacement. Finally, costs for small tools, and general construction equipment are included.

## MechFormulaDoc (hidden)
Generally, data is found from 5 climate zones, based on capacity [col I & J from HVAC_Data]
and then interpolated from standard costs [HVAC Costs Comp] to find relevant cost for prototype
Example from small office
The following is done for each of up to 5 climte zones
Cell K 13 as an example
|  | Formula: | =IF(CZ_1=0,0,IF(OR(INDIRECT("$"&K$4&ROW(K13))>=MAX(INDIRECT($C13&K$5)),(INDIRECT("$"&K$4&ROW(K13))<MIN(INDIRECT($C13&K$5)))),"OUT OF RANGE",INDEX(INDIRECT($C13&K$6),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1),K$7)+(INDEX(INDIRECT($C13&K$6),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1)+1,K$7)-INDEX(INDIRECT($C13&K$6),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1),K$7))*(INDIRECT("$"&K$4&ROW(K13))-INDEX(INDIRECT($C13&K$5),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1)))/(INDEX(INDIRECT($C13&K$5),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1)+1)-INDEX(INDIRECT($C13&K$5),MATCH(INDIRECT("$"&K$4&ROW(K13)),INDIRECT($C13&K$5),1)))))
0 if current CZ inactive |  | Breakdown: | =IF(CZ_1=0,0,
Test for interpolation out of range |  |  | ,IF(OR(INDIRECT("$"&K$4&ROW(K13))>=MAX(INDIRECT($C13&K$5)),(INDIRECT("$"&K$4&ROW(K13))<MIN(INDIRECT($C13&K$5)))),"OUT OF RANGE", | compare current row, col I (ref from row4) to interpolation range, a named range formed from col C and row 5 "Heat_Pump_2007Par"
|  |  | INDEX(INDIRECT($C13&K$6), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1),K$7) +(INDEX(INDIRECT($C13&K$6), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1)+1,K$7) -INDEX(INDIRECT($C13&K$6), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1),K$7)) *(INDIRECT("$"&K$4&ROW(K13)) -INDEX(INDIRECT($C13&K$5), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1))) /(INDEX(INDIRECT($C13&K$5), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1)+1) -INDEX(INDIRECT($C13&K$5), MATCH(INDIRECT("$"&K$4&ROW(K13)), INDIRECT($C13&K$5),1))))) | this is an interpolation formula, given the size parameters in column "I" will look up the cost on HVAC comp using the KEY_2007_Par & KEY_2007Costs names on [HVAC Costs Comp], where KEY is the technology word in col C As long as the formula is relatively copied, it will work, if things are properly named on [HVAC Costs Comp] Name setup required for formula to reference: Key Equip Type name part in Col C System name/parameter in Col G Ref column for case size parameter in row 4 parameter name part in row 5 cost name part in row 6 Col A needs an x for items to be counted in summaries below Spot checking is best performed by manually reproducing the interpolation
Note:
Cost cells referred to in HVAC Costs Comp have the form:
XXX_2007_Costs
where:
|  |  | XXX | is the equipment type, and
|  |  | _2007_Costs | is a range that includes cost information for the base case that can be looked up
|  |  | XXX_2007_par | refers to the parameters related to the cost rows
The above are referenced for interpolation; Par = x; Costs = y
For now - leaving 2007 as reference to base and 2010 as reference to target; as changing all those names is problematic. These are internal name references; and the reference rows will be hidden in the public copy.

## HVAC Methodology
90.1 Cost Effectiveness - HVAC Cost Methodology
Mid Rise Apartment Split system cost vs. capacity
The regressions for bare costs + 10% (subcontractor cost level) are:
|  |  | material | labor
|  | C | 2690.6 | 2202.7
|  | x | -208.45 | -73.657
|  | x^2 | 17.693 | 6.1014
The costs above, developed in 2012, are updated with labor and
material inflation multipliers applied at the prototype cost level.
An incremental cost was determined for changes in required apartment system capacity. Individual unit capacities from the prototype model were evaluated for a cost for both the baseline and target runs. The difference represented the cost change. Individual unit costs were based on data from RS Means Mechanical Cost Data, 2012 for split -system air cooled air conditioners with a DX evaporator cooling coil in a heating and cooling unit with ducted supply air. (Means D3050 165). Data from several typical applications were tabulated to arrive at material and labor costs in terms of $ per ton of cooling. Outliers were removed and a curve fit developed.
There are 14 addenda to 90.1-2016 with analyzed energy savings that affected the HVAC requirements in chapter 6 of 90.1.
Explanation of how these addenda are applied to the cost estimates is provided in the cost descriptions in the mechanical component and prototype worksheets and are not covered in this methodology narrative.
Note that the Mid-rise Apartment prototype has less extensive incremental mechanical costs and a simplified method is used to determine those costs based on simulated equipment capacities. Detail is shown at right.
The topic that is highlighted here is the costs developed to address changes in HVAC system and plant capacity between the 90.1-2016 and 90.1-2019 prototype models. The changes are due to changes in cooling and heating loads primarily because of changes in the interior lighting power allowance.
The HVAC capacity changes are a large part of the mechanical cost estimates. The costs were estimated for a range of equipment sizes corresponding to the models. The cost estimate sheet is laid out with 90.1-2016 and 90.1-2019 descriptions together for ease of comparison, followed by the related costs in adjacent sections. The costs in these two parts are the same when estimated as components with the exception of the ductwork and piping costs. Ductwork and piping cost results are presented in the HVAC cost component worksheet and the same costs are presented in the prototype specific cost worksheets. For the other capacity related inputs, the component costs are mapped to the prototype model information in the prototype worksheets.
The capacity related costs are organized with other related addenda in two sections, the upper portion for HVAC system related costs such as packaged variable air volume rooftop units and ductwork, and HVAC plant related costs such as chillers and piping.
In general, two manufacturers' equipment selections are included along with an average of the prototype costs, which is what is used for the cost estimate. RS Means Mechanical Cost Data costs for 2012 or 2014 are also included for comparison. The RS Means 2020 labor estimate is used for all cases. The material costs are usually similar to the costs used for the estimate except the material costs for air handling units (AHUs), both variable air volume and constant air volume units. The RS Means AHU equipment costs are substantially higher but it is not known what these costs include. Review of the air handler unit costs by Faithful+Gould, the primary mechanical cost estimator, with the suppliers who provided these costs, determined that the costs fit the equipment descriptions provided by PNNL including costs for the cabinet, fan, and cooling and heating coils. The lower costs from the consultant and suppliers is used. Note that where material costs were developed in prior years, they have been updated to 2020 using inflation factors specific to the equipment type that are based on a comparison of material costs in the RS Means 2012, 2014, and 2020 cost handbooks.
The costs are assigned to the prototypes using formulas that extract the corresponding component costs to the model capacity inputs and outputs as appropriate. A few cost items are simply pasted into the component costs such as the ductwork and piping costs, which were developed specifically for a given prototype and climate. The formulas are complex and include interpolation between the component cost values for selected capacities. The formulas are converted to values in this version of the spreadsheet. This method is believed to provide representative costs for the category of buildings for each prototype, at least those with some similarity in building size, shape and HVAC system type, rather than just the specific inputs and output capacities of these prototype models.
Generally, there was a decrease in costs due to a decrease in capacity and airflow for mechanical equipment, thus offsetting increased costs from addenda that added costs.
Piping and Ductwork Costs
Piping and ductwork costs (and some controls costs) were developed by Solarc, an integrated architectural, mechanical, electrical and plumbing design consultant, who specialize in green buildings. This effort includes developing schematic level single line representative layout of the ductwork and piping for each prototype. Detailed costs for these at the level of duct and pipe size and length, and all fittings were developed based on the component by component costs from RS Means 2012. In some cases, the multiple costs are used to develop regressions for material and labor costs as a function of unit capacity or transfer fluid flow. Where these costs were developed in 2012, they have been updated to 2020 using inflation factors specific to the equipment type that are based on a comparison of material costs in the RS Means 2012 and 2020 cost handbooks. Acquiring these costs from individual suppliers was cost prohibitive for the project budget and would diverge greatly between suppliers according to Solarc. Solarc identified that for some prototypes and climates, the differences in capacity were so close that there were very limited cost differences and separate costs were not developed. This is why some of these costs are identical to each other between climate zones for a given prototype.

## HVAC Costs Comp
[16 empty] | 90.1 Cost Effectiveness - HVAC Costs by Component |  |  |  |  | Hide | [10 empty] | Find Rows
Incremental Costs for verification only
[16 empty] | Hide rows colored orange | Range name extensions | _2007Par | _2007Costs | _2010Par | _2010Costs | [13 empty] | 3 | [6 empty] | 10 | [31 empty] | incremental costs are captured in total cost calculations
Not used - retain to avoid disrupting other | [15 empty] | Item and Addenda | Base Code | [5 empty] | Target Code | [10 empty] | Base Code - costs (no costs if just an added item in Target Code ) | [19 empty] | Target Code - costs with added or changed code provisions (or see description if costs are just tied to change in capacity). | [19 empty] | Incremental Costs
cell references | [28 empty] | Other Parameters |  |  |  |  | New Constrution | [7 empty] | Maintenance | Replacement | [10 empty] | New Construction | [8 empty] | Maintenance | Replacement
[17 empty] | Description | Source of Information | Manufacturer | Model and Series | Series | 90.1-2016 Cost Parameter | Description | Source of Information (RS Means Mechanical Cost Data 2014 used for labor unless stated) | Manufacturer | Model and Series | Not Used | 90.1-2019 Cost Parameter | Appropriate Other Parameters |  |  |  | 2012 to 2020 Material inflation adjustment | Material Subtotal | Labor Crew Type | Labor ($/Hr) | Labor (Hours) | Labor Subtotal | Construction Equipment | Cost Adjustments (OH&P, G-C, GC, infl., contingency etc.) | Total | Annual | Replacement Life (years) | Not Used | Material Subtotal | Labor Crew Type | Labor ($/Hr) | Labor (Hours) | Labor Subtotal | Construction Equipment | Cost Adjustments (OH&P, G-C, GC, contingency etc.) | Total | Not Used | Material Subtotal | Labor Crew Type | Labor ($/Hr) | Labor (Hours) | Labor Subtotal | Construction Equipment | Cost Adjustments (OH&P, G-C, GC, cont'gcy., infl. etc.) |  | Total Cost | Annual | Replacement Life (years) | Not Used | Material Subtotal | Labor Crew Type | Labor ($/Hr) | Labor (Hours) | Labor Subtotal | Construction Equipment | Cost Adjustments (OH&P, G-C, GC, contingency etc.) | Total Cost | New Construction 2019 minus 2016
[16 empty] | HVAC System Costs Associated with Capacity Changes | Costs used to account for changes in system capacity due to other changes in 90.1, primarily lighting. Costs are base costs for system that meets 90.1 standard requirements before application of addenda. This cost is without an economizer or ERV as they are not always required. Systems have DDC control. These costs are current or have been adjusted for inflation to current prices. | Costs developed in 2012 are updated with inflation factors based on Means to bring them forward. |  |  |  |  | Costs shown are the same for base code and target code. Difference in cost for capacity between base and target models is without any of the addenda changes. Difference in cost by capacity will be calculated in final summary sheet based on the base and target capacity for a particular system in a prototype and climate zone.
[16 empty] | VAV Air Handling Units | VAV air handling units with chilled and hot water coils, built-up, or rooftop as available, based on supply airflow. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. VFD used to provide variable airflow. This cost is without an economizer or ERV as they are not always required. Coils selected in mid-range of coil sizes for unit sized based on supply airflow. | Equipment information below. Labor hours from RS Means 2020 Mechanical Cost Data. Packaged, Outdoor Type, Central-Station AHU, 23 74 13.10 |  |  |  | Supply Airflow, cfm | Same as for base code for same size units. |  |  |  |  | Supply Airflow, cfm |  |  |  |  | Inflation from 2012 to 2020
[17 empty] | Manufacturer 1 | Faithful+Gould - Carrier | Carrier | 39 M |  | 16000 | [5 empty] | 16000 |  |  |  |  | 1.122 | 20250 | Q-6 | 61.19 | 64.5518 | 3949.9246 |  | 17217.2094 | 41417.1341 |  | 15 |  | 20250 | Q-6 | 61.19 | 106.5105 | 6517.3757 |  | 23875.6679 | 50643.0436 |  | 20250 | Q-6 | 61.19 | 64.5518 | 3949.9246 |  | 17217.2094 |  | 41417.1341 |  | 15 |  | 20250 | Q-6 | 61.19 | 106.5105 | 6517.3757 |  | 23875.6679 | 50643.0436 | 0
[18 empty] | Airtech Thermex | Carrier | 39 M |  | 20000 | [5 empty] | 20000 |  |  |  |  | 1.122 | 21600 | Q-6 | 61.19 | 82.759 | 5064.0232 |  | 19186.4319 | 45850.4551 |  | 15 |  | 21600 | Q-6 | 61.19 | 136.5523 | 8355.6383 |  | 26998.0846 | 56953.7229 |  | 21600 | Q-6 | 61.19 | 82.759 | 5064.0232 |  | 19186.4319 |  | 45850.4551 |  | 15 |  | 21600 | Q-6 | 61.19 | 136.5523 | 8355.6383 |  | 26998.0846 | 56953.7229 | 0
[18 empty] | Airtech Thermex, Minneapolis MN | Carrier | 39 M |  | 25000 | [5 empty] | 25000 |  |  |  |  | 1.122 | 27000 | Q-6 | 61.19 | 101.3795 | 6203.4116 |  | 23860.7923 | 57064.2039 |  | 15 |  | 27000 | Q-6 | 61.19 | 167.2762 | 10235.6291 |  | 33519.7958 | 70755.4249 |  | 27000 | Q-6 | 61.19 | 101.3795 | 6203.4116 |  | 23860.7923 |  | 57064.2039 |  | 15 |  | 27000 | Q-6 | 61.19 | 167.2762 | 10235.6291 |  | 33519.7958 | 70755.4249 | 0
[19 empty] | Carrier | 39 M |  | 30000 | [5 empty] | 30000 |  |  |  |  | 1.122 | 32400 | Q-6 | 61.19 | 120 | 7342.8 |  | 28535.1526 | 68277.9526 |  | 15 |  | 32400 | Q-6 | 61.19 | 198 | 12115.62 |  | 40041.5069 | 84557.1269 |  | 32400 | Q-6 | 61.19 | 120 | 7342.8 |  | 28535.1526 |  | 68277.9526 |  | 15 |  | 32400 | Q-6 | 61.19 | 198 | 12115.62 |  | 40041.5069 | 84557.1269 | 0
[19 empty] | Carrier | 39 M |  | 40000 | [5 empty] | 40000 |  |  |  |  | 1.122 | 40500 | Q-6 | 61.19 | 157.241 | 9621.5768 |  | 36096.7261 | 86218.3029 |  | 15 |  | 40500 | Q-6 | 61.19 | 259.4477 | 15875.6017 |  | 50849.0672 | 107224.6689 |  | 40500 | Q-6 | 61.19 | 157.241 | 9621.5768 |  | 36096.7261 |  | 86218.3029 |  | 15 |  | 40500 | Q-6 | 61.19 | 259.4477 | 15875.6017 |  | 50849.0672 | 107224.6689 | 0
[19 empty] | extrapolated |  |  | 50000 | [5 empty] | 50000 |  |  |  |  | 1.122 | 48600 | Q-6 | 61.19 | 194.482 | 11900.3536 |  | 43658.2996 | 104158.6532 |  | 15 |  | 48600 | Q-6 | 61.19 | 320.8953 | 19635.5834 |  | 61656.6275 | 129892.211 |  | 48600 | Q-6 | 61.19 | 194.482 | 11900.3536 |  | 43658.2996 |  | 104158.6532 |  | 15 |  | 48600 | Q-6 | 61.19 | 320.8953 | 19635.5834 |  | 61656.6275 | 129892.211 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould - Trane price estimates for range of sizes | Trane | Performance Climate Changer |  | 16000 | [5 empty] | 16000 | 562.5 | 40 |  |  | 1.122 | 22500 | Q-6 | 61.19 | 64.5518 | 3949.9246 |  | 18706.4988 | 45156.4235 |  | 15 |  | 22500 | Q-6 | 61.19 | 106.5105 | 6517.3757 |  | 25738.8862 | 54756.2619 |  | 22500 | Q-6 | 61.19 | 64.5518 | 3949.9246 |  | 18706.4988 |  | 45156.4235 |  | 15 |  | 22500 | Q-6 | 61.19 | 106.5105 | 6517.3757 |  | 25738.8862 | 54756.2619 | 0
[18 empty] | Minneapolis MN | Trane | Performance Climate Changer |  | 20000 | [5 empty] | 20000 | 480 | 50 |  |  | 1.122 | 24000 | Q-6 | 61.19 | 82.759 | 5064.0232 |  | 20775.0072 | 49839.0305 |  | 15 |  | 24000 | Q-6 | 61.19 | 136.5523 | 8355.6383 |  | 28985.5175 | 61341.1558 |  | 24000 | Q-6 | 61.19 | 82.759 | 5064.0232 |  | 20775.0072 |  | 49839.0305 |  | 15 |  | 24000 | Q-6 | 61.19 | 136.5523 | 8355.6383 |  | 28985.5175 | 61341.1558 | 0
[19 empty] | Trane | Performance Climate Changer |  | 25000 | [5 empty] | 25000 | 480 | 62.5 |  |  | 1.122 | 30000 | Q-6 | 61.19 | 101.3795 | 6203.4116 |  | 25846.5115 | 62049.9231 |  | 15 |  | 30000 | Q-6 | 61.19 | 167.2762 | 10235.6291 |  | 36004.0869 | 76239.716 |  | 30000 | Q-6 | 61.19 | 101.3795 | 6203.4116 |  | 25846.5115 |  | 62049.9231 |  | 15 |  | 30000 | Q-6 | 61.19 | 167.2762 | 10235.6291 |  | 36004.0869 | 76239.716 | 0
[19 empty] | Trane | Performance Climate Changer |  | 30000 | [5 empty] | 30000 | 480 | 65 |  |  | 1.122 | 31200 | Q-6 | 61.19 | 120 | 7342.8 |  | 27740.865 | 66283.665 |  | 15 |  | 31200 | Q-6 | 61.19 | 198 | 12115.62 |  | 39047.7905 | 82363.4105 |  | 31200 | Q-6 | 61.19 | 120 | 7342.8 |  | 27740.865 |  | 66283.665 |  | 15 |  | 31200 | Q-6 | 61.19 | 198 | 12115.62 |  | 39047.7905 | 82363.4105 | 0
[19 empty] | Trane | Performance Climate Changer |  | 40000 | [5 empty] | 40000 | 450 | 97.5 |  |  | 1.122 | 43875 | Q-6 | 61.19 | 157.241 | 9621.5768 |  | 38330.6602 | 91827.237 |  | 15 |  | 43875 | Q-6 | 61.19 | 259.4477 | 15875.6017 |  | 53643.8947 | 113394.4964 |  | 43875 | Q-6 | 61.19 | 157.241 | 9621.5768 |  | 38330.6602 |  | 91827.237 |  | 15 |  | 43875 | Q-6 | 61.19 | 259.4477 | 15875.6017 |  | 53643.8947 | 113394.4964 | 0
[19 empty] | extrapolated |  |  | 50000 | [5 empty] | 50000 | 450 | 105 |  |  | 1.122 | 56550 | Q-6 | 61.19 | 194.482 | 11900.3536 |  | 48920.4555 | 117370.8091 |  | 15 |  | 56550 | Q-6 | 61.19 | 320.8953 | 19635.5834 |  | 68239.999 | 144425.5824 |  | 56550 | Q-6 | 61.19 | 194.482 | 11900.3536 |  | 48920.4555 |  | 117370.8091 |  | 15 |  | 56550 | Q-6 | 61.19 | 320.8953 | 19635.5834 |  | 68239.999 | 144425.5824 | 0
[16 empty] | VAV_AHU | Average of two manufacturers | [15 empty] | 1.122 | [6 empty] | 0 | [10 empty] | 0 | [8 empty] | 0
[18 empty] | Faithful+Gould |  |  |  | 16000 | [5 empty] | 16000 |  |  |  |  | 1.122 | 21375 | Q-6 | 61.19 | 64.5518 | 3949.9246 |  | 17961.8541 | 43286.7788 |  | 15 |  | 21375 | Q-6 | 61.19 | 106.5105 | 6517.3757 |  | 24807.2771 | 52699.6527 |  | 21375 | Q-6 | 61.19 | 64.5518 | 3949.9246 |  | 17961.8541 |  | 43286.7788 |  | 15 |  | 21375 | Q-6 | 61.19 | 106.5105 | 6517.3757 |  | 24807.2771 | 52699.6527 | 0
[16 empty] | used for load changes | [5 empty] | 20000 | [5 empty] | 20000 |  |  |  |  | 1.122 | 22800 | Q-6 | 61.19 | 82.759 | 5064.0232 |  | 19980.7196 | 47844.7428 |  | 15 |  | 22800 | Q-6 | 61.19 | 136.5523 | 8355.6383 |  | 27991.801 | 59147.4393 |  | 22800 | Q7 | 61.19 | 82.759 | 5064.0232 |  | 19980.7196 |  | 47844.7428 |  | 15 |  | 22800 | Q-6 | 61.19 | 136.5523 | 8355.6383 |  | 27991.801 | 59147.4393 | 0
[22 empty] | 25000 | [5 empty] | 25000 |  |  |  |  | 1.122 | 28500 | Q-6 | 61.19 | 101.3795 | 6203.4116 |  | 24853.6519 | 59557.0635 |  | 15 |  | 28500 | Q-6 | 61.19 | 167.2762 | 10235.6291 |  | 34761.9413 | 73497.5705 |  | 28500 | Q7 | 61.19 | 101.3795 | 6203.4116 |  | 24853.6519 |  | 59557.0635 |  | 15 |  | 28500 | Q-6 | 61.19 | 167.2762 | 10235.6291 |  | 34761.9413 | 73497.5705 | 0
[22 empty] | 30000 | [5 empty] | 30000 |  |  |  |  | 1.122 | 31800 | Q-6 | 61.19 | 120 | 7342.8 |  | 28138.0088 | 67280.8088 |  | 15 |  | 31800 | Q-6 | 61.19 | 198 | 12115.62 |  | 39544.6487 | 83460.2687 |  | 31800 | Q7 | 61.19 | 120 | 7342.8 |  | 28138.0088 |  | 67280.8088 |  | 15 |  | 31800 | Q-6 | 61.19 | 198 | 12115.62 |  | 39544.6487 | 83460.2687 | 0
[22 empty] | 40000 | [5 empty] | 40000 |  |  |  |  | 1.122 | 42187.5 | Q-6 | 61.19 | 157.241 | 9621.5768 |  | 37213.6932 | 89022.77 |  | 15 |  | 42187.5 | Q-6 | 61.19 | 259.4477 | 15875.6017 |  | 52246.481 | 110309.5827 |  | 42187.5 | Q7 | 61.19 | 157.241 | 9621.5768 |  | 37213.6932 |  | 89022.77 |  | 15 |  | 42187.5 | Q-6 | 61.19 | 259.4477 | 15875.6017 |  | 52246.481 | 110309.5827 | 0
[22 empty] | 50000 | [5 empty] | 50000 |  |  |  |  | 1.122 | 52575 | Q-6 | 61.19 | 194.482 | 11900.3536 |  | 46289.3776 | 110764.7311 |  | 15 |  | 52575 | Q-6 | 61.19 | 320.8953 | 19635.5834 |  | 64948.3133 | 137158.8967 |  | 52575 | Q7 | 61.19 | 194.482 | 11900.3536 |  | 46289.3776 |  | 110764.7311 |  | 15 |  | 52575 | Q-6 | 61.19 | 320.8953 | 19635.5834 |  | 64948.3133 | 137158.8967 | 0
1.122
[16 empty] | CAV Air Handling Units | CAV air handling units with chilled and hot water coils, built-up, or rooftop as available based on supply airflow. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. This cost is without an economizer or ERV as they are not always required. Coils selected in mid-range of coil sizes for unit sized based on supply airflow. Duct work, diffusers etc. not included. | Equipment information below. Labor hours from RS Means 2020 Mechanical Cost Data. Packaged, Outdoor Type, Central-Station AHU, 23 74 13.10 31XX |  |  |  | Supply Airflow, cfm | Same as for base code for same size units. |  |  |  |  | Supply Airflow, cfm |  |  |  |  | Inflation from 2012 to 2020
[17 empty] | Manufacturer 1 | Faithful+Gould | Carrier | 39 L |  | 400 | [5 empty] | 1650 |  |  |  |  | 1.146 | 3060 | Q6 | 61.19 | 23.2547 | 1422.9571 |  | 3508.0609 | 7991.0181 |  | 15 |  | 3060 | Q6 | 61.19 | 38.3703 | 2347.8793 |  | 5213.8181 | 10621.6974 |  | 3060 | Q6 | 61.19 | 23.2547 | 1422.9571 |  | 3508.0609 |  | 7991.0181 |  | 15 |  | 3060 | Q6 | 61.19 | 38.3703 | 2347.8793 |  | 5213.8181 | 10621.6974 | 0
[18 empty] | Airtech Thermex |  | 39 L |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1.146 | 9000 | Q6 | 61.19 | 24 | 1468.56 |  | 7694.9739 | 18163.5339 |  | 15 |  | 9000 | Q6 | 61.19 | 39.6 | 2423.124 |  | 10447.039 | 21870.163 |  | 9000 | Q6 | 61.19 | 24 | 1468.56 |  | 7694.9739 |  | 18163.5339 |  | 15 |  | 9000 | Q6 | 61.19 | 39.6 | 2423.124 |  | 10447.039 | 21870.163 | 0
[18 empty] | Minneapolis MN |  | 39 L |  | 4000 | [5 empty] | 4000 |  |  |  |  | 1.146 | 10350 | Q6 | 61.19 | 28.2587 | 1729.1478 |  | 8888.1328 | 20967.2806 |  | 15 |  | 10350 | Q6 | 61.19 | 46.6268 | 2853.0939 |  | 12086.6095 | 25289.7034 |  | 10350 | Q6 | 61.19 | 28.2587 | 1729.1478 |  | 8888.1328 |  | 20967.2806 |  | 15 |  | 10350 | Q6 | 61.19 | 46.6268 | 2853.0939 |  | 12086.6095 | 25289.7034 | 0
[18 empty] | Carrier |  | 39 L |  | 8000 | [5 empty] | 8000 |  |  |  |  | 1.146 | 13050 | Q6 | 61.19 | 39.8476 | 2438.2746 |  | 11455.9153 | 26944.1899 |  | 15 |  | 13050 | Q6 | 61.19 | 65.7485 | 4023.1532 |  | 15703.9122 | 32777.0653 |  | 13050 | Q6 | 61.19 | 39.8476 | 2438.2746 |  | 11455.9153 |  | 26944.1899 |  | 15 |  | 13050 | Q6 | 61.19 | 65.7485 | 4023.1532 |  | 15703.9122 | 32777.0653 | 0
[20 empty] | 39 M |  | 16000 | [5 empty] | 16000 |  |  |  |  | 1.146 | 18900 | Q6 | 61.19 | 62.8296 | 3844.5432 |  | 16893.7636 | 39638.3069 |  | 15 |  | 18900 | Q6 | 61.19 | 103.6688 | 6343.4963 |  | 23307.1942 | 48550.6906 |  | 18900 | Q6 | 61.19 | 62.8296 | 3844.5432 |  | 16893.7636 |  | 39638.3069 |  | 15 |  | 18900 | Q6 | 61.19 | 103.6688 | 6343.4963 |  | 23307.1942 | 48550.6906 | 0
[20 empty] | 39 M |  | 20000 | [5 empty] | 20000 |  |  |  |  | 1.146 | 20700 | Q6 | 61.19 | 80 | 4895.2 |  | 19163.5795 | 44758.7795 |  | 15 |  | 20700 | Q6 | 61.19 | 132 | 8077.08 |  | 26758.4968 | 55535.5768 |  | 20700 | Q6 | 61.19 | 80 | 4895.2 |  | 19163.5795 |  | 44758.7795 |  | 15 |  | 20700 | Q6 | 61.19 | 132 | 8077.08 |  | 26758.4968 | 55535.5768 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould | Trane | Performance |  | 1650 | [5 empty] | 1650 |  | 1650 |  |  | 1.146 | 3400 | Q6 | 61.19 | 23.2547 | 1422.9571 |  | 3745.1957 | 8568.1528 |  | 15 |  | 3400 | Q6 | 61.19 | 38.3703 | 2347.8793 |  | 5508.6664 | 11256.5456 |  | 3400 | Q6 | 61.19 | 23.2547 | 1422.9571 |  | 3745.1957 |  | 8568.1528 |  | 15 |  | 3400 | Q6 | 61.19 | 38.3703 | 2347.8793 |  | 5508.6664 | 11256.5456 | 0
[18 empty] | Trane Corp. |  | Performance |  | 2000 | [5 empty] | 2000 |  | 0 |  |  | 1.146 | 10000 | Q6 | 61.19 | 24 | 1468.56 |  | 8392.4291 | 19860.9891 |  | 15 |  | 10000 | Q6 | 61.19 | 39.6 | 2423.124 |  | 11314.2398 | 23737.3638 |  | 10000 | Q6 | 61.19 | 24 | 1468.56 |  | 8392.4291 |  | 19860.9891 |  | 15 |  | 10000 | Q6 | 61.19 | 39.6 | 2423.124 |  | 11314.2398 | 23737.3638 | 0
[18 empty] | Minneapolis MN |  | Performance |  | 4000 | [5 empty] | 4000 |  | 0 |  |  | 1.146 | 11500 | Q6 | 61.19 | 28.2587 | 1729.1478 |  | 9690.2063 | 22919.3541 |  | 15 |  | 11500 | Q6 | 61.19 | 46.6268 | 2853.0939 |  | 13083.8903 | 27436.9842 |  | 11500 | Q6 | 61.19 | 28.2587 | 1729.1478 |  | 9690.2063 |  | 22919.3541 |  | 15 |  | 11500 | Q6 | 61.19 | 46.6268 | 2853.0939 |  | 13083.8903 | 27436.9842 | 0
[22 empty] | 8000 | [5 empty] | 8000 |  | 0 |  |  | 1.146 | 14500 | Q6 | 61.19 | 39.8476 | 2438.2746 |  | 12467.2253 | 29405.5 |  | 15 |  | 14500 | Q6 | 61.19 | 65.7485 | 4023.1532 |  | 16961.3532 | 35484.5064 |  | 14500 | Q6 | 61.19 | 39.8476 | 2438.2746 |  | 12467.2253 |  | 29405.5 |  | 15 |  | 14500 | Q6 | 61.19 | 65.7485 | 4023.1532 |  | 16961.3532 | 35484.5064 | 0
[20 empty] | Performance |  | 16000 | [5 empty] | 16000 |  | 0 |  |  | 1.146 | 21000 | Q6 | 61.19 | 62.8296 | 3844.5432 |  | 18358.4195 | 43202.9628 |  | 15 |  | 21000 | Q6 | 61.19 | 103.6688 | 6343.4963 |  | 25128.3158 | 52471.8121 |  | 21000 | Q6 | 61.19 | 62.8296 | 3844.5432 |  | 18358.4195 |  | 43202.9628 |  | 15 |  | 21000 | Q6 | 61.19 | 103.6688 | 6343.4963 |  | 25128.3158 | 52471.8121 | 0
[20 empty] | Performance |  | 20000 | [5 empty] | 20000 |  | 20000 |  |  | 1.146 | 20700 | Q6 | 61.19 | 80 | 4895.2 |  | 19163.5795 | 44758.7795 |  | 15 |  | 20700 | Q6 | 61.19 | 132 | 8077.08 |  | 26758.4968 | 55535.5768 |  | 20700 | Q6 | 61.19 | 80 | 4895.2 |  | 19163.5795 |  | 44758.7795 |  | 15 |  | 20700 | Q6 | 61.19 | 132 | 8077.08 |  | 26758.4968 | 55535.5768 | 0
[16 empty] | CAV_AHU | Average of two manufacturers | [15 empty] | 1.146 | [6 empty] | 0 | [10 empty] | 0 | [8 empty] | 0
[22 empty] | 400 | [5 empty] | 1650 |  |  |  |  | 1.146 | 3230 | Q6 | 61.19 | 23.2547 | 1422.9571 |  | 3626.6283 | 8279.5855 |  | 15 |  | 3230 | Q6 | 61.19 | 38.3703 | 2347.8793 |  | 5361.2422 | 10939.1215 |  | 3230 | Q6 | 61.19 | 23.2547 | 1422.9571 |  | 3626.6283 |  | 8279.5855 | 0 | 15 |  | 3230 | Q6 | 61.19 | 38.3703 | 2347.8793 |  | 5361.2422 | 10939.1215 | 0
[16 empty] | used for load changes | [5 empty] | 2000 | [5 empty] | 2000 |  |  |  |  | 1.146 | 9500 | Q6 | 61.19 | 24 | 1468.56 |  | 8043.7015 | 19012.2615 |  | 15 |  | 9500 | Q6 | 61.19 | 39.6 | 2423.124 |  | 10880.6394 | 22803.7634 |  | 9500 | Q6 | 61.19 | 24 | 1468.56 |  | 8043.7015 |  | 19012.2615 | 0 | 15 |  | 9500 | Q6 | 61.19 | 39.6 | 2423.124 |  | 10880.6394 | 22803.7634 | 0
[22 empty] | 4000 | [5 empty] | 4000 |  |  |  |  | 1.146 | 10925 | Q6 | 61.19 | 28.2587 | 1729.1478 |  | 9289.1695 | 21943.3173 |  | 15 |  | 10925 | Q6 | 61.19 | 46.6268 | 2853.0939 |  | 12585.2499 | 26363.3438 |  | 10925 | Q6 | 61.19 | 28.2587 | 1729.1478 |  | 9289.1695 |  | 21943.3173 | 0 | 15 |  | 10925 | Q6 | 61.19 | 46.6268 | 2853.0939 |  | 12585.2499 | 26363.3438 | 0
[22 empty] | 8000 | [5 empty] | 8000 |  |  |  |  | 1.146 | 13775 | Q6 | 61.19 | 39.8476 | 2438.2746 |  | 11961.5703 | 28174.8449 |  | 15 |  | 13775 | Q6 | 61.19 | 65.7485 | 4023.1532 |  | 16332.6327 | 34130.7858 |  | 13775 | Q6 | 61.19 | 39.8476 | 2438.2746 |  | 11961.5703 |  | 28174.8449 | 0 | 15 |  | 13775 | Q6 | 61.19 | 65.7485 | 4023.1532 |  | 16332.6327 | 34130.7858 | 0
[22 empty] | 12000 | [5 empty] | 12000 |  |  |  |  | 1.146 | 16625 | Q6 | 61.19 | 51.1072 | 3127.2496 |  | 14614.5146 | 34366.7642 |  | 15 |  | 16625 | Q6 | 61.19 | 84.3269 | 5159.9618 |  | 20043.7581 | 41828.7199 |  | 16625 | Q6 | 61.19 | 51.1072 | 3127.2496 |  | 14614.5146 |  | 34366.7642 | 0 | 15 |  | 16625 | Q6 | 61.19 | 84.3269 | 5159.9618 |  | 20043.7581 | 41828.7199 | 0
[22 empty] | 16000 | [5 empty] | 16000 |  |  |  |  | 1.146 | 19950 | Q6 | 61.19 | 62.8296 | 3844.5432 |  | 17626.0916 | 41420.6348 |  | 15 |  | 19950 | Q6 | 61.19 | 103.6688 | 6343.4963 |  | 24217.755 | 50511.2513 |  | 19950 | Q6 | 61.19 | 62.8296 | 3844.5432 |  | 17626.0916 |  | 41420.6348 | 0 | 15 |  | 19950 | Q6 | 61.19 | 103.6688 | 6343.4963 |  | 24217.755 | 50511.2513 | 0
[22 empty] | 20000 | [5 empty] | 20000 |  |  |  |  | 1.146 | 20700 | Q6 | 61.19 | 80 | 4895.2 |  | 19163.5795 | 44758.7795 |  | 15 |  | 20700 | Q6 | 61.19 | 132 | 8077.08 |  | 26758.4968 | 55535.5768 |  | 20700 | Q6 | 61.19 | 80 | 4895.2 |  | 19163.5795 |  | 44758.7795 | 0 | 15 |  | 20700 | Q6 | 61.19 | 132 | 8077.08 |  | 26758.4968 | 55535.5768 | 0
[16 empty] | Packaged VAV DX Rooftoop Unit | Packaged VAV rooftop system with gas furnace. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. This cost is without an economizer or ERV as they are not always required. | Equipment information below. Labor hours from RS Means 2020 Mechanical Cost Data. Single zone, electric cool, gas heat, VAV, 23 74 33.10 41XX |  |  |  | Cooling Capacity, Tons | Same as for base code for same size units. |  |  |  |  | Cooling Capacity, Tons |  |  |  |  | Inflation from 2012 to 2020 | [32 empty] | 0
[17 empty] | Manufacturer 1 | Faithful+Gould | Carrier | 48 A |  | 20 | [5 empty] | 20 |  |  |  |  | 1.15 | 19800 | Q6 | 61.19 | 56.5667 | 3461.3172 |  | 17268.7843 | 40530.1015 |  | 15 |  | 19800 | Q6 | 61.19 | 93.3351 | 5711.1735 |  | 23527.217 | 49038.3905 |  | 19800 | Q6 | 61.19 | 56.5667 | 3461.3172 |  | 17268.7843 |  | 40530.1015 | 0 | 15 |  | 19800 | Q6 | 61.19 | 93.3351 | 5711.1735 |  | 23527.217 | 49038.3905 | 0
[18 empty] | Airtech Thermex |  | 48 A |  | 25 | [5 empty] | 25 |  |  |  |  | 1.15 | 23400 | Q7 | 62.4 | 66.116 | 4125.6384 |  | 20442.3464 | 47967.9848 |  | 15 |  | 23400 | Q7 | 62.4 | 109.0914 | 6807.3034 |  | 27867.8482 | 58075.1515 |  | 23400 | Q7 | 62.4 | 66.116 | 4125.6384 |  | 20442.3464 |  | 47967.9848 | 0 | 15 |  | 23400 | Q7 | 62.4 | 109.0914 | 6807.3034 |  | 27867.8482 | 58075.1515 | 0
[18 empty] | Minneapolis MN |  | 48 A |  | 30 | [5 empty] | 30 |  |  |  |  | 1.15 | 23850 | Q7 | 62.4 | 78.744 | 4913.6256 |  | 21519.6596 | 50283.2852 |  | 15 |  | 23850 | Q7 | 62.4 | 129.9276 | 8107.4822 |  | 29678.7675 | 61636.2498 |  | 23850 | Q7 | 62.4 | 78.744 | 4913.6256 |  | 21519.6596 |  | 50283.2852 | 0 | 15 |  | 23850 | Q7 | 62.4 | 129.9276 | 8107.4822 |  | 29678.7675 | 61636.2498 | 0
[18 empty] | Carrier |  | 48 A |  | 40 | [5 empty] | 40 |  |  |  |  | 1.15 | 31950 | Q7 | 62.4 | 104 | 6489.6 |  | 28738.6219 | 67178.2219 |  | 15 |  | 31950 | Q7 | 62.4 | 171.6 | 10707.84 |  | 39591.3758 | 82249.2158 |  | 31950 | Q7 | 62.4 | 104 | 6489.6 |  | 28738.6219 |  | 67178.2219 | 0 | 15 |  | 31950 | Q7 | 62.4 | 171.6 | 10707.84 |  | 39591.3758 | 82249.2158 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould | Trane | YCD |  | 20 | [5 empty] | 20 |  |  |  |  | 1.15 | 19500 | Q6 | 61.19 | 56.5667 | 3461.3172 |  | 17057.7703 | 40019.0875 |  | 15 |  | 19500 | Q6 | 61.19 | 93.3351 | 5711.1735 |  | 23265.1016 | 48476.2751 |  | 19500 | Q6 | 61.19 | 56.5667 | 3461.3172 |  | 17057.7703 |  | 40019.0875 | 0 | 15 |  | 19500 | Q6 | 61.19 | 93.3351 | 5711.1735 |  | 23265.1016 | 48476.2751 | 0
[18 empty] | Trane Corp. |  | YCD |  | 25 | [5 empty] | 25 |  |  |  |  | 1.15 | 23125 | Q7 | 62.4 | 66.116 | 4125.6384 |  | 20248.9169 | 47499.5553 |  | 15 |  | 23125 | Q7 | 62.4 | 109.0914 | 6807.3034 |  | 27627.5757 | 57559.8791 |  | 23125 | Q7 | 62.4 | 66.116 | 4125.6384 |  | 20248.9169 |  | 47499.5553 | 0 | 15 |  | 23125 | Q7 | 62.4 | 109.0914 | 6807.3034 |  | 27627.5757 | 57559.8791 | 0
[18 empty] | Minneapolis MN |  | YCD |  | 30 | [5 empty] | 30 |  |  |  |  | 1.15 | 30000 | Q7 | 62.4 | 78.744 | 4913.6256 |  | 25845.4466 | 60759.0722 |  | 15 |  | 30000 | Q7 | 62.4 | 129.9276 | 8107.4822 |  | 35052.1332 | 73159.6155 |  | 30000 | Q7 | 62.4 | 78.744 | 4913.6256 |  | 25845.4466 |  | 60759.0722 | 0 | 15 |  | 30000 | Q7 | 62.4 | 129.9276 | 8107.4822 |  | 35052.1332 | 73159.6155 | 0
[18 empty] | Trane |  | YCD |  | 40 | [5 empty] | 40 |  |  |  |  | 1.15 | 39000 | Q7 | 62.4 | 104 | 6489.6 |  | 33697.4509 | 79187.0509 |  | 15 |  | 39000 | Q7 | 62.4 | 171.6 | 10707.84 |  | 45751.0877 | 95458.9277 |  | 39000 | Q7 | 62.4 | 104 | 6489.6 |  | 33697.4509 |  | 79187.0509 | 0 | 15 |  | 39000 | Q7 | 62.4 | 171.6 | 10707.84 |  | 45751.0877 | 95458.9277 | 0
[16 empty] | VAV_DX | Average of two manufacturers | [15 empty] | 1.15 | [6 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [8 empty] | 0
[18 empty] | 15 ton unit prorated from 20 ton per Means 23 74 33.10 |  |  |  | 15 | [5 empty] | 15 |  |  |  |  | 1.15 | 14478.9474 | Q6 | 61.19 | 48.0159 | 2938.0949 |  | 13020.8973 | 30437.9396 |  | 15 |  | 14478.9474 | Q6 | 61.19 | 79.2263 | 4847.8565 |  | 17936.7361 | 37263.54 |  | 14478.9474 | Q6 | 61.19 | 48.0159 | 2938.0949 |  | 13020.8973 |  | 30437.9396 | 0 | 15 |  | 14478.9474 | Q6 | 61.19 | 79.2263 | 4847.8565 |  | 17936.7361 | 37263.54 | 0
[16 empty] | used for load changes | [5 empty] | 20 | [5 empty] | 20 |  |  |  |  | 1.15 | 19650 | Q6 | 61.19 | 56.5667 | 3461.3172 |  | 17163.2773 | 40274.5945 |  | 15 |  | 19650 | Q6 | 61.19 | 93.3351 | 5711.1735 |  | 23396.1593 | 48757.3328 |  | 19650 | Q6 | 61.19 | 56.5667 | 3461.3172 |  | 17163.2773 |  | 40274.5945 | 0 | 15 |  | 19650 | Q6 | 61.19 | 93.3351 | 5711.1735 |  | 23396.1593 | 48757.3328 | 0
[22 empty] | 25 | [5 empty] | 25 |  |  |  |  | 1.15 | 23262.5 | Q7 | 62.4 | 66.116 | 4125.6384 |  | 20345.6316 | 47733.77 |  | 15 |  | 23262.5 | Q7 | 62.4 | 109.0914 | 6807.3034 |  | 27747.7119 | 57817.5153 |  | 23262.5 | Q7 | 62.4 | 66.116 | 4125.6384 |  | 20345.6316 |  | 47733.77 | 0 | 15 |  | 23262.5 | Q7 | 62.4 | 109.0914 | 6807.3034 |  | 27747.7119 | 57817.5153 | 0
[22 empty] | 30 | [5 empty] | 30 |  |  |  |  | 1.15 | 26925 | Q7 | 62.4 | 78.744 | 4913.6256 |  | 23682.5531 | 55521.1787 |  | 15 |  | 26925 | Q7 | 62.4 | 129.9276 | 8107.4822 |  | 32365.4504 | 67397.9326 |  | 26925 | Q7 | 62.4 | 78.744 | 4913.6256 |  | 23682.5531 |  | 55521.1787 | 0 | 15 |  | 26925 | Q7 | 62.4 | 129.9276 | 8107.4822 |  | 32365.4504 | 67397.9326 | 0
[22 empty] | 40 | [5 empty] | 40 |  |  |  |  | 1.15 | 35475 | Q7 | 62.4 | 104 | 6489.6 |  | 31218.0364 | 73182.6364 |  | 15 |  | 35475 | Q7 | 62.4 | 171.6 | 10707.84 |  | 42671.2318 | 88854.0718 |  | 35475 | Q7 | 62.4 | 104 | 6489.6 |  | 31218.0364 |  | 73182.6364 | 0 | 15 |  | 35475 | Q7 | 62.4 | 171.6 | 10707.84 |  | 42671.2318 | 88854.0718 | 0
[16 empty] | Packaged CAV DX Rooftop Unit | Packaged CAV rooftop system with gas furnace. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. This cost is without an economizer or ERV as they are not always required. | Equipment information below. Labor hours from RS Means 2020 Mechanical Cost Data. Outdoor-Air-Units Roof Top Air Conditioners, single zone, electric cool, gas heat, RS Means 23 74 33.10 11XX |  |  |  | Cooling Capacity, Tons | Same as for base code for same size units. |  |  |  |  | Cooling Capacity, Tons |  |  |  |  | Inflation from 2012 to 2020 | [19 empty] | Material adjustment for inflation | [12 empty] | 0
[17 empty] | Manufacturer 1 | Faithful+Gould | Carrier | 48 ES |  | 2 |  |  |  | 1 |  | 2 |  |  |  |  | 0.833 | 2250 | Q5 | 59 | 19.311 | 1139.349 |  | 1626.1669 | 5015.5159 |  | 15 |  | 2250 | Q5 | 59 | 31.8632 | 1879.9259 |  | 2853.6693 | 6983.5951 |  | 2250 | Q5 | 59 | 19.311 | 1139.349 |  | 1626.1669 |  | 5015.5159 | 0 | 15 |  | 2250 | Q5 | 59 | 31.8632 | 1879.9259 |  | 2853.6693 | 6983.5951 | 0
[17 empty] | No Increased efficiency from 2013 to 2016 | Airtech Thermex | Carrier | 48 ES |  | 2.5 | Means standard vs. Green book values for these units |  |  | 1 |  | 2.5 |  |  |  |  | 0.833 | 2700 | Q5 | 59 | 21.084 | 1243.956 |  | 1832.3915 | 5776.3475 |  | 15 |  | 2700 | Q5 | 59 | 34.7886 | 2052.5274 |  | 3202.6287 | 7955.1561 |  | 2700 | Q5 | 59 | 21.084 | 1243.956 |  | 1832.3915 |  | 5776.3475 | 0 | 15 |  | 2700 | Q5 | 59 | 34.7886 | 2052.5274 |  | 3202.6287 | 7955.1561 | 0
[18 empty] | Minneapolis MN | Carrier | 48 HC |  | 3 | Green book indicates SEER 14 |  |  | 1 |  | 3 |  |  |  |  | 0.833 | 2925 | Q5 | 59 | 22.857 | 1348.563 |  | 1986.0022 | 6259.5652 |  | 15 |  | 2925 | Q5 | 59 | 37.7141 | 2225.1289 |  | 3471.2129 | 8621.3419 |  | 2925 | Q5 | 59 | 22.857 | 1348.563 |  | 1986.0022 |  | 6259.5652 | 0 | 15 |  | 2925 | Q5 | 59 | 37.7141 | 2225.1289 |  | 3471.2129 | 8621.3419 | 0
[18 empty] | Carrier | Carrier | 48 HC |  | 4 | 23 74 33.10 Roof Top Air conditioners |  |  | 1 |  | 4 |  |  |  |  | 0.833 | 3600 | Q5 | 59 | 26.403 | 1557.777 |  | 2345.8376 | 7503.6146 |  | 15 |  | 3600 | Q5 | 59 | 43.565 | 2570.332 |  | 4088.7566 | 10259.0886 |  | 3600 | Q5 | 59 | 26.403 | 1557.777 |  | 2345.8376 |  | 7503.6146 | 0 | 15 |  | 3600 | Q5 | 59 | 43.565 | 2570.332 |  | 4088.7566 | 10259.0886 | 0
[19 empty] | Carrier | 48 HC | 60 | 5 |  |  |  | 1 |  | 5 |  |  |  |  | 0.833 | 4050 | Q5 | 59 | 28.521 | 1682.739 |  | 2571.7147 | 8304.4537 |  | 15 |  | 4050 | Q5 | 59 | 47.0596 | 2776.5194 |  | 4474.3388 | 11300.8581 |  | 4050 | Q5 | 59 | 28.521 | 1682.739 |  | 2571.7147 |  | 8304.4537 | 0 | 15 |  | 4050 | Q5 | 59 | 47.0596 | 2776.5194 |  | 4474.3388 | 11300.8581 | 0
[19 empty] | Carrier | 48 HC | 72 | 6 | [5 empty] | 6 |  |  |  |  | 0.833 | 4500 | Q5 | 59 | 30.769 | 1815.371 |  | 2804.9971 | 9120.3681 |  | 15 |  | 4500 | Q5 | 59 | 50.7689 | 2995.3621 |  | 4873.7208 | 12369.0829 |  | 4500 | Q5 | 59 | 30.769 | 1815.371 |  | 2804.9971 |  | 9120.3681 | 0 | 15 |  | 4500 | Q5 | 59 | 50.7689 | 2995.3621 |  | 4873.7208 | 12369.0829 | 0
[19 empty] | Carrier | 48 HC |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 0.833 | 5850 | Q5 | 59 | 32.258 | 1903.222 |  | 3205.4997 | 10958.7217 |  | 15 |  | 5850 | Q5 | 59 | 53.2257 | 3140.3163 |  | 5514.0341 | 14504.3504 |  | 5850 | Q5 | 59 | 32.258 | 1903.222 |  | 3205.4997 |  | 10958.7217 | 0 | 15 |  | 5850 | Q5 | 59 | 53.2257 | 3140.3163 |  | 5514.0341 | 14504.3504 | 0
[19 empty] | prorated |  |  | 8.5 | [5 empty] | 8.5 |  |  |  |  | 0.833 | 6390 | Q5 | 59 | 33.7476 | 1991.1084 |  | 3416.6263 | 11797.7347 |  | 15 |  | 6390 | Q5 | 59 | 55.6835 | 3285.3289 |  | 5865.06 | 15540.3888 |  | 6390 | Q5 | 59 | 33.7476 | 1991.1084 |  | 3416.6263 |  | 11797.7347 | 0 | 15 |  | 6390 | Q5 | 59 | 55.6835 | 3285.3289 |  | 5865.06 | 15540.3888 | 0
[19 empty] | Carrier | 48 HC |  | 10 | [5 empty] | 10 |  |  |  |  | 0.833 | 7200 | Q6 | 61.19 | 35.982 | 2201.7386 |  | 3809.3973 | 13211.1359 |  | 15 |  | 7200 | Q6 | 61.19 | 59.3703 | 3632.8687 |  | 6533.3768 | 17366.2455 |  | 7200 | Q6 | 61.19 | 35.982 | 2201.7386 |  | 3809.3973 |  | 13211.1359 | 0 | 15 |  | 7200 | Q6 | 61.19 | 59.3703 | 3632.8687 |  | 6533.3768 | 17366.2455 | 0
[19 empty] | Carrier | 48 HC |  | 12.5 | [5 empty] | 12.5 |  |  |  |  | 0.833 | 9000 | Q6 | 61.19 | 37.975 | 2323.6903 |  | 4348.0515 | 15671.7417 |  | 15 |  | 9000 | Q6 | 61.19 | 62.6587 | 3834.0889 |  | 7395.7946 | 20229.8835 |  | 9000 | Q6 | 61.19 | 37.975 | 2323.6903 |  | 4348.0515 |  | 15671.7417 | 0 | 15 |  | 9000 | Q6 | 61.19 | 62.6587 | 3834.0889 |  | 7395.7946 | 20229.8835 | 0
[19 empty] | Carrier | 48 HC |  | 15 | [5 empty] | 15 |  |  |  |  | 0.833 | 9675 | Q6 | 61.19 | 43.032 | 2633.1281 |  | 4804.6517 | 17112.7798 |  | 15 |  | 9675 | Q6 | 61.19 | 71.0028 | 4344.6613 |  | 8193.6609 | 22213.3223 |  | 9675 | Q6 | 61.19 | 43.032 | 2633.1281 |  | 4804.6517 |  | 17112.7798 | 0 | 15 |  | 9675 | Q6 | 61.19 | 71.0028 | 4344.6613 |  | 8193.6609 | 22213.3223 | 0
[19 empty] | Carrier | 48 HC |  | 17.5 | [5 empty] | 17.5 |  |  |  |  | 0.833 | 11250 | Q6 | 61.19 | 45.889 | 2807.9479 |  | 5341.7355 | 19399.6834 |  | 15 |  | 11250 | Q6 | 61.19 | 75.7168 | 4633.1141 |  | 9070.8238 | 24953.9379 |  | 11250 | Q6 | 61.19 | 45.889 | 2807.9479 |  | 5341.7355 |  | 19399.6834 | 0 | 15 |  | 11250 | Q6 | 61.19 | 75.7168 | 4633.1141 |  | 9070.8238 | 24953.9379 | 0
[19 empty] | Carrier | 48 HC |  | 20 | [5 empty] | 20 |  |  |  |  | 0.833 | 12375 | Q7 | 62.4 | 47.976 | 2993.7024 |  | 5784.1488 | 21152.8512 |  | 15 |  | 12375 | Q7 | 62.4 | 79.1604 | 4939.609 |  | 9806.9097 | 27121.5187 |  | 12375 | Q7 | 62.4 | 47.976 | 2993.7024 |  | 5784.1488 |  | 21152.8512 | 0 | 15 |  | 12375 | Q7 | 62.4 | 79.1604 | 4939.609 |  | 9806.9097 | 27121.5187 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould | Trane | 4TCC |  | 2 | [5 empty] | 2 |  |  |  |  | 0.833 | 2500 | Q5 | 59 | 19.311 | 1139.349 |  | 1684.6268 | 5323.9758 |  | 15 |  | 2500 | Q5 | 59 | 31.8632 | 1879.9259 |  | 2942.9752 | 7322.901 |  | 2500 | Q5 | 59 | 19.311 | 1139.349 |  | 1684.6268 |  | 5323.9758 | 0 | 15 |  | 2500 | Q5 | 59 | 31.8632 | 1879.9259 |  | 2942.9752 | 7322.901 | 0
[18 empty] | Trane Corp. | Trane | 4TCC |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 0.833 | 3000 | Q5 | 59 | 21.084 | 1243.956 |  | 1902.5434 | 6146.4994 |  | 15 |  | 3000 | Q5 | 59 | 34.7886 | 2052.5274 |  | 3309.7958 | 8362.3232 |  | 3000 | Q5 | 59 | 21.084 | 1243.956 |  | 1902.5434 |  | 6146.4994 | 0 | 15 |  | 3000 | Q5 | 59 | 34.7886 | 2052.5274 |  | 3309.7958 | 8362.3232 | 0
[18 empty] | Minneapolis MN | Trane | 4TCC |  | 3 | [5 empty] | 3 |  |  |  |  | 0.833 | 3250 | Q5 | 59 | 22.857 | 1348.563 |  | 2062.0001 | 6660.5631 |  | 15 |  | 3250 | Q5 | 59 | 37.7141 | 2225.1289 |  | 3587.3106 | 9062.4395 |  | 3250 | Q5 | 59 | 22.857 | 1348.563 |  | 2062.0001 |  | 6660.5631 | 0 | 15 |  | 3250 | Q5 | 59 | 37.7141 | 2225.1289 |  | 3587.3106 | 9062.4395 | 0
[18 empty] | Trane | Trane | YSC |  | 4 | [5 empty] | 4 |  |  |  |  | 0.833 | 4000 | Q5 | 59 | 26.403 | 1557.777 |  | 2439.3734 | 7997.1504 |  | 15 |  | 4000 | Q5 | 59 | 43.565 | 2570.332 |  | 4231.646 | 10801.978 |  | 4000 | Q5 | 59 | 26.403 | 1557.777 |  | 2439.3734 |  | 7997.1504 | 0 | 15 |  | 4000 | Q5 | 59 | 43.565 | 2570.332 |  | 4231.646 | 10801.978 | 0
[19 empty] | Trane | YSC |  | 5 | [5 empty] | 5 |  |  |  |  | 0.833 | 4500 | Q5 | 59 | 28.521 | 1682.739 |  | 2676.9425 | 8859.6815 |  | 15 |  | 4500 | Q5 | 59 | 47.0596 | 2776.5194 |  | 4635.0894 | 11911.6087 |  | 4500 | Q5 | 59 | 28.521 | 1682.739 |  | 2676.9425 |  | 8859.6815 | 0 | 15 |  | 4500 | Q5 | 59 | 47.0596 | 2776.5194 |  | 4635.0894 | 11911.6087 | 0
[19 empty] | Trane | YSC |  | 6 | [5 empty] | 6 |  |  |  |  | 0.833 | 5000 | Q5 | 59 | 30.769 | 1815.371 |  | 2921.9169 | 9737.2879 |  | 15 |  | 5000 | Q5 | 59 | 50.7689 | 2995.3621 |  | 5052.3326 | 13047.6947 |  | 5000 | Q5 | 59 | 30.769 | 1815.371 |  | 2921.9169 |  | 9737.2879 | 0 | 15 |  | 5000 | Q5 | 59 | 50.7689 | 2995.3621 |  | 5052.3326 | 13047.6947 | 0
[19 empty] | Trane | YSC |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 0.833 | 6500 | Q5 | 59 | 32.258 | 1903.222 |  | 3357.4954 | 11760.7174 |  | 15 |  | 6500 | Q5 | 59 | 53.2257 | 3140.3163 |  | 5746.2294 | 15386.5457 |  | 6500 | Q5 | 59 | 32.258 | 1903.222 |  | 3357.4954 |  | 11760.7174 | 0 | 15 |  | 6500 | Q5 | 59 | 53.2257 | 3140.3163 |  | 5746.2294 | 15386.5457 | 0
[19 empty] | prorated |  |  | 8.5 | [5 empty] | 8.5 |  |  |  |  | 0.833 | 7366.6667 | Q5 | 59 | 33.7476 | 1991.1084 |  | 3645.0097 | 13002.7847 |  | 15 |  | 7366.6667 | Q5 | 59 | 55.6835 | 3285.3289 |  | 6213.9483 | 16865.9439 |  | 7366.6667 | Q5 | 59 | 33.7476 | 1991.1084 |  | 3645.0097 |  | 13002.7847 | 0 | 15 |  | 7366.6667 | Q5 | 59 | 55.6835 | 3285.3289 |  | 6213.9483 | 16865.9439 | 0
[19 empty] | Trane | YSC |  | 10 | [5 empty] | 10 |  |  |  |  | 0.833 | 8000 | Q6 | 61.19 | 35.982 | 2201.7386 |  | 3996.469 | 14198.2076 |  | 15 |  | 8000 | Q6 | 61.19 | 59.3703 | 3632.8687 |  | 6819.1557 | 18452.0243 |  | 8000 | Q6 | 61.19 | 35.982 | 2201.7386 |  | 3996.469 |  | 14198.2076 | 0 | 15 |  | 8000 | Q6 | 61.19 | 59.3703 | 3632.8687 |  | 6819.1557 | 18452.0243 | 0
[19 empty] | Trane | YSC |  | 12.5 | [5 empty] | 12.5 |  |  |  |  | 0.833 | 10000 | Q6 | 61.19 | 37.975 | 2323.6903 |  | 4581.8911 | 16905.5813 |  | 15 |  | 10000 | Q6 | 61.19 | 62.6587 | 3834.0889 |  | 7753.0182 | 21587.1071 |  | 10000 | Q6 | 61.19 | 37.975 | 2323.6903 |  | 4581.8911 |  | 16905.5813 | 0 | 15 |  | 10000 | Q6 | 61.19 | 62.6587 | 3834.0889 |  | 7753.0182 | 21587.1071 | 0
[19 empty] | Trane | YSC |  | 15 | [5 empty] | 15 |  |  |  |  | 0.833 | 10750 | Q6 | 61.19 | 43.032 | 2633.1281 |  | 5056.0293 | 18439.1573 |  | 15 |  | 10750 | Q6 | 61.19 | 71.0028 | 4344.6613 |  | 8577.6763 | 23672.3376 |  | 10750 | Q6 | 61.19 | 43.032 | 2633.1281 |  | 5056.0293 |  | 18439.1573 | 0 | 15 |  | 10750 | Q6 | 61.19 | 71.0028 | 4344.6613 |  | 8577.6763 | 23672.3376 | 0
[19 empty] | Trane | YSC |  | 17.5 | [5 empty] | 17.5 |  |  |  |  | 0.833 | 12500 | Q6 | 61.19 | 45.889 | 2807.9479 |  | 5634.035 | 20941.9829 |  | 15 |  | 12500 | Q6 | 61.19 | 75.7168 | 4633.1141 |  | 9517.3533 | 26650.4673 |  | 12500 | Q6 | 61.19 | 45.889 | 2807.9479 |  | 5634.035 |  | 20941.9829 | 0 | 15 |  | 12500 | Q6 | 61.19 | 75.7168 | 4633.1141 |  | 9517.3533 | 26650.4673 | 0
[19 empty] | Trane | YSC |  | 20 | [5 empty] | 20 |  |  |  |  | 0.833 | 13750 | Q7 | 62.4 | 47.976 | 2993.7024 |  | 6105.6782 | 22849.3806 |  | 15 |  | 13750 | Q7 | 62.4 | 79.1604 | 4939.609 |  | 10298.0921 | 28987.7011 |  | 13750 | Q7 | 62.4 | 47.976 | 2993.7024 |  | 6105.6782 |  | 22849.3806 | 0 | 15 |  | 13750 | Q7 | 62.4 | 79.1604 | 4939.609 |  | 10298.0921 | 28987.7011 | 0
[16 empty] | CAV_DX | Average of two manufacturers
[22 empty] | 1.5 | [5 empty] | 1.5 |  |  |  |  | 0.833 | 1900 | Q5 | 59 | 17.538 | 1034.742 |  | 1443.3262 | 4378.0682 |  | 15 |  | 1900 | Q5 | 59 | 28.9377 | 1707.3243 |  | 2540.4322 | 6147.7565 |  | 1900 | Q5 | 59 | 17.538 | 1034.742 |  | 1443.3262 |  | 4378.0682 | 0 | 15 |  | 1900 | Q5 | 59 | 28.9377 | 1707.3243 |  | 2540.4322 | 6147.7565 | 0
[16 empty] | used for load changes | [5 empty] | 2 | [5 empty] | 2 |  |  |  |  | 0.833 | 2375 | Q5 | 59 | 19.311 | 1139.349 |  | 1655.3968 | 5169.7458 |  | 15 |  | 2375 | Q5 | 59 | 31.8632 | 1879.9259 |  | 2898.3222 | 7153.2481 |  | 2375 | Q5 | 59 | 19.311 | 1139.349 |  | 1655.3968 |  | 5169.7458 | 0 | 15 |  | 2375 | Q5 | 59 | 31.8632 | 1879.9259 |  | 2898.3222 | 7153.2481 | 0
[17 empty] | Material costs shown from 2012 survey are adjusted for inflation to 2020 |  |  |  |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 0.833 | 2850 | Q5 | 59 | 21.084 | 1243.956 |  | 1867.4675 | 5961.4235 |  | 15 |  | 2850 | Q5 | 59 | 34.7886 | 2052.5274 |  | 3256.2123 | 8158.7397 |  | 2850 | Q5 | 59 | 21.084 | 1243.956 |  | 1867.4675 |  | 5961.4235 | 0 | 15 |  | 2850 | Q5 | 59 | 34.7886 | 2052.5274 |  | 3256.2123 | 8158.7397 | 0
[17 empty] | Adjustment included in cost adjustments column and based on |  |  |  |  | 3 | [5 empty] | 3 |  |  |  |  | 0.833 | 3087.5 | Q5 | 59 | 22.857 | 1348.563 |  | 2024.0012 | 6460.0642 |  | 15 |  | 3087.5 | Q5 | 59 | 37.7141 | 2225.1289 |  | 3529.2618 | 8841.8907 |  | 3087.5 | Q5 | 59 | 22.857 | 1348.563 |  | 2024.0012 |  | 6460.0642 | 0 | 15 |  | 3087.5 | Q5 | 59 | 37.7141 | 2225.1289 |  | 3529.2618 | 8841.8907 | 0
[17 empty] | Difference in Means 2012 and 2020 for similar equipment |  |  |  |  | 4 | [5 empty] | 4 |  |  |  |  | 0.833 | 3800 | Q5 | 59 | 26.403 | 1557.777 |  | 2392.6055 | 7750.3825 |  | 15 |  | 3800 | Q5 | 59 | 43.565 | 2570.332 |  | 4160.2013 | 10530.5333 |  | 3800 | Q5 | 59 | 26.403 | 1557.777 |  | 2392.6055 |  | 7750.3825 | 0 | 15 |  | 3800 | Q5 | 59 | 43.565 | 2570.332 |  | 4160.2013 | 10530.5333 | 0
[22 empty] | 5 | [5 empty] | 5 |  |  |  |  | 0.833 | 4275 | Q5 | 59 | 28.521 | 1682.739 |  | 2624.3286 | 8582.0676 |  | 15 |  | 4275 | Q5 | 59 | 47.0596 | 2776.5194 |  | 4554.7141 | 11606.2334 |  | 4275 | Q5 | 59 | 28.521 | 1682.739 |  | 2624.3286 |  | 8582.0676 | 0 | 15 |  | 4275 | Q5 | 59 | 47.0596 | 2776.5194 |  | 4554.7141 | 11606.2334 | 0
[22 empty] | 6 | [5 empty] | 6 |  |  |  |  | 0.833 | 4750 | Q5 | 59 | 30.769 | 1815.371 |  | 2863.457 | 9428.828 |  | 15 |  | 4750 | Q5 | 59 | 50.7689 | 2995.3621 |  | 4963.0267 | 12708.3888 |  | 4750 | Q5 | 59 | 30.769 | 1815.371 |  | 2863.457 |  | 9428.828 | 0 | 15 |  | 4750 | Q5 | 59 | 50.7689 | 2995.3621 |  | 4963.0267 | 12708.3888 | 0
[17 empty] | 2-ton minimum |  |  |  |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 0.833 | 6175 | Q5 | 59 | 32.258 | 1903.222 |  | 3281.4975 | 11359.7195 |  | 15 |  | 6175 | Q5 | 59 | 53.2257 | 3140.3163 |  | 5630.1317 | 14945.448 |  | 6175 | Q5 | 59 | 32.258 | 1903.222 |  | 3281.4975 |  | 11359.7195 | 0 | 15 |  | 6175 | Q5 | 59 | 53.2257 | 3140.3163 |  | 5630.1317 | 14945.448 | 0
[22 empty] | 8.5 | [5 empty] | 8.5 |  |  |  |  | 0.833 | 6878.3333 | Q5 | 59 | 33.7476 | 1991.1084 |  | 3530.818 | 12400.2597 |  | 15 |  | 6878.3333 | Q5 | 59 | 55.6835 | 3285.3289 |  | 6039.5042 | 16203.1664 |  | 6878.3333 | Q5 | 59 | 33.7476 | 1991.1084 |  | 3530.818 |  | 12400.2597 | 0 | 15 |  | 6878.3333 | Q5 | 59 | 55.6835 | 3285.3289 |  | 6039.5042 | 16203.1664 | 0
[22 empty] | 10 | [5 empty] | 10 |  |  |  |  | 0.833 | 7600 | Q6 | 61.19 | 35.982 | 2201.7386 |  | 3902.9331 | 13704.6717 |  | 15 |  | 7600 | Q6 | 61.19 | 59.3703 | 3632.8687 |  | 6676.2662 | 17909.1349 |  | 7600 | Q6 | 61.19 | 35.982 | 2201.7386 |  | 3902.9331 |  | 13704.6717 | 0 | 15 |  | 7600 | Q6 | 61.19 | 59.3703 | 3632.8687 |  | 6676.2662 | 17909.1349 | 0
[22 empty] | 12.5 | [5 empty] | 12.5 |  |  |  |  | 0.833 | 9500 | Q6 | 61.19 | 37.975 | 2323.6903 |  | 4464.9713 | 16288.6615 |  | 15 |  | 9500 | Q6 | 61.19 | 62.6587 | 3834.0889 |  | 7574.4064 | 20908.4953 |  | 9500 | Q6 | 61.19 | 37.975 | 2323.6903 |  | 4464.9713 |  | 16288.6615 | 0 | 15 |  | 9500 | Q6 | 61.19 | 62.6587 | 3834.0889 |  | 7574.4064 | 20908.4953 | 0
[22 empty] | 15 | [5 empty] | 15 |  |  |  |  | 0.833 | 10212.5 | Q6 | 61.19 | 43.032 | 2633.1281 |  | 4930.3405 | 17775.9686 |  | 15 |  | 10212.5 | Q6 | 61.19 | 71.0028 | 4344.6613 |  | 8385.6686 | 22942.8299 |  | 10212.5 | Q6 | 61.19 | 43.032 | 2633.1281 |  | 4930.3405 |  | 17775.9686 | 0 | 15 |  | 10212.5 | Q6 | 61.19 | 71.0028 | 4344.6613 |  | 8385.6686 | 22942.8299 | 0
[22 empty] | 17.5 | [5 empty] | 17.5 |  |  |  |  | 0.833 | 11875 | Q6 | 61.19 | 45.889 | 2807.9479 |  | 5487.8853 | 20170.8332 |  | 15 |  | 11875 | Q6 | 61.19 | 75.7168 | 4633.1141 |  | 9294.0885 | 25802.2026 |  | 11875 | Q6 | 61.19 | 45.889 | 2807.9479 |  | 5487.8853 |  | 20170.8332 | 0 | 15 |  | 11875 | Q6 | 61.19 | 75.7168 | 4633.1141 |  | 9294.0885 | 25802.2026 | 0
[22 empty] | 20 | [5 empty] | 20 |  |  |  |  | 0.833 | 13062.5 | Q7 | 62.4 | 47.976 | 2993.7024 |  | 5944.9135 | 22001.1159 |  | 15 |  | 13062.5 | Q7 | 62.4 | 79.1604 | 4939.609 |  | 10052.5009 | 28054.6099 |  | 13062.5 | Q7 | 62.4 | 47.976 | 2993.7024 |  | 5944.9135 |  | 22001.1159 | 0 | 15 |  | 13062.5 | Q7 | 62.4 | 79.1604 | 4939.609 |  | 10052.5009 | 28054.6099 | 0
[17 empty] | extrapolated - some values in models exceed 20 tons. RS Means shows cost/ton within +/1 5% of the average from 17.5 to 30 tons |  |  |  |  | 30 | [5 empty] | 30 |  |  |  |  | 0.833 | 17812.5 | Q7 | 62.4 | 56.324 | 3514.6176 |  | 7558.589 | 28885.7066 |  | 15 |  | 17812.5 | Q7 | 62.4 | 92.9346 | 5799.119 |  | 12686.5432 | 36298.1623 |  | 17812.5 | Q7 | 62.4 | 56.324 | 3514.6176 |  | 7558.589 |  | 28885.7066 | 0 | 15 |  | 17812.5 | Q7 | 62.4 | 92.9346 | 5799.119 |  | 12686.5432 | 36298.1623 | 0
[16 empty] | Packaged Heat Pump adjusted for load changes | Packaged heat pump with gas backup. This equipment meets the general requirements of the base code that do not change in the target code and are commonly available in the market. This cost is without an economizer or ERV as they are not always required. | Equipment information below. Labor from RS Means 2020 Mechanical Cost Data. Air-Source Heat Pumps, single zone, electric cool, gas heat, RS Means 23 81 43.10 10XX |  |  |  | Cooling Capacity, Tons | Same as for base code for same size units. | [9 empty] | Inflation from 2012 to 2020 | [19 empty] | Material adjustment for inflation
1.158
[17 empty] | Manufacturer 1 | Faithful+Gould | Carrier | 50PSH |  | 1.5 | [5 empty] | 1.5 |  |  |  |  | 1.158 | 1800 | Q5 | 59 | 6.67 | 393.53 |  | 1667.3618 | 3860.8918 |  | 15 |  | 1800 | Q5 | 59 | 11.0055 | 649.3245 |  | 2304.1936 | 4753.5181 |  | 1800 | Q5 | 59 | 6.67 | 393.53 |  | 1667.3618 |  | 3860.8918 | 0 | 15 |  | 1800 | Q5 | 59 | 11.0055 | 649.3245 |  | 2304.1936 | 4753.5181 | 0
[18 empty] | Airtech Thermex | Carrier | 50PSH |  | 2 | [5 empty] | 2 |  |  |  |  | 1.158 | 2250 | Q5 | 59 | 8 | 472 |  | 2064.9769 | 4786.9769 |  | 15 |  | 2250 | Q5 | 59 | 13.2 | 778.8 |  | 2844.4155 | 5873.2155 |  | 2250 | Q5 | 59 | 8 | 472 |  | 2064.9769 |  | 4786.9769 | 0 | 15 |  | 2250 | Q5 | 59 | 13.2 | 778.8 |  | 2844.4155 | 5873.2155 | 0
[18 empty] | Minneapolis MN | Carrier | 50PSH |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.158 | 2475 | Q5 | 59 | 10 | 590 |  | 2339.8312 | 5404.8312 |  | 15 |  | 2475 | Q5 | 59 | 16.5 | 973.5 |  | 3256.2404 | 6704.7404 |  | 2475 | Q5 | 59 | 10 | 590 |  | 2339.8312 |  | 5404.8312 | 0 | 15 |  | 2475 | Q5 | 59 | 16.5 | 973.5 |  | 3256.2404 | 6704.7404 | 0
[18 empty] | Carrier | Carrier | 50PSH |  | 3 |  |  |  | 1 |  | 3 |  |  |  |  | 1.158 | 2700 | Q5 | 59 | 13.33 | 786.47 |  | 2690.4473 | 6176.9173 |  | 15 |  | 2700 | Q5 | 59 | 21.9945 | 1297.6755 |  | 3809.2484 | 7806.9239 |  | 2700 | Q5 | 59 | 13.33 | 786.47 |  | 2690.4473 |  | 6176.9173 | 0 | 15 |  | 2700 | Q5 | 59 | 21.9945 | 1297.6755 |  | 3809.2484 | 7806.9239 | 0
[18 empty] | Carrier | Carrier | 50PSH |  | 4 |  |  |  | 1 |  | 4 |  |  |  |  | 1.158 | 2925 | Q5 | 59 | 20 | 1180 |  | 3231.3224 | 7336.3224 |  | 15 |  | 2925 | Q5 | 59 | 33 | 1947 |  | 4716.8068 | 9588.8068 |  | 2925 | Q5 | 59 | 20 | 1180 |  | 3231.3224 |  | 7336.3224 | 0 | 15 |  | 2925 | Q5 | 59 | 33 | 1947 |  | 4716.8068 | 9588.8068 | 0
[18 empty] | Carrier | Carrier | 50PSH |  | 5 |  |  |  | 1 |  | 5 |  |  |  |  | 1.158 | 3060 | Q5 | 59 | 32 | 1888 |  | 4011.4439 | 8959.4439 |  | 15 |  | 3060 | Q5 | 59 | 52.8 | 3115.2 |  | 6110.3517 | 12285.5517 |  | 3060 | Q5 | 59 | 32 | 1888 |  | 4011.4439 |  | 8959.4439 | 0 | 15 |  | 3060 | Q5 | 59 | 52.8 | 3115.2 |  | 6110.3517 | 12285.5517 | 0
[17 empty] | Manufacturer 2 | Faithful+Gould | [21 empty] | 0
[18 empty] | Trane Corp. | Trane | 4TCC |  | 1.5 | [5 empty] | 1.5 |  |  |  |  | 1.158 | 2025 | Q5 | 59 | 6.67 | 393.53 |  | 1828.2884 | 4246.8184 |  | 15 |  | 2025 | Q5 | 59 | 11.0055 | 649.3245 |  | 2503.713 | 5178.0375 |  | 2025 | Q5 | 59 | 6.67 | 393.53 |  | 1828.2884 |  | 4246.8184 | 0 | 15 |  | 2025 | Q5 | 59 | 11.0055 | 649.3245 |  | 2503.713 | 5178.0375 | 0
[18 empty] | Minneapolis MN | Trane | 4TCC |  | 2 | [5 empty] | 2 |  |  |  |  | 1.158 | 2700 | Q5 | 59 | 8 | 472 |  | 2386.8303 | 5558.8303 |  | 15 |  | 2700 | Q5 | 59 | 13.2 | 778.8 |  | 3243.4541 | 6722.2541 |  | 2700 | Q5 | 59 | 8 | 472 |  | 2386.8303 |  | 5558.8303 | 0 | 15 |  | 2700 | Q5 | 59 | 13.2 | 778.8 |  | 3243.4541 | 6722.2541 | 0
[18 empty] | Trane | Trane | 4TCC |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.158 | 3225 | Q5 | 59 | 10 | 590 |  | 2876.2534 | 6691.2534 |  | 15 |  | 3225 | Q5 | 59 | 16.5 | 973.5 |  | 3921.3048 | 8119.8048 |  | 3225 | Q5 | 59 | 10 | 590 |  | 2876.2534 |  | 6691.2534 | 0 | 15 |  | 3225 | Q5 | 59 | 16.5 | 973.5 |  | 3921.3048 | 8119.8048 | 0
[22 empty] | 3 | [5 empty] | 3
[22 empty] | 4 | [5 empty] | 4
[22 empty] | 5 | [5 empty] | 5
[16 empty] | Heat_Pump | Average of two manufacturers
[22 empty] | 1.5 |  |  |  | 1 |  | 1.5 |  |  |  |  | 1.158 | 1912.5 | Q5 | 59 | 6.67 | 393.53 |  | 1747.8251 | 4053.8551 |  | 15 |  | 1912.5 | Q5 | 59 | 11.0055 | 649.3245 |  | 2403.9533 | 4965.7778 | 1.158 | 1912.5 | Q5 | 59 | 6.67 | 393.53 |  | 1747.8251 |  | 4053.8551 | 0 | 15 |  | 1912.5 | Q5 | 59 | 11.0055 | 649.3245 |  | 2403.9533 | 4965.7778 | 0
[17 empty] | Material costs shown from 2012 survey are adjusted for inflation to 2020 |  |  |  |  | 2 |  |  |  | 1 |  | 2 |  |  |  |  | 1.158 | 2475 | Q5 | 59 | 8 | 472 |  | 2225.9036 | 5172.9036 |  | 15 |  | 2475 | Q5 | 59 | 13.2 | 778.8 |  | 3043.9348 | 6297.7348 | 1.158 | 2475 | Q5 | 59 | 8 | 472 |  | 2225.9036 |  | 5172.9036 | 0 | 15 |  | 2475 | Q5 | 59 | 13.2 | 778.8 |  | 3043.9348 | 6297.7348 | 0
[17 empty] | Adjustment included in cost adjustments column and based on |  |  |  |  | 2.5 |  |  |  | 1 |  | 2.5 |  |  |  |  | 1.158 | 2850 | Q5 | 59 | 10 | 590 |  | 2608.0423 | 6048.0423 |  | 15 |  | 2850 | Q5 | 59 | 16.5 | 973.5 |  | 3588.7726 | 7412.2726 | 1.158 | 2850 | Q5 | 59 | 10 | 590 |  | 2608.0423 |  | 6048.0423 | 0 | 15 |  | 2850 | Q5 | 59 | 16.5 | 973.5 |  | 3588.7726 | 7412.2726 | 0
[17 empty] | Difference in Means 2012 and 2020 for similar equipment |  |  |  |  | 3 |  |  |  | 1 |  | 3 |  |  |  |  | 1.158 | 2700 | Q5 | 59 | 13.33 | 786.47 |  | 2690.4473 | 6176.9173 |  | 15 |  | 2700 | Q5 | 59 | 21.9945 | 1297.6755 |  | 3809.2484 | 7806.9239 | 1.158 | 2700 | Q5 | 59 | 13.33 | 786.47 |  | 2690.4473 |  | 6176.9173 | 0 | 15 |  | 2700 | Q5 | 59 | 21.9945 | 1297.6755 |  | 3809.2484 | 7806.9239 | 0
[22 empty] | 4 |  |  |  | 1 |  | 4 |  |  |  |  | 1.158 | 2925 | Q5 | 59 | 20 | 1180 |  | 3231.3224 | 7336.3224 |  | 15 |  | 2925 | Q5 | 59 | 33 | 1947 |  | 4716.8068 | 9588.8068 | 1.158 | 2925 | Q5 | 59 | 20 | 1180 |  | 3231.3224 |  | 7336.3224 | 0 | 15 |  | 2925 | Q5 | 59 | 33 | 1947 |  | 4716.8068 | 9588.8068 | 0
[22 empty] | 5 |  |  |  | 1 |  | 5 |  |  |  |  | 1.158 | 3060 | Q5 | 59 | 32 | 1888 |  | 4011.4439 | 8959.4439 |  | 15 |  | 3060 | Q5 | 59 | 52.8 | 3115.2 |  | 6110.3517 | 12285.5517 | 1.158 | 3060 | Q5 | 59 | 32 | 1888 |  | 4011.4439 |  | 8959.4439 | 0 | 15 |  | 3060 | Q5 | 59 | 52.8 | 3115.2 |  | 6110.3517 | 12285.5517 | 0
[17 empty] | Split system DX with gas furnace for mid-rise apartment Costs and regression developed in 2012 are updated on apartment prototype sheet with inflation factors based on Means to bring them forward to 2020. | Data shown used to create these: | Curve Fits
[16 empty] | Split-System_W_Furnace |  |  | Material
[18 empty] | All climate zones | y = 17.693x2 - 208.45x + 2690.6
[16 empty] | used for load changes |  |  | R² = 0.9455
Labor
[18 empty] | All climate zones | y = 6.1014x2 - 73.657x + 2202.7
[19 empty] | R² = 0.9001 | [13 empty] | 2020 costs
90.1-2016 bo | [15 empty] | Furnace_eff | 90.1-2016 bo Non-weatherized gas furnace < 225 kBtuh, 78% AFUE, 100 kBtuh | Material costs are from the appliance standard rulemaking. Originally in 2012$ but converted to 2020$. Labor from RS Means 2020 Mechanical Cost Data. Gas-fired furnace, Gas, AGA certified, upflow, direct drive models. RS Means 23 54 16.13 |  |  |  | 100000 | Same as base code but with 81% AFUE | Same as base code 3.4% higher material cost than base code |  |  |  | 100000 |  |  |  |  | 1 | 2673.6 | Q9 | 56.08 | 5 | 280.4 |  | 1557.2592 | 4511.2592 | 0 | 15 |  | 2673.6 | Q9 | 56.08 | 8.25 | 462.66 |  | 2187.0455 | 5323.3055 |  | 2773.6 | Q9 | 56.08 | 5 | 280.4 |  | 1605.3792 |  | 4659.3792 | 0 | 15 |  | 2773.6 | Q9 | 56.08 | 8.25 | 462.66 |  | 2249.9775 | 5486.2375 | 148.12
[16 empty] | Furnace_eff_apt | 90.1-2016 bo Non-weatherized gas furnace < 225 kBtuh, 78% AFUE, 4 kBtuh | Material costs are from the appliance standard rulemaking. Originally in 2012$ but converted to 2020$. Labor from RS Means 2020 Mechanical Cost Data. Gas-fired furnace, Gas, AGA certified, upflow, direct drive models. RS Means 23 54 16.13 |  |  |  | 4000 | Same as base code but with 81% AFUE | Same as base code 3.4% higher material cost than base code |  |  |  | 4000 |  |  |  |  | 1 | 642 | Q9 | 56.08 | 5 | 280.4 |  | 579.6532 | 1502.0532 | 0 | 15 |  | 642 | Q9 | 56.08 | 8.25 | 462.66 |  | 908.519 | 2013.179 |  | 666 | Q9 | 56.08 | 5 | 280.4 |  | 591.202 |  | 1537.602 | 0 | 15 |  | 666 | Q9 | 56.08 | 8.25 | 462.66 |  | 923.6227 | 2052.2827 | 35.5488
|  |  |  | X | X | X | X | X | X | [6 empty] | Duct Work and Zone Air Distribution changes due to HVAC Load Changes | Estimated cost of air delivery duct work and zone components such as terminal units and diffusers for the 6 prototype buildings. Mid-rise apartment common area systems are very small and have negligible differences between cases. Values are ordered from smallest to largest total airflow. The base code and target code estimates are both used for interpolation as the sizing is based on the total airflow, and there are no other differences in duct system costs between the two codes. There are no incremental differences between the two codes except based on changes in load and airflow, so the numbers are relevant, with a cost multiplier based on inflation from 2012 to current prices. Duct costs were developed for a range of climate zones. A curve fit formula was developed with the built-in curve fit function in Excel. Material and labor functions were developed and are shown below with the R2 values. Total costs are computed for each city location with each prototype cost worksheet using the same cost factors - total values shown here are just for these specific airflows. and the total cost is associated with total airflow for purposes of assigning OH&P and other factors. | Solarc one-line diagram and component cost estimate using model HVAC outputs for selected climate zones from PNNL. Costs developed in 2012 are updated with inflation factors based on Means to bring them forward to current costs. |  |  |  | Airflow, cfm | Costs shown are duplicates of the base code costs, adjusted for total airflow. Addendum AU adds deducts from allowed static pressure for systems without central heating and cooling coils. This affects VAV systems in the Primary school and Large office for this CE analysis. Cost impact is evaluated as follows: When units do not have preheat or central heating coils, the fan design static pressure is reduced by 0.3 inches to calculate savings. For those units without preheat coils, it is assumed that ductwork is upsized, resulting in more sheet metal and more labor. Based on an analysis of ductwork sizing for multiple sizes of round ductwork, about 15% of the ductwork needs to be upsized to the next standard size to provide a 0.3" reduction in total system static pressure, resulting in an overall ductwork cost increase of 2.75%. The cost adders are calculated on the HVAC building tabs for units without preheat coils. In the simulation, a preheat coil is used in zones where the mixed air temperature will be less than 55F at design outside air conditions. | Solarc one-line diagram and component cost estimate using model HVAC outputs from PNNL. |  |  |  | Airflow, cfm |  |  |  | 2012 to 2020 Labor inflation adjustment, applied after regression results developed in 2012 | 2012 to 2020 Material inflation adjustment, applied after regression results developed in 2012 | [17 empty] | Inflation cost adjustments not included for air distribution below because they are transferred to where the regressions are applied on prototype sheets
[17 empty] | Small Office | Data shown used to create these: | Curve Fits |  |  |  | Small Office | Data shown used to create these: | Curve Fits | [6 empty] | inf_lab_DUCT | inf_mat_DUCT
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 2958.124 | 3C San Francisco 90.1-2010 |  | Material |  |  | 2958.124 |  |  |  | 1.195 | 1.043 | 5319.4866 | Q-10 | 58.15 | 297.2153 | 17283.0675 |  | 19585.1378 | 42187.6919 |  | 30 |  | 5319.4866 | Q-10 | 58.15 | 490.4052 | 28517.0613 |  | 34443.3474 | 68279.8953 |  | 5319.4866 | Q-10 | 58.15 | 297.2153 | 17283.0675 |  | 19585.1378 |  | 42187.6919 | 0 | 30 |  | 5319.4866 | Q-10 | 58.15 | 490.4052 | 28517.0613 |  | 34816.0347 | 68652.5826 | 0
[17 empty] | 3C San Francisco 90.1-2007 | All climate zones | y = 0.2902x + 4511.3 |  |  | 3055.598 | 3C San Francisco 90.1-2007 | All climate zones | y = 0.2902x + 4511.3 |  |  | 3055.598 |  |  |  | 1.195 | 1.043 | 5325.0322 | Q-10 | 58.15 | 297.7901 | 17316.4916 |  | 19620.4302 | 42261.954 |  | 30 |  | 5325.0322 | Q-10 | 58.15 | 491.3536 | 28572.2111 |  | 34506.974 | 68404.2174 |  | 5325.0322 | Q-10 | 58.15 | 297.7901 | 17316.4916 |  | 19620.4302 |  | 42261.954 | 0 | 30 |  | 5325.0322 | Q-10 | 58.15 | 491.3536 | 28572.2111 |  | 34880.0498 | 68777.2932 | 0
[17 empty] | 7 Duluth 90.1-2010 |  | R² = 0.8963 |  |  | 3318.354 | 7 Duluth 90.1-2010 |  | R² = 0.8963 |  |  | 3318.354 |  |  |  | 1.195 | 1.043 | 5455.4328 | Q-10 | 58.15 | 312.2062 | 18154.7906 |  | 20500.8519 | 44111.0753 |  | 30 |  | 5455.4328 | Q-10 | 58.15 | 515.1402 | 29955.4044 |  | 36097.3049 | 71508.1421 |  | 5455.4328 | Q-10 | 58.15 | 312.2062 | 18154.7906 |  | 20500.8519 |  | 44111.0753 | 0 | 30 |  | 5455.4328 | Q-10 | 58.15 | 515.1402 | 29955.4044 |  | 36479.5166 | 71890.3538 | 0
[17 empty] | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 3369.21 | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 3369.21 |  |  |  | 1.195 | 1.043 | 5524.2951 | Q-10 | 58.15 | 317.2964 | 18450.7831 |  | 20824.1517 | 44799.2299 |  | 30 |  | 5524.2951 | Q-10 | 58.15 | 523.539 | 30443.7921 |  | 36673.191 | 72641.2782 |  | 5524.2951 | Q-10 | 58.15 | 317.2964 | 18450.7831 |  | 20824.1517 |  | 44799.2299 | 0 | 30 |  | 5524.2951 | Q-10 | 58.15 | 523.539 | 30443.7921 |  | 37060.2273 | 73028.3145 | 0
[17 empty] | 5A Chicago 90.1-2010 | All climate zones | y = 1.5764x + 9922.5 |  |  | 3426.423 | 5A Chicago 90.1-2010 | All climate zones | y = 1.5764x + 9922.5 |  |  | 3426.423 |  |  |  | 1.195 | 1.043 | 5560.5069 | Q-10 | 58.15 | 315.3198 | 18335.8485 |  | 20732.9152 | 44629.2705 |  | 30 |  | 5560.5069 | Q-10 | 58.15 | 520.2777 | 30254.15 |  | 36489.1895 | 72303.8463 |  | 5560.5069 | Q-10 | 58.15 | 315.3198 | 18335.8485 |  | 20732.9152 |  | 44629.2705 | 0 | 30 |  | 5560.5069 | Q-10 | 58.15 | 520.2777 | 30254.15 |  | 36878.7628 | 72693.4197 | 0
[17 empty] | 7 Duluth 90.1-2007 |  | R² = 0.9473 |  |  | 3437.018 | 7 Duluth 90.1-2007 |  | R² = 0.9473 |  |  | 3437.018 |  |  |  | 1.195 | 1.043 | 5573.041 | Q-10 | 58.15 | 319.3544 | 18570.4572 |  | 20966.2568 | 45109.755 |  | 30 |  | 5573.041 | Q-10 | 58.15 | 526.9347 | 30641.2544 |  | 36919.1853 | 73133.4807 |  | 5573.041 | Q-10 | 58.15 | 319.3544 | 18570.4572 |  | 20966.2568 |  | 45109.755 | 0 | 30 |  | 5573.041 | Q-10 | 58.15 | 526.9347 | 30641.2544 |  | 37309.6368 | 73523.9322 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  |  |  |  | 3500.588 | 8 Fairbanks 90.1-2007 |  |  |  |  | 3500.588 |  |  |  | 1.195 | 1.043 | 5533.0058 | Q-10 | 58.15 | 318.1283 | 18499.1617 |  | 20875.607 | 44907.7745 |  | 30 |  | 5533.0058 | Q-10 | 58.15 | 524.9117 | 30523.6168 |  | 36765.7155 | 72822.3382 |  | 5533.0058 | Q-10 | 58.15 | 318.1283 | 18499.1617 |  | 20875.607 |  | 44907.7745 | 0 | 30 |  | 5533.0058 | Q-10 | 58.15 | 524.9117 | 30523.6168 |  | 37153.3621 | 73209.9847 | 0
[17 empty] | 5A Chicago 90.1-2007 |  |  |  |  | 3538.73 | 5A Chicago 90.1-2007 |  |  |  |  | 3538.73 |  |  |  | 1.195 | 1.043 | 5528.4947 | Q-10 | 58.15 | 316.1077 | 18381.6646 |  | 20759.7069 | 44669.8662 |  | 30 |  | 5528.4947 | Q-10 | 58.15 | 521.5778 | 30329.7465 |  | 36551.4758 | 72409.7171 |  | 5528.4947 | Q-10 | 58.15 | 316.1077 | 18381.6646 |  | 20759.7069 |  | 44669.8662 | 0 | 30 |  | 5528.4947 | Q-10 | 58.15 | 521.5778 | 30329.7465 |  | 36938.8064 | 72797.0476 | 0
[17 empty] | 2A Houston 90.1-2010 |  |  |  |  | 3788.772 | 2A Houston 90.1-2010 |  |  |  |  | 3788.772 |  |  |  | 1.195 | 1.043 | 5663.377 | Q-10 | 58.15 | 328.2 | 19084.8276 |  | 21512.0986 | 46260.3032 |  | 30 |  | 5663.377 | Q-10 | 58.15 | 541.5299 | 31489.9655 |  | 37901.4906 | 75054.8331 |  | 5663.377 | Q-10 | 58.15 | 328.2 | 19084.8276 |  | 21512.0986 |  | 46260.3032 | 0 | 30 |  | 5663.377 | Q-10 | 58.15 | 541.5299 | 31489.9655 |  | 38298.2711 | 75451.6136 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 3873.532 | 2A Houston 90.1-2007 |  |  |  |  | 3873.532 |  |  |  | 1.195 | 1.043 | 5677.3444 | Q-10 | 58.15 | 329.2156 | 19143.8884 |  | 21576.7318 | 46397.9645 |  | 30 |  | 5677.3444 | Q-10 | 58.15 | 543.2058 | 31587.4158 |  | 38016.5427 | 75281.3029 |  | 5677.3444 | Q-10 | 58.15 | 329.2156 | 19143.8884 |  | 21576.7318 |  | 46397.9645 | 0 | 30 |  | 5677.3444 | Q-10 | 58.15 | 543.2058 | 31587.4158 |  | 38414.3017 | 75679.0619 | 0
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 4026.1 | 3B El Paso 90.1-2010 |  |  |  |  | 4026.1 |  |  |  | 1.195 | 1.043 | 5667.0382 | Q-10 | 58.15 | 334.7161 | 19463.7411 |  | 21879.9299 | 47010.7092 |  | 30 |  | 5667.0382 | Q-10 | 58.15 | 552.2816 | 32115.1727 |  | 38585.5356 | 76367.7465 |  | 5667.0382 | Q-10 | 58.15 | 334.7161 | 19463.7411 |  | 21879.9299 |  | 47010.7092 | 0 | 30 |  | 5667.0382 | Q-10 | 58.15 | 552.2816 | 32115.1727 |  | 38982.5726 | 76764.7835 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 4138.407 | 3B El Paso 90.1-2007 |  |  |  |  | 4138.407 |  |  |  | 1.195 | 1.043 | 5693.3871 | Q-10 | 58.15 | 341.6567 | 19867.3344 |  | 22283.9517 | 47844.6731 |  | 30 |  | 5693.3871 | Q-10 | 58.15 | 563.7335 | 32781.1017 |  | 39328.2624 | 77802.7512 |  | 5693.3871 | Q-10 | 58.15 | 341.6567 | 19867.3344 |  | 22283.9517 |  | 47844.6731 | 0 | 30 |  | 5693.3871 | Q-10 | 58.15 | 563.7335 | 32781.1017 |  | 39727.1454 | 78201.6342 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 4651.205 | 2B Phoenix 90.1-2010 |  |  |  |  | 4651.205 |  |  |  | 1.195 | 1.043 | 5891.0895 | Q-10 | 58.15 | 358.483 | 20845.7885 |  | 23336.3639 | 50073.2419 |  | 30 |  | 5891.0895 | Q-10 | 58.15 | 591.497 | 34395.551 |  | 41213.1148 | 81499.7554 |  | 5891.0895 | Q-10 | 58.15 | 358.483 | 20845.7885 |  | 23336.3639 |  | 50073.2419 | 0 | 30 |  | 5891.0895 | Q-10 | 58.15 | 591.497 | 34395.551 |  | 41625.849 | 81912.4896 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 4771.988 | 2B Phoenix 90.1-2007 |  |  |  |  | 4771.988 |  |  |  | 1.195 | 1.043 | 5933.2863 | Q-10 | 58.15 | 362.1621 | 21059.7239 |  | 23565.9086 | 50558.9188 |  | 30 |  | 5933.2863 | Q-10 | 58.15 | 597.5674 | 34748.5444 |  | 41624.5826 | 82306.4133 |  | 5933.2863 | Q-10 | 58.15 | 362.1621 | 21059.7239 |  | 23565.9086 |  | 50558.9188 | 0 | 30 |  | 5933.2863 | Q-10 | 58.15 | 597.5674 | 34748.5444 |  | 42040.2731 | 82722.1038 | 0
[17 empty] | Large Office | Data shown used to create these: | Curve Fits |  |  |  | Large Office | Data shown used to create these: | Curve Fits | [17 empty] | 30 | [16 empty] | 0 |  |  |  | 30
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 230185 | 3C San Francisco 90.1-2010 |  | Material |  |  | 230185 |  |  |  | 1.195 | 1.043 | 663915.5344 | Q-10 | 58.15 | 48101.7068 | 2797114.2488 |  | 3062342.2396 | 6523372.0228 |  | 30 |  | 663915.5344 | Q-10 | 58.15 | 79367.8162 | 4615238.5105 |  | 5450382.1617 | 10729536.2065 |  | 663915.5344 | Q-10 | 58.15 | 48101.7068 | 2797114.2488 |  | 3062342.2396 |  | 6523372.0228 | 0 | 30 |  | 663915.5344 | Q-10 | 58.15 | 79367.8162 | 4615238.5105 |  | 5496896.5886 | 10776050.6335 | 0
[17 empty] | 3C San Francisco 90.1-2007 | All climate zones | y = 0.7091x + 503192 |  |  | 245425 | 3C San Francisco 90.1-2007 | All climate zones | y = 0.7091x + 503192 |  |  | 245425 |  |  |  | 1.195 | 1.043 | 675326.6127 | Q-10 | 58.15 | 49125.1967 | 2856630.1887 |  | 3126021.9662 | 6657978.7676 |  | 30 |  | 675326.6127 | Q-10 | 58.15 | 81056.5746 | 4713439.8114 |  | 5564644.4368 | 10953410.8609 |  | 675326.6127 | Q-10 | 58.15 | 49125.1967 | 2856630.1887 |  | 3126021.9662 |  | 6657978.7676 | 0 | 30 |  | 675326.6127 | Q-10 | 58.15 | 81056.5746 | 4713439.8114 |  | 5611958.3325 | 11000724.7566 | 0
[17 empty] | 7 Duluth 90.1-2010 |  | R² = 0.8176 |  |  | 253877 | 7 Duluth 90.1-2010 |  | R² = 0.8176 |  |  | 253877 |  |  |  | 1.195 | 1.043 | 689128.217 | Q-10 | 58.15 | 50442.5718 | 2933235.5513 |  | 3207503.9028 | 6829867.6711 |  | 30 |  | 689128.217 | Q-10 | 58.15 | 83230.2435 | 4839838.6597 |  | 5711158.4002 | 11240125.2769 |  | 689128.217 | Q-10 | 58.15 | 50442.5718 | 2933235.5513 |  | 3207503.9028 |  | 6829867.6711 | 0 | 30 |  | 689128.217 | Q-10 | 58.15 | 83230.2435 | 4839838.6597 |  | 5759439.2468 | 11288406.1235 | 0
[17 empty] | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 254832 | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 254832 |  |  |  | 1.195 | 1.043 | 685966.793 | Q-10 | 58.15 | 50314.7022 | 2925799.9334 |  | 3198602.2695 | 6810368.9959 |  | 30 |  | 685966.793 | Q-10 | 58.15 | 83019.2586 | 4827569.8902 |  | 5695790.6921 | 11209327.3752 |  | 685966.793 | Q-10 | 58.15 | 50314.7022 | 2925799.9334 |  | 3198602.2695 |  | 6810368.9959 | 0 | 30 |  | 685966.793 | Q-10 | 58.15 | 83019.2586 | 4827569.8902 |  | 5743850.0469 | 11257386.7301 | 0
[17 empty] | 5A Chicago 90.1-2010 | All climate zones | y = 3.2521x + 2E+06 |  |  | 256016 | 5A Chicago 90.1-2010 | All climate zones | y = 3.2521x + 2E+06 |  |  | 256016 |  |  |  | 1.195 | 1.043 | 675696.0406 | Q-10 | 58.15 | 49513.8753 | 2879231.8512 |  | 3148044.8983 | 6702972.7901 |  | 30 |  | 675696.0406 | Q-10 | 58.15 | 81697.8943 | 4750732.5545 |  | 5605541.8273 | 11031970.4224 |  | 675696.0406 | Q-10 | 58.15 | 49513.8753 | 2879231.8512 |  | 3148044.8983 |  | 6702972.7901 | 0 | 30 |  | 675696.0406 | Q-10 | 58.15 | 81697.8943 | 4750732.5545 |  | 5652881.6054 | 11079310.2006 | 0
[17 empty] | 2A Houston 90.1-2010 |  | R² = 0.8751 |  |  | 258539 | 2A Houston 90.1-2010 |  | R² = 0.8751 |  |  | 258539 |  |  |  | 1.195 | 1.043 | 679011.6898 | Q-10 | 58.15 | 49650.0737 | 2887151.7861 |  | 3157498.1698 | 6723661.6458 |  | 30 |  | 679011.6898 | Q-10 | 58.15 | 81922.6216 | 4763800.4471 |  | 5621877.9754 | 11064690.1124 |  | 679011.6898 | Q-10 | 58.15 | 49650.0737 | 2887151.7861 |  | 3157498.1698 |  | 6723661.6458 | 0 | 30 |  | 679011.6898 | Q-10 | 58.15 | 81922.6216 | 4763800.4471 |  | 5669450.0505 | 11112262.1874 | 0
[17 empty] | 7 Duluth 90.1-2007 |  |  |  |  | 259259 | 7 Duluth 90.1-2007 |  |  |  |  | 259259 |  |  |  | 1.195 | 1.043 | 698774.9563 | Q-10 | 58.15 | 51261.6796 | 2980866.6715 |  | 3258747.6049 | 6938389.2327 |  | 30 |  | 698774.9563 | Q-10 | 58.15 | 84581.7714 | 4918430.008 |  | 5802927.1785 | 11420132.1427 |  | 698774.9563 | Q-10 | 58.15 | 51261.6796 | 2980866.6715 |  | 3258747.6049 |  | 6938389.2327 | 0 | 30 |  | 698774.9563 | Q-10 | 58.15 | 84581.7714 | 4918430.008 |  | 5851883.883 | 11469088.8472 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  |  |  |  | 271190 | 8 Fairbanks 90.1-2007 |  |  |  |  | 271190 |  |  |  | 1.195 | 1.043 | 702825.2456 | Q-10 | 58.15 | 51278.4716 | 2981843.1238 |  | 3261897.3265 | 6946565.6959 |  | 30 |  | 702825.2456 | Q-10 | 58.15 | 84609.4781 | 4920041.1543 |  | 5807232.9392 | 11430099.339 |  | 702825.2456 | Q-10 | 58.15 | 51278.4716 | 2981843.1238 |  | 3261897.3265 |  | 6946565.6959 | 0 | 30 |  | 702825.2456 | Q-10 | 58.15 | 84609.4781 | 4920041.1543 |  | 5856473.41 | 11479339.8099 | 0
[17 empty] | 5A Chicago 90.1-2007 |  |  |  |  | 271316 | 5A Chicago 90.1-2007 |  |  |  |  | 271316 |  |  |  | 1.195 | 1.043 | 697784.9223 | Q-10 | 58.15 | 51200.781 | 2977325.414 |  | 3254789.1021 | 6929899.4384 |  | 30 |  | 697784.9223 | Q-10 | 58.15 | 84481.2886 | 4912586.9331 |  | 5795932.7013 | 11406304.5567 |  | 697784.9223 | Q-10 | 58.15 | 51200.781 | 2977325.414 |  | 3254789.1021 |  | 6929899.4384 | 0 | 30 |  | 697784.9223 | Q-10 | 58.15 | 84481.2886 | 4912586.9331 |  | 5844820.0433 | 11455191.8987 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 271572 | 2A Houston 90.1-2007 |  |  |  |  | 271572 |  |  |  | 1.195 | 1.043 | 699129.7767 | Q-10 | 58.15 | 51290.041 | 2982515.8839 |  | 3260533.2383 | 6942178.8989 |  | 30 |  | 699129.7767 | Q-10 | 58.15 | 84628.5676 | 4921151.2084 |  | 5806117.7363 | 11426398.7214 |  | 699129.7767 | Q-10 | 58.15 | 51290.041 | 2982515.8839 |  | 3260533.2383 |  | 6942178.8989 | 0 | 30 |  | 699129.7767 | Q-10 | 58.15 | 84628.5676 | 4921151.2084 |  | 5855099.2998 | 11475380.2849 | 0
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 281318 | 3B El Paso 90.1-2010 |  |  |  |  | 281318 |  |  |  | 1.195 | 1.043 | 690016.8724 | Q-10 | 58.15 | 50859.3711 | 2957472.4291 |  | 3231388.5382 | 6878877.8397 |  | 30 |  | 690016.8724 | Q-10 | 58.15 | 83917.9623 | 4879829.508 |  | 5755324.6295 | 11325171.0099 |  | 690016.8724 | Q-10 | 58.15 | 50859.3711 | 2957472.4291 |  | 3231388.5382 |  | 6878877.8397 | 0 | 30 |  | 690016.8724 | Q-10 | 58.15 | 83917.9623 | 4879829.508 |  | 5803667.736 | 11373514.1164 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 285937 | 2B Phoenix 90.1-2010 |  |  |  |  | 285937 |  |  |  | 1.195 | 1.043 | 707455.8883 | Q-10 | 58.15 | 52420.6289 | 3048259.572 |  | 3328544.8086 | 7084260.269 |  | 30 |  | 707455.8883 | Q-10 | 58.15 | 86494.0377 | 5029628.2939 |  | 5929643.5424 | 11666727.7246 |  | 707455.8883 | Q-10 | 58.15 | 52420.6289 | 3048259.572 |  | 3328544.8086 |  | 7084260.269 | 0 | 30 |  | 707455.8883 | Q-10 | 58.15 | 86494.0377 | 5029628.2939 |  | 5979208.4396 | 11716292.6218 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 298776 | 3B El Paso 90.1-2007 |  |  |  |  | 298776 |  |  |  | 1.195 | 1.043 | 711463.6654 | Q-10 | 58.15 | 52571.3975 | 3057026.7649 |  | 3339193.2321 | 7107683.6624 |  | 30 |  | 711463.6654 | Q-10 | 58.15 | 86742.8059 | 5044094.162 |  | 5947939.6465 | 11703497.4739 |  | 711463.6654 | Q-10 | 58.15 | 52571.3975 | 3057026.7649 |  | 3339193.2321 |  | 7107683.6624 | 0 | 30 |  | 711463.6654 | Q-10 | 58.15 | 86742.8059 | 5044094.162 |  | 5997785.3316 | 11753343.159 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 300964 | 2B Phoenix 90.1-2007 |  |  |  |  | 300964 |  |  |  | 1.195 | 1.043 | 719825.4451 | Q-10 | 58.15 | 53326.1176 | 3100913.7393 |  | 3386121.8428 | 7206861.0271 |  | 30 |  | 719825.4451 | Q-10 | 58.15 | 87988.0941 | 5116507.6698 |  | 6032163.3084 | 11868496.4233 |  | 719825.4451 | Q-10 | 58.15 | 53326.1176 | 3100913.7393 |  | 3386121.8428 |  | 7206861.0271 | 0 | 30 |  | 719825.4451 | Q-10 | 58.15 | 87988.0941 | 5116507.6698 |  | 6082594.8262 | 11918927.941 | 0
[17 empty] | Stand-Alone Retail | Data shown used to create these: | Curve Fits |  |  |  | Stand-Alone Retail | Data shown used to create these: | Curve Fits | [17 empty] | 30 | [16 empty] | 0 |  |  |  | 30
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 17869.527 | 3C San Francisco 90.1-2010 |  | Material |  |  | 17869.527 |  |  |  | 1.195 | 1.043 | 24053.6174 | Q-10 | 58.15 | 1808.0927 | 105140.5883 |  | 114618.5904 | 243812.7961 |  | 30 |  | 24053.6174 | Q-10 | 58.15 | 2983.3529 | 173481.9707 |  | 204306.3269 | 401841.9149 |  | 24053.6174 | Q-10 | 58.15 | 1808.0927 | 105140.5883 |  | 114618.5904 |  | 243812.7961 | 0 | 30 |  | 24053.6174 | Q-10 | 58.15 | 2983.3529 | 173481.9707 |  | 205991.5416 | 403527.1297 | 0
[17 empty] | 3C San Francisco 90.1-2007 | All climate zones | y = 1.6479x + 55981 |  |  | 18594.225 | 3C San Francisco 90.1-2007 | All climate zones | y = 1.6479x + 55981 |  |  | 18594.225 |  |  |  | 1.195 | 1.043 | 23027.9819 | Q-10 | 58.15 | 1725.7147 | 100350.3114 |  | 109434.7754 | 232813.0687 |  | 30 |  | 23027.9819 | Q-10 | 58.15 | 2847.4293 | 165578.0139 |  | 195042.2097 | 383648.2054 |  | 23027.9819 | Q-10 | 58.15 | 1725.7147 | 100350.3114 |  | 109434.7754 |  | 232813.0687 | 0 | 30 |  | 23027.9819 | Q-10 | 58.15 | 2847.4293 | 165578.0139 |  | 196655.5676 | 385261.5634 | 0
[17 empty] | 2A Houston 90.1-2010 |  | R² = 0.653 |  |  | 19912.243 | 2A Houston 90.1-2010 |  | R² = 0.653 |  |  | 19912.243 |  |  |  | 1.195 | 1.043 | 24479.6468 | Q-10 | 58.15 | 1853.3094 | 107769.9408 |  | 117389.3385 | 249638.926 |  | 30 |  | 24479.6468 | Q-10 | 58.15 | 3057.9605 | 177820.4022 |  | 209305.1656 | 411605.2147 |  | 24479.6468 | Q-10 | 58.15 | 1853.3094 | 107769.9408 |  | 117389.3385 |  | 249638.926 | 0 | 30 |  | 24479.6468 | Q-10 | 58.15 | 3057.9605 | 177820.4022 |  | 211020.2283 | 413320.2773 | 0
[17 empty] | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 20075.406 | 8 Fairbanks 90.1-2010 |  | Labor |  |  | 20075.406 |  |  |  | 1.195 | 1.043 | 24838.5194 | Q-10 | 58.15 | 1857.7226 | 108026.5717 |  | 117832.6592 | 250697.7503 |  | 30 |  | 24838.5194 | Q-10 | 58.15 | 3065.2424 | 178243.8433 |  | 209992.7416 | 413075.1043 |  | 24838.5194 | Q-10 | 58.15 | 1857.7226 | 108026.5717 |  | 117832.6592 |  | 250697.7503 | 0 | 30 |  | 24838.5194 | Q-10 | 58.15 | 3065.2424 | 178243.8433 |  | 211732.9471 | 414815.3098 | 0
[17 empty] | 7 Duluth 90.1-2010 | All climate zones | y = 0.2548x + 18981 |  |  | 20187.713 | 7 Duluth 90.1-2010 | All climate zones | y = 0.2548x + 18981 |  |  | 20187.713 |  |  |  | 1.195 | 1.043 | 24860.9491 | Q-10 | 58.15 | 1865.1998 | 108461.3684 |  | 118264.672 | 251586.9896 |  | 30 |  | 24860.9491 | Q-10 | 58.15 | 3077.5797 | 178961.2579 |  | 210789.1432 | 414611.3502 |  | 24860.9491 | Q-10 | 58.15 | 1865.1998 | 108461.3684 |  | 118264.672 |  | 251586.9896 | 0 | 30 |  | 24860.9491 | Q-10 | 58.15 | 3077.5797 | 178961.2579 |  | 212530.9202 | 416353.1272 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  | R² = 0.4026 |  |  | 20344.519 | 8 Fairbanks 90.1-2007 |  | R² = 0.4026 |  |  | 20344.519 |  |  |  | 1.195 | 1.043 | 23693.168 | Q-10 | 58.15 | 1764.6613 | 102615.053 |  | 111983.8105 | 238292.0315 |  | 30 |  | 23693.168 | Q-10 | 58.15 | 2911.6911 | 169314.8374 |  | 199535.5468 | 392543.5522 |  | 23693.168 | Q-10 | 58.15 | 1764.6613 | 102615.053 |  | 111983.8105 |  | 238292.0315 | 0 | 30 |  | 23693.168 | Q-10 | 58.15 | 2911.6911 | 169314.8374 |  | 201195.5081 | 394203.5136 | 0
[17 empty] | 7 Duluth 90.1-2007 |  |  |  |  | 20594.561 | 7 Duluth 90.1-2007 |  |  |  |  | 20594.561 |  |  |  | 1.195 | 1.043 | 23714.1003 | Q-10 | 58.15 | 1786.22 | 103868.6947 |  | 113205.5923 | 240788.3873 |  | 30 |  | 23714.1003 | Q-10 | 58.15 | 2947.263 | 171383.3462 |  | 201804.2715 | 396901.718 |  | 23714.1003 | Q-10 | 58.15 | 1786.22 | 103868.6947 |  | 113205.5923 |  | 240788.3873 | 0 | 30 |  | 23714.1003 | Q-10 | 58.15 | 2947.263 | 171383.3462 |  | 203465.6994 | 398563.1459 | 0
[17 empty] | 5A Chicago 90.1-2007 |  |  |  |  | 21058.622 | 5A Chicago 90.1-2007 |  |  |  |  | 21058.622 |  |  |  | 1.195 | 1.043 | 23474.7283 | Q-10 | 58.15 | 1834.799 | 106693.5636 |  | 115802.5377 | 245970.8296 |  | 30 |  | 23474.7283 | Q-10 | 58.15 | 3027.4184 | 176044.38 |  | 206736.1331 | 406255.2414 |  | 23474.7283 | Q-10 | 58.15 | 1834.799 | 106693.5636 |  | 115802.5377 |  | 245970.8296 | 0 | 30 |  | 23474.7283 | Q-10 | 58.15 | 3027.4184 | 176044.38 |  | 208380.7904 | 407899.8987 | 0
[17 empty] | 5A Chicago 90.1-2010 |  |  |  |  | 21062.86 | 5A Chicago 90.1-2010 |  |  |  |  | 21062.86 |  |  |  | 1.195 | 1.043 | 24612.6341 | Q-10 | 58.15 | 1928.187 | 112124.0732 |  | 121665.6648 | 258402.3721 |  | 30 |  | 24612.6341 | Q-10 | 58.15 | 3181.5085 | 185004.7208 |  | 217222.8106 | 426840.1655 |  | 24612.6341 | Q-10 | 58.15 | 1928.187 | 112124.0732 |  | 121665.6648 |  | 258402.3721 | 0 | 30 |  | 24612.6341 | Q-10 | 58.15 | 3181.5085 | 185004.7208 |  | 218947.1904 | 428564.5454 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 21287.474 | 2A Houston 90.1-2007 |  |  |  |  | 21287.474 |  |  |  | 1.195 | 1.043 | 23595.4942 | Q-10 | 58.15 | 1845.4964 | 107315.6157 |  | 116468.9257 | 247380.0356 |  | 30 |  | 23595.4942 | Q-10 | 58.15 | 3045.0691 | 177070.7659 |  | 207931.3292 | 408597.5893 |  | 23595.4942 | Q-10 | 58.15 | 1845.4964 | 107315.6157 |  | 116468.9257 |  | 247380.0356 | 0 | 30 |  | 23595.4942 | Q-10 | 58.15 | 3045.0691 | 177070.7659 |  | 209584.4475 | 410250.7076 | 0
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 23285.691 | 3B El Paso 90.1-2010 |  |  |  |  | 23285.691 |  |  |  | 1.195 | 1.043 | 25234.9412 | Q-10 | 58.15 | 1986.5171 | 115515.9719 |  | 125279.5922 | 266030.5053 |  | 30 |  | 25234.9412 | Q-10 | 58.15 | 3277.7533 | 190601.3537 |  | 223717.1437 | 439553.4385 |  | 25234.9412 | Q-10 | 58.15 | 1986.5171 | 115515.9719 |  | 125279.5922 |  | 266030.5053 | 0 | 30 |  | 25234.9412 | Q-10 | 58.15 | 3277.7533 | 190601.3537 |  | 225485.1228 | 441321.4177 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 23677.706 | 2B Phoenix 90.1-2010 |  |  |  |  | 23677.706 |  |  |  | 1.195 | 1.043 | 25849.2066 | Q-10 | 58.15 | 2007.8867 | 116758.6125 |  | 126814.0548 | 269421.8739 |  | 30 |  | 25849.2066 | Q-10 | 58.15 | 3313.0131 | 192651.7106 |  | 226339.4716 | 444840.3889 |  | 25849.2066 | Q-10 | 58.15 | 2007.8867 | 116758.6125 |  | 126814.0548 |  | 269421.8739 | 0 | 30 |  | 25849.2066 | Q-10 | 58.15 | 3313.0131 | 192651.7106 |  | 228150.4867 | 446651.4039 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 24031.579 | 3B El Paso 90.1-2007 |  |  |  |  | 24031.579 |  |  |  | 1.195 | 1.043 | 24888.2633 | Q-10 | 58.15 | 1940.6309 | 112847.6848 |  | 122514.4911 | 260250.4392 |  | 30 |  | 24888.2633 | Q-10 | 58.15 | 3202.0409 | 186198.6799 |  | 218698.1912 | 429785.1344 |  | 24888.2633 | Q-10 | 58.15 | 1940.6309 | 112847.6848 |  | 122514.4911 |  | 260250.4392 | 0 | 30 |  | 24888.2633 | Q-10 | 58.15 | 3202.0409 | 186198.6799 |  | 220441.8818 | 431528.825 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 24279.502 | 2B Phoenix 90.1-2007 |  |  |  |  | 24279.502 |  |  |  | 1.195 | 1.043 | 24907.6016 | Q-10 | 58.15 | 1929.756 | 112215.3116 |  | 121914.4796 | 259037.3928 |  | 30 |  | 24907.6016 | Q-10 | 58.15 | 3184.0974 | 185155.2642 |  | 217572.5956 | 427635.4613 |  | 24907.6016 | Q-10 | 58.15 | 1929.756 | 112215.3116 |  | 121914.4796 |  | 259037.3928 | 0 | 30 |  | 24907.6016 | Q-10 | 58.15 | 3184.0974 | 185155.2642 |  | 219317.6411 | 429380.5068 | 0
[17 empty] | Primary School | Data shown used to create these: | Curve Fits |  |  |  | Primary School | Data shown used to create these: | Curve Fits | [17 empty] | 30 | [16 empty] | 0 |  |  |  | 30
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 35054.617 | 3C San Francisco 90.1-2010 |  | Material |  |  | 35054.617 |  |  |  | 1.195 | 1.043 | 53620.9438 | Q-10 | 58.15 | 3548.0497 | 206319.0884 |  | 228416.2059 | 488356.2381 |  | 30 |  | 53620.9438 | Q-10 | 58.15 | 5854.282 | 340426.4959 |  | 404953.9537 | 799001.3934 |  | 53620.9438 | Q-10 | 58.15 | 3548.0497 | 206319.0884 |  | 228416.2059 |  | 488356.2381 | 0 | 30 |  | 53620.9438 | Q-10 | 58.15 | 5854.282 | 340426.4959 |  | 408710.6778 | 802758.1175 | 0
[17 empty] | 5A Chicago 90.1-2010 | All climate zones | y = 0.7194x + 28317 |  |  | 37404.588 | 5A Chicago 90.1-2010 | All climate zones | y = 0.7194x + 28317 |  |  | 37404.588 |  |  |  | 1.195 | 1.043 | 54570.3589 | Q-10 | 58.15 | 3675.0338 | 213703.2171 |  | 236062.8219 | 504336.3979 |  | 30 |  | 54570.3589 | Q-10 | 58.15 | 6063.8058 | 352610.3083 |  | 418836.961 | 826017.6282 |  | 54570.3589 | Q-10 | 58.15 | 3675.0338 | 213703.2171 |  | 236062.8219 |  | 504336.3979 | 0 | 30 |  | 54570.3589 | Q-10 | 58.15 | 6063.8058 | 352610.3083 |  | 422660.2018 | 829840.869 | 0
[17 empty] | 2A Houston 90.1-2010 |  | R² = 0.8831 |  |  | 37580.465 | 2A Houston 90.1-2010 |  | R² = 0.8831 |  |  | 37580.465 |  |  |  | 1.195 | 1.043 | 55188.5807 | Q-10 | 58.15 | 3707.4736 | 215589.5883 |  | 238220.9545 | 508999.1235 |  | 30 |  | 55188.5807 | Q-10 | 58.15 | 6117.3314 | 355722.8207 |  | 422619.9787 | 833531.3801 |  | 55188.5807 | Q-10 | 58.15 | 3707.4736 | 215589.5883 |  | 238220.9545 |  | 508999.1235 | 0 | 30 |  | 55188.5807 | Q-10 | 58.15 | 6117.3314 | 355722.8207 |  | 426486.5326 | 837397.934 | 0
[17 empty] | 3B El Paso 90.1-2010 |  | Labor |  |  | 38726.844 | 3B El Paso 90.1-2010 |  | Labor |  |  | 38726.844 |  |  |  | 1.195 | 1.043 | 55188.6914 | Q-10 | 58.15 | 3734.7954 | 217178.3545 |  | 239754.9495 | 512121.9953 |  | 30 |  | 55188.6914 | Q-10 | 58.15 | 6162.4125 | 358344.2849 |  | 425478.5558 | 839011.5321 |  | 55188.6914 | Q-10 | 58.15 | 3734.7954 | 217178.3545 |  | 239754.9495 |  | 512121.9953 | 0 | 30 |  | 55188.6914 | Q-10 | 58.15 | 6162.4125 | 358344.2849 |  | 429345.1175 | 842878.0938 | 0
[17 empty] | 8 Fairbanks 90.1-2010 | All climate zones | y = 2.3902x + 122683 |  |  | 41513.329 | 8 Fairbanks 90.1-2010 | All climate zones | y = 2.3902x + 122683 |  |  | 41513.329 |  |  |  | 1.195 | 1.043 | 63139.493 | Q-10 | 58.15 | 3802.255 | 221101.1294 |  | 247874.6665 | 532115.2889 |  | 30 |  | 63139.493 | Q-10 | 58.15 | 6273.7208 | 364816.8634 |  | 437540.0092 | 865496.3656 |  | 63139.493 | Q-10 | 58.15 | 3802.255 | 221101.1294 |  | 247874.6665 |  | 532115.2889 | 0 | 30 |  | 63139.493 | Q-10 | 58.15 | 6273.7208 | 364816.8634 |  | 441963.6101 | 869919.9665 | 0
[17 empty] | 5A Chicago 90.1-2007 |  | R² = 0.9806 |  |  | 42066.388 | 5A Chicago 90.1-2007 |  | R² = 0.9806 |  |  | 42066.388 |  |  |  | 1.195 | 1.043 | 58574.8997 | Q-10 | 58.15 | 3780.3358 | 219826.5244 |  | 244156.8422 | 522558.2664 |  | 30 |  | 58574.8997 | Q-10 | 58.15 | 6237.554 | 362713.7653 |  | 432374.1507 | 853662.8157 |  | 58574.8997 | Q-10 | 58.15 | 3780.3358 | 219826.5244 |  | 244156.8422 |  | 522558.2664 | 0 | 30 |  | 58574.8997 | Q-10 | 58.15 | 6237.554 | 362713.7653 |  | 436477.9527 | 857766.6177 | 0
[17 empty] | 7 Duluth 90.1-2010 |  |  |  |  | 42464.76 | 7 Duluth 90.1-2010 |  |  |  |  | 42464.76 |  |  |  | 1.195 | 1.043 | 56869.5314 | Q-10 | 58.15 | 3860.7914 | 224505.019 |  | 247744.6317 | 529119.1821 |  | 30 |  | 56869.5314 | Q-10 | 58.15 | 6370.3058 | 370433.2814 |  | 439718.4739 | 867021.2866 |  | 56869.5314 | Q-10 | 58.15 | 3860.7914 | 224505.019 |  | 247744.6317 |  | 529119.1821 | 0 | 30 |  | 56869.5314 | Q-10 | 58.15 | 6370.3058 | 370433.2814 |  | 443702.7965 | 871005.6092 | 0
[17 empty] | 3C San Francisco 90.1-2007 |  |  |  |  | 43291.17 | 3C San Francisco 90.1-2007 |  |  |  |  | 43291.17 |  |  |  | 1.195 | 1.043 | 59289.5655 | Q-10 | 58.15 | 3839.2298 | 223251.2135 |  | 247852.7538 | 530393.5328 |  | 30 |  | 59289.5655 | Q-10 | 58.15 | 6334.7292 | 368364.5022 |  | 438985.6033 | 866639.671 |  | 59289.5655 | Q-10 | 58.15 | 3839.2298 | 223251.2135 |  | 247852.7538 |  | 530393.5328 | 0 | 30 |  | 59289.5655 | Q-10 | 58.15 | 6334.7292 | 368364.5022 |  | 443139.4753 | 870793.543 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 44649.449 | 2A Houston 90.1-2007 |  |  |  |  | 44649.449 |  |  |  | 1.195 | 1.043 | 60114.8423 | Q-10 | 58.15 | 3949.7563 | 229678.3293 |  | 254507.7434 | 544300.915 |  | 30 |  | 60114.8423 | Q-10 | 58.15 | 6517.0979 | 378969.2434 |  | 451068.6308 | 890152.7165 |  | 60114.8423 | Q-10 | 58.15 | 3949.7563 | 229678.3293 |  | 254507.7434 |  | 544300.915 | 0 | 30 |  | 60114.8423 | Q-10 | 58.15 | 6517.0979 | 378969.2434 |  | 455280.3223 | 894364.408 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 46596.81 | 3B El Paso 90.1-2007 |  |  |  |  | 46596.81 |  |  |  | 1.195 | 1.043 | 61199.8034 | Q-10 | 58.15 | 4019.5966 | 233739.5417 |  | 259019.9815 | 553959.3266 |  | 30 |  | 61199.8034 | Q-10 | 58.15 | 6632.3344 | 385670.2438 |  | 459058.3503 | 905928.3975 |  | 61199.8034 | Q-10 | 58.15 | 4019.5966 | 233739.5417 |  | 259019.9815 |  | 553959.3266 | 0 | 30 |  | 61199.8034 | Q-10 | 58.15 | 6632.3344 | 385670.2438 |  | 463346.055 | 910216.1023 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  |  |  |  | 47094.775 | 8 Fairbanks 90.1-2007 |  |  |  |  | 47094.775 |  |  |  | 1.195 | 1.043 | 62766.6473 | Q-10 | 58.15 | 4012.2401 | 233311.7644 |  | 259460.7276 | 555539.1393 |  | 30 |  | 62766.6473 | Q-10 | 58.15 | 6620.1962 | 384964.4112 |  | 459274.7396 | 907005.7981 |  | 62766.6473 | Q-10 | 58.15 | 4012.2401 | 233311.7644 |  | 259460.7276 |  | 555539.1393 | 0 | 30 |  | 62766.6473 | Q-10 | 58.15 | 6620.1962 | 384964.4112 |  | 463672.2186 | 911403.2771 | 0
[17 empty] | 7 Duluth 90.1-2007 |  |  |  |  | 48137.323 | 7 Duluth 90.1-2007 |  |  |  |  | 48137.323 |  |  |  | 1.195 | 1.043 | 63027.4877 | Q-10 | 58.15 | 4052.6703 | 235662.7784 |  | 261872.7332 | 560562.9994 |  | 30 |  | 63027.4877 | Q-10 | 58.15 | 6686.906 | 388843.5844 |  | 463668.8353 | 915539.9074 |  | 63027.4877 | Q-10 | 58.15 | 4052.6703 | 235662.7784 |  | 261872.7332 |  | 560562.9994 | 0 | 30 |  | 63027.4877 | Q-10 | 58.15 | 6686.906 | 388843.5844 |  | 468084.5889 | 919955.661 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 50716.146 | 2B Phoenix 90.1-2010 |  |  |  |  | 50716.146 |  |  |  | 1.195 | 1.043 | 63463.7216 | Q-10 | 58.15 | 4234.0229 | 246208.4323 |  | 272292.1356 | 581964.2895 |  | 30 |  | 63463.7216 | Q-10 | 58.15 | 6986.1378 | 406243.9132 |  | 482917.1021 | 952624.7369 |  | 63463.7216 | Q-10 | 58.15 | 4234.0229 | 246208.4323 |  | 272292.1356 |  | 581964.2895 | 0 | 30 |  | 63463.7216 | Q-10 | 58.15 | 6986.1378 | 406243.9132 |  | 487363.4187 | 957071.0535 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 58073.314 | 2B Phoenix 90.1-2007 |  |  |  |  | 58073.314 |  |  |  | 1.195 | 1.043 | 70667.8186 | Q-10 | 58.15 | 4532.0979 | 263541.4906 |  | 292952.4475 | 627161.7567 |  | 30 |  | 70667.8186 | Q-10 | 58.15 | 7477.9615 | 434843.4596 |  | 518636.4162 | 1024147.6943 |  | 70667.8186 | Q-10 | 58.15 | 4532.0979 | 263541.4906 |  | 292952.4475 |  | 627161.7567 | 0 | 30 |  | 70667.8186 | Q-10 | 58.15 | 7477.9615 | 434843.4596 |  | 523587.4572 | 1029098.7354 | 0
[17 empty] | Small Hotel | Data shown used to create these: | Curve Fits |  |  |  | Small Hotel | Data shown used to create these: | Curve Fits | [17 empty] | 30 | [16 empty] | 0 |  |  |  | 30
[17 empty] | 3C San Francisco 90.1-2010 |  | Material |  |  | 3492.112 | 3C San Francisco 90.1-2010 |  | Material |  |  | 3492.112 |  |  |  | 1.195 | 1.043 | 8425.4318 | Q-10 | 58.15 | 532.8548 | 30985.5066 |  | 34507.0819 | 73918.0203 |  | 30 |  | 8425.4318 | Q-10 | 58.15 | 879.2104 | 51126.086 |  | 61051.4039 | 120602.9217 |  | 8425.4318 | Q-10 | 58.15 | 532.8548 | 30985.5066 |  | 34507.0819 |  | 73918.0203 | 0 | 30 |  | 8425.4318 | Q-10 | 58.15 | 879.2104 | 51126.086 |  | 61641.6961 | 121193.2139 | 0
[17 empty] | 8 Fairbanks 90.1-2010 | All climate zones | y = 0.7074x + 6086.9 |  |  | 3737.916 | 8 Fairbanks 90.1-2010 | All climate zones | y = 0.7074x + 6086.9 |  |  | 3737.916 |  |  |  | 1.195 | 1.043 | 8587.9865 | Q-10 | 58.15 | 547.4913 | 31836.6175 |  | 35417.3938 | 75841.9978 |  | 30 |  | 8587.9865 | Q-10 | 58.15 | 903.3606 | 52530.4188 |  | 62685.0211 | 123803.4265 |  | 8587.9865 | Q-10 | 58.15 | 547.4913 | 31836.6175 |  | 35417.3938 |  | 75841.9978 | 0 | 30 |  | 8587.9865 | Q-10 | 58.15 | 903.3606 | 52530.4188 |  | 63286.702 | 124405.1073 | 0
[17 empty] | 5A Chicago 90.1-2010 |  | R² = 0.9622 |  |  | 4411.758 | 5A Chicago 90.1-2010 |  | R² = 0.9622 |  |  | 4411.758 |  |  |  | 1.195 | 1.043 | 9353.6082 | Q-10 | 58.15 | 613.6193 | 35681.9602 |  | 39547.2069 | 84582.7754 |  | 30 |  | 9353.6082 | Q-10 | 58.15 | 1012.4718 | 58875.2343 |  | 70085.3812 | 138314.2238 |  | 9353.6082 | Q-10 | 58.15 | 613.6193 | 35681.9602 |  | 39547.2069 |  | 84582.7754 | 0 | 30 |  | 9353.6082 | Q-10 | 58.15 | 1012.4718 | 58875.2343 |  | 70740.7021 | 138969.5447 | 0
[17 empty] | 7 Duluth 90.1-2010 |  | Labor |  |  | 4511.351 | 7 Duluth 90.1-2010 |  | Labor |  |  | 4511.351 |  |  |  | 1.195 | 1.043 | 9314.2037 | Q-10 | 58.15 | 611.6989 | 35570.2922 |  | 39417.9216 | 84302.4175 |  | 30 |  | 9314.2037 | Q-10 | 58.15 | 1009.3032 | 58690.9821 |  | 69859.6702 | 137864.856 |  | 9314.2037 | Q-10 | 58.15 | 611.6989 | 35570.2922 |  | 39417.9216 |  | 84302.4175 | 0 | 30 |  | 9314.2037 | Q-10 | 58.15 | 1009.3032 | 58690.9821 |  | 70512.2304 | 138517.4162 | 0
[17 empty] | 2A Houston 90.1-2010 | All climate zones | y = 2.9572x + 16341 |  |  | 4593.992 | 2A Houston 90.1-2010 | All climate zones | y = 2.9572x + 16341 |  |  | 4593.992 |  |  |  | 1.195 | 1.043 | 9553.1801 | Q-10 | 58.15 | 633.9429 | 36863.7808 |  | 40796.9856 | 87213.9465 |  | 30 |  | 9553.1801 | Q-10 | 58.15 | 1046.0058 | 60825.2384 |  | 72337.307 | 142715.7255 |  | 9553.1801 | Q-10 | 58.15 | 633.9429 | 36863.7808 |  | 40796.9856 |  | 87213.9465 | 0 | 30 |  | 9553.1801 | Q-10 | 58.15 | 1046.0058 | 60825.2384 |  | 73006.6101 | 143385.0286 | 0
[17 empty] | 7 Duluth 90.1-2007 |  | R² = 0.9466 |  |  | 4680.871 | 7 Duluth 90.1-2007 |  | R² = 0.9466 |  |  | 4680.871 |  |  |  | 1.195 | 1.043 | 9312.7364 | Q-10 | 58.15 | 614.8847 | 35755.5454 |  | 39595.9819 | 84664.2637 |  | 30 |  | 9312.7364 | Q-10 | 58.15 | 1014.5598 | 58996.6499 |  | 70192.0543 | 138501.4406 |  | 9312.7364 | Q-10 | 58.15 | 614.8847 | 35755.5454 |  | 39595.9819 |  | 84664.2637 | 0 | 30 |  | 9312.7364 | Q-10 | 58.15 | 1014.5598 | 58996.6499 |  | 70844.5116 | 139153.898 | 0
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 5083.481 | 3B El Paso 90.1-2010 |  |  |  |  | 5083.481 |  |  |  | 1.195 | 1.043 | 9819.5651 | Q-10 | 58.15 | 659.927 | 38374.7528 |  | 42400.9618 | 90595.2797 |  | 30 |  | 9819.5651 | Q-10 | 58.15 | 1088.8795 | 63318.342 |  | 75223.4885 | 148361.3956 |  | 9819.5651 | Q-10 | 58.15 | 659.927 | 38374.7528 |  | 42400.9618 |  | 90595.2797 | 0 | 30 |  | 9819.5651 | Q-10 | 58.15 | 1088.8795 | 63318.342 |  | 75911.4547 | 149049.3618 | 0
[17 empty] | 3C San Francisco 90.1-2007 |  |  |  |  | 5085.6 | 3C San Francisco 90.1-2007 |  |  |  |  | 5085.6 |  |  |  | 1.195 | 1.043 | 9591.5348 | Q-10 | 58.15 | 640.6247 | 37252.3236 |  | 41193.0182 | 88036.8766 |  | 30 |  | 9591.5348 | Q-10 | 58.15 | 1057.0307 | 61466.334 |  | 73060.5104 | 144118.3792 |  | 9591.5348 | Q-10 | 58.15 | 640.6247 | 37252.3236 |  | 41193.0182 |  | 88036.8766 | 0 | 30 |  | 9591.5348 | Q-10 | 58.15 | 1057.0307 | 61466.334 |  | 73732.5007 | 144790.3694 | 0
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 5094.076 | 2B Phoenix 90.1-2010 |  |  |  |  | 5094.076 |  |  |  | 1.195 | 1.043 | 9784.4779 | Q-10 | 58.15 | 656.0811 | 38151.1166 |  | 42165.9251 | 90101.5196 |  | 30 |  | 9784.4779 | Q-10 | 58.15 | 1082.5338 | 62949.3424 |  | 74799.0414 | 147532.8617 |  | 9784.4779 | Q-10 | 58.15 | 656.0811 | 38151.1166 |  | 42165.9251 |  | 90101.5196 | 0 | 30 |  | 9784.4779 | Q-10 | 58.15 | 1082.5338 | 62949.3424 |  | 75484.5494 | 148218.3697 | 0
[17 empty] | 8 Fairbanks 90.1-2007 |  |  |  |  | 5350.475 | 8 Fairbanks 90.1-2007 |  |  |  |  | 5350.475 |  |  |  | 1.195 | 1.043 | 9862.534 | Q-10 | 58.15 | 663.9704 | 38609.8804 |  | 42651.3882 | 91123.8026 |  | 30 |  | 9862.534 | Q-10 | 58.15 | 1095.5512 | 63706.3027 |  | 75673.5713 | 149242.408 |  | 9862.534 | Q-10 | 58.15 | 663.9704 | 38609.8804 |  | 42651.3882 |  | 91123.8026 | 0 | 30 |  | 9862.534 | Q-10 | 58.15 | 1095.5512 | 63706.3027 |  | 76364.5479 | 149933.3846 | 0
[17 empty] | 5A Chicago 90.1-2007 |  |  |  |  | 5405.569 | 5A Chicago 90.1-2007 |  |  |  |  | 5405.569 |  |  |  | 1.195 | 1.043 | 9917.4022 | Q-10 | 58.15 | 670.7663 | 39005.0604 |  | 43062.8269 | 91985.2894 |  | 30 |  | 9917.4022 | Q-10 | 58.15 | 1106.7644 | 64358.3497 |  | 76419.1086 | 150694.8604 |  | 9917.4022 | Q-10 | 58.15 | 670.7663 | 39005.0604 |  | 43062.8269 |  | 91985.2894 | 0 | 30 |  | 9917.4022 | Q-10 | 58.15 | 1106.7644 | 64358.3497 |  | 77113.9293 | 151389.6812 | 0
[17 empty] | 2A Houston 90.1-2007 |  |  |  |  | 5859.035 | 2A Houston 90.1-2007 |  |  |  |  | 5859.035 |  |  |  | 1.195 | 1.043 | 10203.735 | Q-10 | 58.15 | 688.2672 | 40022.7362 |  | 44201.401 | 94427.8721 |  | 30 |  | 10203.735 | Q-10 | 58.15 | 1135.6408 | 66037.5147 |  | 78430.3054 | 154671.5551 |  | 10203.735 | Q-10 | 58.15 | 688.2672 | 40022.7362 |  | 44201.401 |  | 94427.8721 | 0 | 30 |  | 10203.735 | Q-10 | 58.15 | 1135.6408 | 66037.5147 |  | 79145.1868 | 155386.4365 | 0
[17 empty] | 3B El Paso 90.1-2007 |  |  |  |  | 6164.171 | 3B El Paso 90.1-2007 |  |  |  |  | 6164.171 |  |  |  | 1.195 | 1.043 | 10465.5171 | Q-10 | 58.15 | 709.2653 | 41243.7769 |  | 45522.9441 | 97232.2381 |  | 30 |  | 10465.5171 | Q-10 | 58.15 | 1170.2877 | 68052.2319 |  | 80791.9462 | 159309.6953 |  | 10465.5171 | Q-10 | 58.15 | 709.2653 | 41243.7769 |  | 45522.9441 |  | 97232.2381 | 0 | 30 |  | 10465.5171 | Q-10 | 58.15 | 1170.2877 | 68052.2319 |  | 81525.1683 | 160042.9174 | 0
[17 empty] | 2B Phoenix 90.1-2007 |  |  |  |  | 6388.785 | 2B Phoenix 90.1-2007 |  |  |  |  | 6388.785 |  |  |  | 1.195 | 1.043 | 10445.111 | Q-10 | 58.15 | 701.6581 | 40801.419 |  | 45084.7336 | 96331.2635 |  | 30 |  | 10445.111 | Q-10 | 58.15 | 1157.7359 | 67322.3413 |  | 79983.2139 | 157750.6661 |  | 10445.111 | Q-10 | 58.15 | 701.6581 | 40801.419 |  | 45084.7336 |  | 96331.2635 | 0 | 30 |  | 10445.111 | Q-10 | 58.15 | 1157.7359 | 67322.3413 |  | 80715.0063 | 158482.4585 | 0
[16 empty] | VFD 90.1-2013 dd affects both heating and cooling pumps | Cost to add VFD to other listed equipment and integrated into the package. In some cases both base case and target case equipment are required to have VFDs, and in some cases not. The thresholds change, but changes can also occur as a result of load and system sizing changes. | Equipment information below. Labor from RS Means 2020 Mechanical Cost Data. Variable Frequency Drives/Adj. Frequency Drives 26 29 23.10 01XX |  |  |  | VFD motor horsepower controlled | Same as base code |  |  |  |  | VFD motor horsepower controlled |  |  |  |  | Inflation from 2012 to 2020
Manufacturer 1
[18 empty] | online | ABB |  |  | 1 | [5 empty] | 1 |  |  |  |  | 1.246 | 570 | Elec | 61.35 | 10 | 613.5 |  | 1074.3048 | 2257.8048 |  | 15 |  | 570 | Elec | 61.35 | 16.5 | 1012.275 |  | 1690.9846 | 3273.2596 |  | 570 | Elec | 61.35 | 10 | 613.5 |  | 1074.3048 |  | 2257.8048 | 0 | 15 |  | 570 | Elec | 61.35 | 16.5 | 1012.275 |  | 1690.9846 | 3273.2596 | 0
[16 empty] | used for load changes |  | www.joiliettech.com/abb_acs-550 | ABB |  |  | 2 | [5 empty] | 2 |  |  |  |  | 1.246 | 585 | 1 Elec | 61.35 | 10 | 613.5 |  | 1086.9884 | 2285.4884 |  | 15 |  | 585 | Elec | 61.35 | 16.5 | 1012.275 |  | 1706.4366 | 3303.7116 |  | 585 | 1 Elec | 61.35 | 10 | 613.5 |  | 1086.9884 |  | 2285.4884 | 0 | 15 |  | 585 | Elec | 61.35 | 16.5 | 1012.275 |  | 1706.4366 | 3303.7116 | 0
[18 empty] | -ac_drive_480v_ratings.htm | ABB |  |  | 3 | [5 empty] | 3 |  |  |  |  | 1.246 | 744 | 1 Elec | 61.35 | 10 | 613.5 |  | 1221.4348 | 2578.9348 |  | 15 |  | 744 | Elec | 61.35 | 16.5 | 1012.275 |  | 1870.2277 | 3626.5027 |  | 744 | 1 Elec | 61.35 | 10 | 613.5 |  | 1221.4348 |  | 2578.9348 | 0 | 15 |  | 744 | Elec | 61.35 | 16.5 | 1012.275 |  | 1870.2277 | 3626.5027 | 0
[19 empty] | ABB |  |  | 5 | [5 empty] | 5 |  |  |  |  | 1.246 | 954 | 1 Elec | 61.35 | 10 | 613.5 |  | 1399.0056 | 2966.5056 |  | 15 |  | 954 | Elec | 61.35 | 16.5 | 1012.275 |  | 2086.5556 | 4052.8306 |  | 954 | 1 Elec | 61.35 | 10 | 613.5 |  | 1399.0056 |  | 2966.5056 | 0 | 15 |  | 954 | Elec | 61.35 | 16.5 | 1012.275 |  | 2086.5556 | 4052.8306 | 0
[19 empty] | ABB |  |  | 10 | [5 empty] | 10 |  |  |  |  | 1.246 | 1300 | 1 Elec | 61.35 | 11.94 | 732.519 |  | 1806.4861 | 3839.0051 |  | 15 |  | 1300 | Elec | 61.35 | 19.701 | 1208.6563 |  | 2657.1204 | 5165.7768 |  | 1300 | 1 Elec | 61.35 | 11.94 | 732.519 |  | 1806.4861 |  | 3839.0051 | 0 | 15 |  | 1300 | Elec | 61.35 | 19.701 | 1208.6563 |  | 2657.1204 | 5165.7768 | 0
[19 empty] | ABB |  |  | 20 | [5 empty] | 20 |  |  |  |  | 1.246 | 2159 | 2 Elec | 61.35 | 17.8 | 1092.03 |  | 2879.9387 | 6130.9687 |  | 15 |  | 2159 | Elec | 61.35 | 29.37 | 1801.8495 |  | 4188.8365 | 8149.686 |  | 2159 | 2 Elec | 61.35 | 17.8 | 1092.03 |  | 2879.9387 |  | 6130.9687 | 0 | 15 |  | 2159 | Elec | 61.35 | 29.37 | 1801.8495 |  | 4188.8365 | 8149.686 | 0
[19 empty] | ABB |  |  | 50 | [5 empty] | 50 |  |  |  |  | 1.246 | 4113 | 2 Elec | 61.35 | 30.189 | 1852.0952 |  | 5266.0264 | 11231.1216 |  | 15 |  | 4113 | Elec | 61.35 | 49.8118 | 3055.957 |  | 7569.2247 | 14738.1817 |  | 4113 | 2 Elec | 61.35 | 30.189 | 1852.0952 |  | 5266.0264 |  | 11231.1216 | 0 | 15 |  | 4113 | Elec | 61.35 | 49.8118 | 3055.957 |  | 7569.2247 | 14738.1817 | 0
[19 empty] | ABB |  |  | 75 | [5 empty] | 75 |  |  |  |  | 1.246 | 6660 | R-3 | 61.12 | 35.174 | 2149.8349 |  | 7707.1706 | 16517.0055 |  | 15 |  | 6660 | Elec | 61.12 | 58.0371 | 3547.2276 |  | 10728.666 | 20935.8935 |  | 6660 | R-3 | 61.12 | 35.174 | 2149.8349 |  | 7707.1706 |  | 16517.0055 | 0 | 15 |  | 6660 | Elec | 61.12 | 58.0371 | 3547.2276 |  | 10728.666 | 20935.8935 | 0
[19 empty] | ABB |  |  | 100 | [5 empty] | 100 |  |  |  |  | 1.246 | 7758 | R-3 | 61.12 | 40 | 2444.8 |  | 8920.3975 | 19123.1975 |  | 15 |  | 7758 | Elec | 61.12 | 66 | 4033.92 |  | 12390.4528 | 24182.3728 |  | 7758 | R-3 | 61.12 | 40 | 2444.8 |  | 8920.3975 |  | 19123.1975 | 0 | 15 |  | 7758 | Elec | 61.12 | 66 | 4033.92 |  | 12390.4528 | 24182.3728 | 0
[16 empty] | VFD_Size | [16 empty] | 1.246 | [11 empty] | 0 | [27 empty] | 0
[18 empty] | PNNL from online | ABB |  |  | 1 | [5 empty] | 1 |  |  |  |  | 1.246 | 570 | 1 Elec | 61.35 | 10 | 613.5 |  | 1074.3048 | 2257.8048 |  | 15 |  | 570 | 1 Elec | 61.35 | 16.5 | 1012.275 |  | 1690.9846 | 3273.2596 |  | 570 | 1 Elec | 61.35 | 10 | 613.5 |  | 1074.3048 |  | 2257.8048 | 0 | 15 |  | 570 | 1 Elec | 61.35 | 16.5 | 1012.275 |  | 1690.9846 | 3273.2596 | 0
[18 empty] | www.joiliettech.com/abb_acs-550 | ABB |  |  | 2 | [5 empty] | 2 |  |  |  |  | 1.246 | 585 | 1 Elec | 61.35 | 10 | 613.5 |  | 1086.9884 | 2285.4884 |  | 15 |  | 585 | 1 Elec | 61.35 | 16.5 | 1012.275 |  | 1706.4366 | 3303.7116 |  | 585 | 1 Elec | 61.35 | 10 | 613.5 |  | 1086.9884 |  | 2285.4884 | 0 | 15 |  | 585 | 1 Elec | 61.35 | 16.5 | 1012.275 |  | 1706.4366 | 3303.7116 | 0
[18 empty] | -ac_drive_480v_ratings.htm | ABB |  |  | 3 | [5 empty] | 3 |  |  |  |  | 1.246 | 744 | 1 Elec | 61.35 | 10 | 613.5 |  | 1221.4348 | 2578.9348 |  | 15 |  | 744 | 1 Elec | 61.35 | 16.5 | 1012.275 |  | 1870.2277 | 3626.5027 |  | 744 | 1 Elec | 61.35 | 10 | 613.5 |  | 1221.4348 |  | 2578.9348 | 0 | 15 |  | 744 | 1 Elec | 61.35 | 16.5 | 1012.275 |  | 1870.2277 | 3626.5027 | 0
[19 empty] | ABB |  |  | 5 | [5 empty] | 5 |  |  |  |  | 1.246 | 954 | 1 Elec | 61.35 | 10 | 613.5 |  | 1399.0056 | 2966.5056 |  | 15 |  | 954 | 1 Elec | 61.35 | 16.5 | 1012.275 |  | 2086.5556 | 4052.8306 |  | 954 | 1 Elec | 61.35 | 10 | 613.5 |  | 1399.0056 |  | 2966.5056 | 0 | 15 |  | 954 | 1 Elec | 61.35 | 16.5 | 1012.275 |  | 2086.5556 | 4052.8306 | 0
[19 empty] | ABB |  |  | 10 | [5 empty] | 10 |  |  |  |  | 1.246 | 1300 | 1 Elec | 61.35 | 11.94 | 732.519 |  | 1806.4861 | 3839.0051 |  | 15 |  | 1300 | 1 Elec | 61.35 | 19.701 | 1208.6563 |  | 2657.1204 | 5165.7768 |  | 1300 | 1 Elec | 61.35 | 11.94 | 732.519 |  | 1806.4861 |  | 3839.0051 | 0 | 15 |  | 1300 | 1 Elec | 61.35 | 19.701 | 1208.6563 |  | 2657.1204 | 5165.7768 | 0
[19 empty] | ABB |  |  | 20 | [5 empty] | 20 |  |  |  |  | 1.246 | 2159 | 2 Elec | 61.35 | 17.8 | 1092.03 |  | 2879.9387 | 6130.9687 |  | 15 |  | 2159 | 2 Elec | 61.35 | 29.37 | 1801.8495 |  | 4188.8365 | 8149.686 |  | 2159 | 2 Elec | 61.35 | 17.8 | 1092.03 |  | 2879.9387 |  | 6130.9687 | 0 | 15 |  | 2159 | 2 Elec | 61.35 | 29.37 | 1801.8495 |  | 4188.8365 | 8149.686 | 0
[19 empty] | ABB |  |  | 50 | [5 empty] | 50 |  |  |  |  | 1.246 | 4113 | 2 Elec | 61.35 | 30.189 | 1852.0952 |  | 5266.0264 | 11231.1216 |  | 15 |  | 4113 | 2 Elec | 61.35 | 49.8118 | 3055.957 |  | 7569.2247 | 14738.1817 |  | 4113 | 2 Elec | 61.35 | 30.189 | 1852.0952 |  | 5266.0264 |  | 11231.1216 | 0 | 15 |  | 4113 | 2 Elec | 61.35 | 49.8118 | 3055.957 |  | 7569.2247 | 14738.1817 | 0
[19 empty] | ABB |  |  | 75 | [5 empty] | 75 |  |  |  |  | 1.246 | 6660 | R-3 | 61.12 | 35.174 | 2149.8349 |  | 7707.1706 | 16517.0055 |  | 15 |  | 6660 | R-3 | 61.12 | 58.0371 | 3547.2276 |  | 10728.666 | 20935.8935 |  | 6660 | R-3 | 61.12 | 35.174 | 2149.8349 |  | 7707.1706 |  | 16517.0055 | 0 | 15 |  | 6660 | R-3 | 61.12 | 58.0371 | 3547.2276 |  | 10728.666 | 20935.8935 | 0
[19 empty] | ABB |  |  | 100 | [5 empty] | 100 |  |  |  |  | 1.246 | 7758 | R-3 | 61.12 | 40 | 2444.8 |  | 8920.3975 | 19123.1975 |  | 15 |  | 7758 | R-3 | 61.12 | 66 | 4033.92 |  | 12390.4528 | 24182.3728 |  | 7758 | R-3 | 61.12 | 40 | 2444.8 |  | 8920.3975 |  | 19123.1975 | 0 | 15 |  | 7758 | R-3 | 61.12 | 66 | 4033.92 |  | 12390.4528 | 24182.3728 | 0
90.1-07bw | 6. HVAC |  | PTAC Efficiency | [12 empty] | PTAC_Efficiency | PTAC Adjustments for load changes resulting in capacity changes. 90.1-2013 and 90.1-2016 have the same efficiency requirements. | Equipment information below. Labor from RS Means 2014 Mechanical Cost Data. 28 81 13 - Packaged Terminal Air Conditioners 23 81 13.10 0220 |  |  |  |  | PTAC, 9,000 Btu/hr, minimum efficiency 11.3 EER
PTAC_Efficiency
[8 empty] | X |  | X | X | X | X | X |  |  | Two similar units, 9,000 Bthuh, electric heat, EER 11.3 | http://www.ptacunits.com | Amana | PTC094G25AXXX, PTC094G35AXXX |  | Each | Two similar units, 9,000 Bthuh, electric heat, EER 11.5 | www.ptacunits.com | Amana | PTC093G25AXXX, PTC093G35AXXX |  | Each |  |  |  |  | 1 | 704 | Q5 | 59 | 3.2 | 188.8 |  | 521.0489 | 1413.8489 |  | 15 |  | 704 | Q5 | 59 | 5.28 | 311.52 |  | 782.7302 | 1798.2502 |  | 739 | Q5 | 59 | 3.2 | 188.8 |  | 537.8909 | 0 | 1465.6909 | 0 | 15 |  | 739 | Q5 | 59 | 5.28 | 311.52 |  | 804.7564 | 1855.2764 | 51.842
[16 empty] | N. Carolina hotel room HVAC control N. Carolina amendment | Base code for North Carolina only includes exception for automatic shutdown for hotel rooms. Base code model includes this type of control, assumed to be implemented with an occupancy sensor. Therefore, a credit for the cost of occupancy sensor control is provided. Need to add cost - see \\korea\comstd\90.1_IECC_ State_Cost_Eff\Costs and Cost-Effectiveness\HVAC\hotel guest room on-off control | PNNL staff experience |  |  |  |  | No cost or credit. | [36 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
[16 empty] | NC_hotel_HVAC | [43 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
90.1-07n and 90.1-07ca | 6. HVAC | 6.4.3.10 | Single zone fan speed control | [12 empty] | Singe Zone Fan Speed Control When capacity change creates change in requirement | Constant volume single zone DX units serve some individual zones in the prototypes. Base costs are included above. Sometimes with a change in capacity; the system may no longer require multiple speed fans or multiple stage compressors. | [5 empty] | Addendum AQ added fan control and staging requirements. For single zone control units; conversion is to a 2 speed fan, and addition of one stage of cooling. There are additional economizer integration requirements, but they are related to settings and configuration of the controller, and there are no incremental costs once the market adapts to the requirements. Requirements are applied as follows: All DX units over 65 MBH: add a stage of cooling. All single zone units over 65 MBH: add 2 speed fan control. All DX units serving multiple zones: add VSD fan. | Incremental cost is based on data gathered from manufacturers by AHRI and presented in a composite fashion at ASHRAE 90.1 SSPC.
Add 2 speed fan y = 6.458x + 206.12
[24 empty] | Cf_Fan2spd_I | 206.12 |  |  | tons
[24 empty] | Cf_Fan2spd_x | 6.458 |  |  | tons
[23 empty] | Add cooling stage: y = 51.075x - 44.585 |  |  |  |  | tons
[24 empty] | cf_CoolStage_I | -44.585 |  |  | tons
[24 empty] | cf_CoolStage_x | 51.075 |  |  | tons
90.1-07h | 6. HVAC | 6.5.2.1 exc. b. | VAV dual minimum damper control | [12 empty] | VAV Dual Minimum Damper Control 90.1-07h Note: Item includes no added costs as explained in description. | This addendum applies to multi-zone VAV systems. 90.1-07 models use standard VAV terminal unit damper control with a fixed minimum for cooling, with reheat operating only at this minimum position. DDC control of terminal units is included in the base case. No added cost. | Faithful+Gould, Solarc |  |  |  |  | The addendum allows the option of a dual minimum damper control with modulated heating airflow. The minimum is 20% when in reheat/recool or in deadband (or minimum required to meet ventilation requirement). The minimum is 50% when in reheat/recool or mixed mode when in peak heating, and airflow in heating and cooling outside of deadband shall be modulated to meet the load. No added costs are identified: terminal units selected for base case are capable of dual minimum. (90.1-2007 baseline assumed to have DDC control. | Faithful+Gould, Solarc | [8 empty] | 1
90.1-07bh | 6. HVAC | 6.5.3.4 | Supply air temperature reset | [12 empty] | Supply Air Temperature Reset 90.1-07bh | This addendum applies to multi-zone VAV systems. 90.1-07 models use standard VAV temperature controls with a supply air temperature of 55°F. Base cost for these systems is accounted for under the general HVAC capacity costs above. | [5 empty] | The addendum requires supply air temperature reset for multi-zone VAV systems. Supply air temperature is reset to at least 25% of the difference between the design supply air temperature and the design room air temperature (in prototype this is a reset from 55°F at full load, to 60°F at low load (based on outdoor air temperature (OAT)), Setting it up uses 4 inputs, e.g. 55°F at 70°F OAT; 60°F at 30°F OAT. Zones that experience relatively constant loads (core with consistent occupancy, etc.) require design for the air supply based on the reset supply air temperature instead of the higher OAT supply air temperature. The codes require that zones which experience relatively constant loads be designed to meet the load at the fully reset supply air temperature. The 90.1 MSC used an estimate of $0.19 per square foot of interior building area served by HVAC systems affected by the control requirement to account for increased air distribution equipment compared to VAV system air distribution without this requirement. Cost is shown as total cost, and is assumed to have a 20 year life like ductwork costs for replacement cost Area affected assumed to be portion of core area of open office type excluding top floor determined to be 98,600 ft2. There is also incremental cost for programming and commissioning added to the HVAC system cost developed above, for the 2010 case, with supply air temperature reset added. | Solarc commissioning estimate. This is consistent with information received from members of the 90.1 mechanical subcommittee and Faithful+Gould, and Solarc. | [8 empty] | 1
[16 empty] | Supply_Air_Temp_Reset | [16 empty] | 1
[23 empty] | 4 hours of programming, and 4 hours of commissioning per system | Solarc | [8 empty] | 1 | [21 empty] | Programming | 125 | 4 | 500 |  | 482.744 |  | 982.744 |  |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 982.744
[23 empty] | Large office additional ductwork and other system costs for design at reset temperature. | prototype model for area, 90.1 MSC for cost/area | [8 empty] | 1 | [26 empty] | 0 |  | 18734 |  | 20 |  | 0 |  |  |  | 0 |  | 0 | 18734 | 18734
90.1-16ap | [15 empty] | Supply Air Temperature Reset 90.1-16ap | base case exempts 0A, 1A, 2A, 3A thus costs = 0 |  | Material cost = 4E-07x2 + 0.0307x + 1618 | where x = SA cfm |  | Supply airflow, cfm | only 0A, 1A, 2A, 3A MZ systems only <3000 cfm design OA is exempt only large office and primary school
[16 empty] | SAT_reset_16ap |  |  | Labor hours = 0.0054x + 3.6055 | where x = SA cfm
90.1-07ck | 6. HVAC | 6.5.3.3 | VAV system ventilation optimization | [12 empty] | VAV System Ventilation Optimization | 2013 baseline includes VAV optimized outside airflow based on the ASHRAE 62.1 ventilation requirements for multi-zone systems, except where excepted for DCV. 2016 VAV systems required to have ventilation optimization to meet 62.1 outside air requirements, wven where ERV is required. | [5 empty] | Under 90.1-2010 multi-zone VAV systems are required to provide control to automatically reduce outdoor intake flow below the maxium design outdoor airflow in response to changes in system ventilation efficiency as defined by the multi-zone requirements in Standard 62.1. The VAV systems modeled are assumed to have DDC control of zone dampers and outdoor airflow sensors in the AHU or RTU in order to meet other provisions of Standard 90.1 and requirements under Stanadard 62.1. With this equipment already in place, costs are limited to programming and checkout/commissioning. Costs include 30 minutes programming for each perimeter zone, and 1 hour (2 people 30 minutes each) for commissioning per perimeter zone. The number of perimeter zones is based on the ductwork layout prepared by the mechanical engineering consultant described under Duct Work and Zone Air Distribution costs above. Large office has 12 perimeter zones per floor, 12 floors total (basement is served by constant volume systems). Primary school has 28 perimeter zones served by variable air volume. | Solarc commissioning estimate. This is consistent but not identical with information received from members of the 90.1 mechanical subcommittee and Faithful+Gould, and Solarc. | [8 empty] | 1 | [38 empty] | 0
[16 empty] | Vent_Optimize | [6 empty] | Costs applied based on the number of perimeter zones for each affected prototype system. | [9 empty] | 1.122 | [26 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
[33 empty] | 1.122 |  | Programming | 125 | 0.5 | 62.5 |  | 60.343 | 122.843 |  |  |  | 0 |  |  | 0.825 |  |  | 0 |  |  |  | Programming | 125 | 0.5 | 62.5 |  | 60.343 |  | 122.843 |  |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0
[16 empty] | VAV Fan Control Type Threshold 2009 to 2012 IECC Primary school only | Fan motor horsepower 10 hp and greater requires VFD. Costs shown for base are zero. Costs shown for target are incremental cost for going from non-VFD <inlet vanes?> to VFD. | [5 empty] | Fan motor hp 7.5 hp and greater requires VFD. Costs shown for target are incremental cost for going from non-VFD <inlet vanes?> to VFD. Cost added if fan nameplate motor hp equals 7.5 hp. Applies for IECC 2009 or 90.1-2007 to IECC 2012 | [9 empty] | 1 | [11 empty] | 0 | [5 empty] | 0 | [8 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
[16 empty] | VAV_fan_control | [6 empty] | Incremental cost for non-VFD <inlet vanes> to VFD fan motor control at 7.5 hp motor | [9 empty] | 1 | [11 empty] | 0 | [5 empty] | 0 | [8 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
90.1-16a | 6. HVAC | 6.4.3.4.2 and 6.4.3.4.3 | Automatic dampers | X |  | X | X | [8 empty] | Automatic Outdoor Air Dampers 90.1-16a | Return dampers are NOT required to be low leakage Maintenance: Carnes, online http://www.carnes.com/ventilation/pdf/1511.pdf http://www.nextag.com/replacement-damper-motor/products-html RS Means Facilities Maintenance and Repair 2004 Guidebook for labor hours - unit heater motor replacement labor hours. | Equipment information below. Labor from RS Means 2012 Mechanical Cost Data. 23 33 13 Dampers. Multi-blade opposed blade 23.33.13.13 (motorized 7500+) Prices adjusted to 2020$ |  |  |  | Outside Airflow, cfm | Return dampers ARE required to be low leakage | major manufacturer of return air dampers |  |  |  | Outside Airflow, cfm |  |  |  |  | 1 | [38 empty] | 0
0
[16 empty] | Outdoor_ Air_ Dampers | [49 empty] | 0 | [5 empty] | 0
[17 empty] | Gravity outdoor intake dampers | Faithful+Gould from Honeywell representative | 8" x 6" | A2OAB006006NAA |  | 50 | Same as the 90.1-2007 |  |  |  |  | 50 |  |  |  |  | 1.146 | 144.82 | 1 Shee | 62.3 | 0.333 | 20.7459 |  | 121.0354 | 286.6013 | 95.5213 | 20 |  | 144.82 | 1 Shee | 62.3 | 0.54945 | 34.2307 |  | 128.4641 | 307.5149 |  | 159.302 | 1 Shee | 62.3 | 0.333 | 20.7459 |  | 131.1359 |  | 311.1838 | 95.5213 | 20 |  | 159.302 | 1 Shee | 62.3 | 0.54945 | 34.2307 |  | 175.4728 | 369.0056 | 24.5825
[19 empty] | 8" x 8" | A2OAB008008NAA |  | 100 | [5 empty] | 100 |  |  |  |  | 1.146 | 144.82 | 1 Shee | 62.3 | 0.364 | 22.6772 |  | 122.9 | 290.3972 | 96.1951 | 20 |  | 144.82 | 1 Shee | 62.3 | 0.6006 | 37.4174 |  | 131.9389 | 314.1763 |  | 159.302 | 1 Shee | 62.3 | 0.364 | 22.6772 |  | 133.0006 |  | 314.9798 | 96.1951 | 20 |  | 159.302 | 1 Shee | 62.3 | 0.6006 | 37.4174 |  | 178.9476 | 375.667 | 24.5825
[19 empty] | 10" x 10" | A2OAB0010010NAA |  | 250 | Cost premium = |  |  |  |  | 250 |  |  |  |  | 1.146 | 144.82 | 1 Shee | 62.3 | 0.382 | 23.7986 |  | 123.9827 | 292.6013 | 96.8689 | 20 |  | 144.82 | 1 Shee | 62.3 | 0.6303 | 39.2677 |  | 133.9566 | 318.0442 |  | 159.302 | 1 Shee | 62.3 | 0.382 | 23.7986 |  | 134.0833 |  | 317.1839 | 96.8689 | 20 |  | 159.302 | 1 Shee | 62.3 | 0.6303 | 39.2677 |  | 180.9652 | 379.5349 | 24.5825
[19 empty] | 12" x 12" | A2OAB0012012NAA |  | 500 | 10% |  |  |  |  | 500 |  |  |  |  | 1.146 | 144.82 | 1 Shee | 62.3 | 0.381 | 23.7363 |  | 123.9226 | 292.4789 | 98.8902 | 20 |  | 144.82 | 1 Shee | 62.3 | 0.62865 | 39.1649 |  | 133.8445 | 317.8294 |  | 159.302 | 1 Shee | 62.3 | 0.381 | 23.7363 |  | 134.0231 |  | 317.0614 | 98.8902 | 20 |  | 159.302 | 1 Shee | 62.3 | 0.62865 | 39.1649 |  | 180.8532 | 379.32 | 24.5825
[19 empty] | 16" x 10" | A2OAB0016010NAA |  | 1000 | [5 empty] | 1000 |  |  |  |  | 1.146 | 152.6 | 1 Shee | 62.3 | 0.444 | 27.6612 |  | 133.1382 | 313.3994 | 102.2592 | 20 |  | 152.6 | 1 Shee | 62.3 | 0.7326 | 45.641 |  | 145.8023 | 344.0432 |  | 167.86 | 1 Shee | 62.3 | 0.444 | 27.6612 |  | 143.7814 |  | 339.3026 | 102.2592 | 20 |  | 167.86 | 1 Shee | 62.3 | 0.7326 | 45.641 |  | 195.3363 | 408.8373 | 25.9032
[19 empty] | 18" x 16" | A2OAB0018016NAA |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1.146 | 188.56 | 1 Shee | 62.3 | 0.533 | 33.2059 |  | 163.5721 | 385.338 | 108.997 | 20 |  | 188.56 | 1 Shee | 62.3 | 0.87945 | 54.7897 |  | 178.4086 | 421.7584 |  | 207.416 | 1 Shee | 62.3 | 0.533 | 33.2059 |  | 176.7233 |  | 417.3452 | 108.997 | 20 |  | 207.416 | 1 Shee | 62.3 | 0.87945 | 54.7897 |  | 239.6153 | 501.8211 | 32.0072
[19 empty] | 28" x 16" | A2OAB0028016NAA |  | 3000 | [5 empty] | 3000 |  |  |  |  | 1.146 | 254.66 | 1 Shee | 62.3 | 0.615 | 38.3145 |  | 214.6061 | 507.5806 | 122.4727 | 20 |  | 254.66 | 1 Shee | 62.3 | 1.0148 | 63.2189 |  | 229.1981 | 547.077 |  | 280.126 | 1 Shee | 62.3 | 0.615 | 38.3145 |  | 232.3675 |  | 550.808 | 122.4727 | 20 |  | 280.126 | 1 Shee | 62.3 | 1.0148 | 63.2189 |  | 311.8609 | 655.2058 | 43.2274
[19 empty] | 24" x 24" | pro-rated |  | 4000 | [5 empty] | 4000 |  |  |  |  | 1.146 | 298.596 | 1 Shee | 62.3 | 1 | 62.3 |  | 268.4072 | 629.3032 | 135.9484 | 20 |  | 298.596 | 1 Shee | 62.3 | 1.65 | 102.795 |  | 300.0026 | 701.3936 |  | 328.4556 | 1 Shee | 62.3 | 1 | 62.3 |  | 289.233 |  | 679.9886 | 135.9484 | 20 |  | 328.4556 | 1 Shee | 62.3 | 1.65 | 102.795 |  | 396.9271 | 828.1777 | 50.6853
[19 empty] | 30" x 30" | pro-rated |  | 7000 | [5 empty] | 7000 |  |  |  |  | 1.146 | 463.65 | 1 Shee | 62.3 | 2.424 | 151.0152 |  | 469.1785 | 1083.8437 | 149.4241 | 20 |  | 463.65 | 1 Shee | 62.3 | 3.9996 | 249.1751 |  | 563.4907 | 1276.3158 |  | 510.015 | 1 Shee | 62.3 | 2.424 | 151.0152 |  | 501.516 |  | 1162.5462 | 149.4241 | 20 |  | 510.015 | 1 Shee | 62.3 | 3.9996 | 249.1751 |  | 713.9919 | 1473.1819 | 78.7025
[19 empty] | 36" x 36" | pro-rated |  | 10000 | [5 empty] | 10000 |  |  |  |  | 1.146 | 620.3925 | 1 Shee | 62.3 | 2.667 | 166.1541 |  | 593.1158 | 1379.6624 | 189.8512 | 20 |  | 620.3925 | 1 Shee | 62.3 | 4.4005 | 274.1543 |  | 689.3698 | 1583.9166 |  | 682.4317 | 1 Shee | 62.3 | 2.667 | 166.1541 |  | 636.3854 |  | 1484.9712 | 189.8512 | 20 |  | 682.4317 | 1 Shee | 62.3 | 4.4005 | 274.1543 |  | 890.7497 | 1847.3357 | 105.3088
[19 empty] | 56" x 36" | pro-rated |  | 14000 | [5 empty] | 14000 |  |  |  |  | 1.146 | 834.9235 | 1 Shee | 62.3 | 2.963 | 184.5949 |  | 760.5459 | 1780.0643 | 230.2783 | 20 |  | 834.9235 | 1 Shee | 62.3 | 4.889 | 304.5816 |  | 857.5571 | 1997.0622 |  | 918.4158 | 1 Shee | 62.3 | 2.963 | 184.5949 |  | 818.7781 |  | 1921.7888 | 230.2783 | 20 |  | 918.4158 | 1 Shee | 62.3 | 4.889 | 304.5816 |  | 1128.574 | 2351.5714 | 141.7245
[33 empty] | 1.146 | [26 empty] | 0 | [11 empty] | 0
[17 empty] | Motorized return air dampers not low leakage | Faithful+Gould from Honeywell representative |  | ZD6x6 |  | 50 | Motorized return air dampers Motorized with class II Leakage, 3 V blade w/seals, opposed galvanized frame, w/ galvanized linkages & axles, Acetal Bearings/Vinyl Seal. One manufacturer only | major damper manufacturer |  |  |  | 50 |  |  |  |  | 1.146 | 314.06 | 1 Shee | 62.3 | 0.533 | 33.2059 |  | 251.1027 | 598.3686 | 95.5213 | 20 |  | 314.06 | 1 Shee | 62.3 | 0.87945 | 54.7897 |  | 257.3883 | 626.238 |  | 361.169 | 1 Shee | 62.3 | 0.533 | 33.2059 |  | 283.9591 |  | 678.334 | 95.5213 | 20 |  | 361.169 | 1 Shee | 62.3 | 0.87945 | 54.7897 |  | 372.9501 | 788.9088 | 79.9654
[20 empty] | ZD8X8 |  | 100 | [5 empty] | 100 |  |  |  |  | 1.146 | 321.11 | 1 Shee | 62.3 | 0.571 | 35.5733 |  | 258.3054 | 614.9887 | 96.1951 | 20 |  | 321.11 | 1 Shee | 62.3 | 0.94215 | 58.6959 |  | 266.0844 | 645.8904 |  | 369.2765 | 1 Shee | 62.3 | 0.571 | 35.5733 |  | 291.8994 |  | 696.7492 | 96.1951 | 20 |  | 369.2765 | 1 Shee | 62.3 | 0.94215 | 58.6959 |  | 384.2403 | 812.2128 | 81.7605
[20 empty] | ZD10X10 |  | 250 | [5 empty] | 250 |  |  |  |  | 1.146 | 342.01 | 1 Shee | 62.3 | 0.615 | 38.3145 |  | 275.5288 | 655.8533 | 96.8689 | 20 |  | 342.01 | 1 Shee | 62.3 | 1.0148 | 63.2189 |  | 284.1692 | 689.3981 |  | 393.3115 | 1 Shee | 62.3 | 0.615 | 38.3145 |  | 311.3093 |  | 742.9353 | 96.8689 | 20 |  | 393.3115 | 1 Shee | 62.3 | 1.0148 | 63.2189 |  | 410.0154 | 866.5459 | 87.082
[20 empty] | ZD12X12 |  | 500 | [5 empty] | 500 |  |  |  |  | 1.146 | 352.42 | 1 Shee | 62.3 | 0.667 | 41.5541 |  | 285.9171 | 679.8912 | 98.8902 | 20 |  | 352.42 | 1 Shee | 62.3 | 1.1005 | 68.5643 |  | 296.5491 | 717.5333 |  | 405.283 | 1 Shee | 62.3 | 0.667 | 41.5541 |  | 322.7867 |  | 769.6238 | 98.8902 | 20 |  | 405.283 | 1 Shee | 62.3 | 1.1005 | 68.5643 |  | 426.2258 | 900.0731 | 89.7326
[20 empty] | ZD16X10 |  | 1000 | [5 empty] | 1000 |  |  |  |  | 1.146 | 370.71 | 1 Shee | 62.3 | 0.667 | 41.5541 |  | 298.6736 | 710.9377 | 102.2592 | 20 |  | 370.71 | 1 Shee | 62.3 | 1.1005 | 68.5643 |  | 308.0593 | 747.3336 |  | 426.3165 | 1 Shee | 62.3 | 0.667 | 41.5541 |  | 337.4566 |  | 805.3272 | 102.2592 | 20 |  | 426.3165 | 1 Shee | 62.3 | 1.1005 | 68.5643 |  | 444.4661 | 939.3469 | 94.3895
[20 empty] | ZD18X16 |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1.146 | 428.16 | 1 Shee | 62.3 | 0.889 | 55.3847 |  | 352.0957 | 835.6404 | 108.997 | 20 |  | 428.16 | 1 Shee | 62.3 | 1.4668 | 91.3848 |  | 369.0978 | 888.6425 |  | 492.384 | 1 Shee | 62.3 | 0.889 | 55.3847 |  | 396.889 |  | 944.6577 | 108.997 | 20 |  | 492.384 | 1 Shee | 62.3 | 1.4668 | 91.3848 |  | 526.6439 | 1110.4126 | 109.0174
[20 empty] | ZD28X16 |  | 3000 | Cost premium = |  |  |  |  | 3000 |  |  |  |  | 1.146 | 509.09 | 1 Shee | 62.3 | 1.333 | 83.0459 |  | 435.2473 | 1027.3832 | 122.4727 | 20 |  | 509.09 | 1 Shee | 62.3 | 2.1995 | 137.0257 |  | 469.7967 | 1115.9124 |  | 585.4535 | 1 Shee | 62.3 | 1.333 | 83.0459 |  | 488.5074 |  | 1157.0068 | 122.4727 | 20 |  | 585.4535 | 1 Shee | 62.3 | 2.1995 | 137.0257 |  | 657.1218 | 1379.6011 | 129.6236
[20 empty] | ZD28X20 |  | 4000 | 15% |  |  |  |  | 4000 |  |  |  |  | 1.146 | 558.68 | 1 Shee | 62.3 | 1.4665 | 91.3629 |  | 477.8641 | 1127.9071 | 135.9484 | 20 |  | 558.68 | 1 Shee | 62.3 | 2.4197 | 150.7489 |  | 515.9687 | 1225.3975 |  | 642.482 | 1 Shee | 62.3 | 1.4665 | 91.3629 |  | 536.3122 |  | 1270.1572 | 135.9484 | 20 |  | 642.482 | 1 Shee | 62.3 | 2.4197 | 150.7489 |  | 721.541 | 1514.7719 | 142.2501
[19 empty] | 30" x 30" | pro-rated |  | 7000 | [5 empty] | 7000 |  |  |  |  | 1.146 | 707.45 | 1 Shee | 62.3 | 2.21 | 137.683 |  | 626.346 | 1471.479 | 149.4241 | 20 |  | 707.45 | 1 Shee | 62.3 | 3.6465 | 227.177 |  | 692.9316 | 1627.5586 |  | 813.5675 | 1 Shee | 62.3 | 2.21 | 137.683 |  | 700.3582 |  | 1651.6087 | 149.4241 | 20 |  | 813.5675 | 1 Shee | 62.3 | 3.6465 | 227.177 |  | 953.2455 | 1993.99 | 180.1297
[19 empty] | 36" x 36" | pro-rated |  | 10000 | [5 empty] | 10000 |  |  |  |  | 1.146 | 856.22 | 1 Shee | 62.3 | 2.32 | 144.536 |  | 736.7229 | 1737.4789 | 189.8512 | 20 |  | 856.22 | 1 Shee | 62.3 | 3.828 | 238.4844 |  | 798.8855 | 1893.5899 |  | 984.653 | 1 Shee | 62.3 | 2.32 | 144.536 |  | 826.2991 |  | 1955.4881 | 189.8512 | 20 |  | 984.653 | 1 Shee | 62.3 | 3.828 | 238.4844 |  | 1113.9409 | 2337.0783 | 218.0093
[19 empty] | 48" x 48" | pro-rated |  | 14000 | [5 empty] | 14000 |  |  |  |  | 1.146 | 1054.58 | 1 Shee | 62.3 | 2.667 | 166.1541 |  | 895.9421 | 2116.6762 | 230.2783 | 20 |  | 1054.58 | 1 Shee | 62.3 | 4.4005 | 274.1543 |  | 962.6127 | 2291.3469 |  | 1212.767 | 1 Shee | 62.3 | 2.667 | 166.1541 |  | 1006.2704 |  | 2385.1915 | 230.2783 | 20 |  | 1212.767 | 1 Shee | 62.3 | 4.4005 | 274.1543 |  | 1350.6568 | 2837.5781 | 268.5153
90.1-07cy | 6. HVAC | 6.5.1 | Economizers | X |  | X | X | [8 empty] | Economizer 90.1-07cy | The 90.1-2007 costs entered include economizers at the same cost as for 90.1-2010 costs. Under 90.l-2007 some systems are not required to have economizers. Increased costs will occur when the costs are applied to the prototypes when economizers are not required under 90.1-2007, but are required under 90.1- 2010. Maintenance - Verification that the economizer opens, closes, and appears to function properly using cold spray or ice on the outside air sensor. Estimated 45 minutes. To allow for periodic actuator replacement, an additonal 30 minutes is added annually, as well as $25 for a portion of the actuator cost. A web search showed costs in the $50 to $100 range for actuators. Since entire economizers are replaced, not repaired, at typical life, assuming motor replacement costs are accounted for. Adding 5 minutes and $5 for material per 1000 cfm above 1000 cfm. | Equipment from cost estimator estimate with some size units from supplier. Labor estimated approximately from motorized damper costs from RS Means 2012 Mechanical Cost Data. 23 33 13 Dampers. Multi-blade opposed blade 23.33.13.13 (gravity 5990+, motorized 7500+) Maintenance PNNL staff, prior experience with an energy services and commissioning firm. http://www.nextag.com/replacement-damper-motor/products-html RS Means Facilities Maintenance and Repair Guidebook - unit heater motor replacement labor hours. | Faithful and Gould, Aireco representative estimate from some Carrier units |  |  | supply airflow, cfm | Addendum 90.1-07cy adds economizer requirements for climate zones 1a, 2a, 3a, 4a, as shown in 90.1-2010, Table 6.5.1A, Economizers are added in some cases for the climate zone and system types where the new cooling capacity thresholds are lowered under Table 6.5.1A in 90.1-2010. Other provisions require integrated vs. non-integrated economizers, but as noted under the 90.1-2007 case, no costs were identified for this. Costs shown apply to both AHU and DX system economizers, and are added to the base system cost. Costs are the same for sytems for 90.1-2007 and 90.1-2010 for systems that have an economizer. |  | same as for 90.1-2007 | same as for 90.1-2007 |  | supply airflow, cfm |  |  |  |  | 1.146 | [38 empty] | 0
[16 empty] | AHU_Economizer |  | Faithful+Gould | [7 empty] | Aireco - Carrier (pro rated- 3T) |  | SA cfm |  |  |  |  | 1.146 | Mat$ |  |  |  | Lab$ | [33 empty] | 0
[17 empty] | Air-side economizer suitable for an AHU. | Aireco - rep | Carrier | Series 39M |  | 50 |  | Aireco - rep | Carrier | Series 39M |  | 50 |  |  |  |  | 1.146 | 600 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 448.518 | 1079.6368 | 161.5385 | 15 |  | 600 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 433.581 | 1084.9271 |  | 600 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 448.518 |  | 1079.6368 | 161.5385 | 15 |  | 600 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 576.3095 | 1227.6556 | 0
[20 empty] | 3T |  | 100 |  |  |  | 3T |  | 100 |  |  |  |  | 1.146 | 700 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 518.2635 | 1249.3824 | 162.0299 | 15 |  | 700 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 496.513 | 1247.8591 |  | 700 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 518.2635 |  | 1249.3824 | 162.0299 | 15 |  | 700 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 663.0295 | 1414.3756 | 0
[16 empty] | These apply to computer rooms |  |  |  | (pro rated- 3T) |  | 250 |  | Vendor indicated costs varied directly with outdoor airflow in proportion to 100 cfm and 1000 cfm units up to 5,000 cfm. Cost estimator estimated larger sizes. |  | (pro rated- 3T) |  | 250 |  |  |  |  | 1.146 | 800 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 588.009 | 1419.1279 | 163.504 | 15 |  | 800 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 559.445 | 1410.7911 |  | 800 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 588.009 |  | 1419.1279 | 163.504 | 15 |  | 800 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 749.7496 | 1601.0957 | 0
[16 empty] | 90.1-13 i |  | Vendor indicated costs varied directly with outdoor airflow in proportion to 100 cfm and 1000 cfm units up to 5,000 cfm. Cost estimator estimated larger sizes. |  | (pro rated- 3T) |  | 500 |  |  |  | (pro rated- 3T) |  | 500 |  |  |  |  | 1.146 | 950 | 1 Shee | 62.3 | 0.5715 | 35.6044 |  | 696.9581 | 1682.5626 | 165.9609 | 15 |  | 950 | 1 Shee | 62.3 | 0.94298 | 58.7473 |  | 887.9002 | 1896.6475 |  | 950 | 1 Shee | 62.3 | 0.5715 | 35.6044 |  | 696.9581 |  | 1682.5626 | 165.9609 | 15 |  | 950 | 1 Shee | 62.3 | 0.94298 | 58.7473 |  | 887.9002 | 1896.6475 | 0
[20 empty] | (pro rated- 3T) |  | 1000 |  |  |  | (pro rated- 3T) |  | 1000 |  |  |  |  | 1.146 | 1350 | 1 Shee | 62.3 | 0.666 | 41.4918 |  | 981.6244 | 2373.1162 | 170.8746 | 15 |  | 1350 | 1 Shee | 62.3 | 1.0989 | 68.4615 |  | 1245.373 | 2663.8345 |  | 1350 | 1 Shee | 62.3 | 0.666 | 41.4918 |  | 981.6244 |  | 2373.1162 | 170.8746 | 15 |  | 1350 | 1 Shee | 62.3 | 1.0989 | 68.4615 |  | 1245.373 | 2663.8345 | 0
[20 empty] | (pro rated- 3T) |  | 2000 |  |  |  | (pro rated- 3T) |  | 2000 |  |  |  |  | 1.146 | 1805 | 1 Shee | 62.3 | 0.7995 | 49.8088 |  | 1306.9965 | 3161.8053 | 180.7021 | 15 |  | 1805 | 1 Shee | 62.3 | 1.3192 | 82.1846 |  | 1654.9134 | 3542.098 |  | 1805 | 1 Shee | 62.3 | 0.7995 | 49.8088 |  | 1306.9965 |  | 3161.8053 | 180.7021 | 15 |  | 1805 | 1 Shee | 62.3 | 1.3192 | 82.1846 |  | 1654.9134 | 3542.098 | 0
[20 empty] | (pro rated- 3T) |  | 3000 |  |  |  | (pro rated- 3T) |  | 3000 |  |  |  |  | 1.146 | 2137.5 | 1 Shee | 62.3 | 0.9225 | 57.4718 |  | 1546.2988 | 3741.2705 | 190.5295 | 15 |  | 2137.5 | 1 Shee | 62.3 | 1.5221 | 94.8284 |  | 1957.0447 | 4189.3731 |  | 2137.5 | 1 Shee | 62.3 | 0.9225 | 57.4718 |  | 1546.2988 |  | 3741.2705 | 190.5295 | 15 |  | 2137.5 | 1 Shee | 62.3 | 1.5221 | 94.8284 |  | 1957.0447 | 4189.3731 | 0
[20 empty] | (pro rated- 3T) |  | 4000 |  |  |  | (pro rated- 3T) |  | 4000 |  |  |  |  | 1.146 | 2850 | 1 Shee | 62.3 | 1.0455 | 65.1346 |  | 2050.634 | 4965.7687 | 200.3569 | 15 |  | 2850 | 1 Shee | 62.3 | 1.7251 | 107.4722 |  | 2588.7123 | 5546.1845 |  | 2850 | 1 Shee | 62.3 | 1.0455 | 65.1346 |  | 2050.634 |  | 4965.7687 | 200.3569 | 15 |  | 2850 | 1 Shee | 62.3 | 1.7251 | 107.4722 |  | 2588.7123 | 5546.1845 | 0
[20 empty] | (pro rated- 3T) |  | 5000 |  |  |  | (pro rated- 3T) |  | 5000 |  |  |  |  | 1.146 | 3384.375 | 1 Shee | 62.3 | 1.1685 | 72.7976 |  | 2430.7351 | 5887.9077 | 210.1844 | 15 |  | 3384.375 | 1 Shee | 62.3 | 1.928 | 120.116 |  | 3065.9098 | 6570.4007 |  | 3384.375 | 1 Shee | 62.3 | 1.1685 | 72.7976 |  | 2430.7351 |  | 5887.9077 | 210.1844 | 15 |  | 3384.375 | 1 Shee | 62.3 | 1.928 | 120.116 |  | 3065.9098 | 6570.4007 | 0
[20 empty] | cost estimator |  | 6000 |  |  |  | cost estimator |  | 6000 |  |  |  |  | 1.146 | 4061.25 | 1 Shee | 62.3 | 1.2915 | 80.4604 |  | 2910.2235 | 7051.934 | 220.0118 | 15 |  | 4061.25 | 1 Shee | 62.3 | 2.131 | 132.7597 |  | 3666.6833 | 7860.6931 |  | 4061.25 | 1 Shee | 62.3 | 1.2915 | 80.4604 |  | 2910.2235 |  | 7051.934 | 220.0118 | 15 |  | 4061.25 | 1 Shee | 62.3 | 2.131 | 132.7597 |  | 3666.6833 | 7860.6931 | 0
[20 empty] | cost estimator |  | 7000 |  |  |  | cost estimator |  | 7000 |  |  |  |  | 1.146 | 4738.125 | 1 Shee | 62.3 | 1.4145 | 88.1234 |  | 3389.712 | 8215.9603 | 229.8393 | 15 |  | 4738.125 | 1 Shee | 62.3 | 2.3339 | 145.4035 |  | 4267.4569 | 9150.9854 |  | 4738.125 | 1 Shee | 62.3 | 1.4145 | 88.1234 |  | 3389.712 |  | 8215.9603 | 229.8393 | 15 |  | 4738.125 | 1 Shee | 62.3 | 2.3339 | 145.4035 |  | 4267.4569 | 9150.9854 | 0
[20 empty] | cost estimator |  | 10000 |  |  |  | cost estimator |  | 10000 |  |  |  |  | 1.146 | 6410 | 1 Shee | 62.3 | 2.02 | 125.846 |  | 4592.1906 | 11128.0366 | 259.3216 | 15 |  | 6410 | 1 Shee | 62.3 | 3.333 | 207.6459 |  | 5785.1787 | 12402.8246 |  | 6410 | 1 Shee | 62.3 | 2.02 | 125.846 |  | 4592.1906 |  | 11128.0366 | 259.3216 | 15 |  | 6410 | 1 Shee | 62.3 | 3.333 | 207.6459 |  | 5785.1787 | 12402.8246 | 0
[20 empty] | cost estimator |  | 20000 |  |  |  | cost estimator |  | 20000 |  |  |  |  | 1.146 | 12820 | 1 Shee | 62.3 | 4.04 | 251.692 |  | 9184.3813 | 22256.0733 | 357.596 | 15 |  | 12820 | 1 Shee | 62.3 | 6.666 | 415.2918 |  | 11570.3574 | 24805.6492 |  | 12820 | 1 Shee | 62.3 | 4.04 | 251.692 |  | 9184.3813 |  | 22256.0733 | 357.596 | 15 |  | 12820 | 1 Shee | 62.3 | 6.666 | 415.2918 |  | 11570.3574 | 24805.6492 | 0
[20 empty] | cost estimator |  | 30000 |  |  |  | cost estimator |  | 30000 |  |  |  |  | 1.146 | 19230 | 1 Shee | 62.3 | 6.06 | 377.538 |  | 13776.5719 | 33384.1099 | 455.8704 | 15 |  | 19230 | 1 Shee | 62.3 | 9.999 | 622.9377 |  | 17355.5361 | 37208.4738 |  | 19230 | 1 Shee | 62.3 | 6.06 | 377.538 |  | 13776.5719 |  | 33384.1099 | 455.8704 | 15 |  | 19230 | 1 Shee | 62.3 | 9.999 | 622.9377 |  | 17355.5361 | 37208.4738 | 0
[20 empty] | cost estimator |  | 40000 |  |  |  | cost estimator |  | 40000 |  |  |  |  | 1.146 | 25640 | 1 Shee | 62.3 | 8.08 | 503.384 |  | 18368.7625 | 44512.1465 | 554.1448 | 15 |  | 25640 | 1 Shee | 62.3 | 13.332 | 830.5836 |  | 23140.7148 | 49611.2984 |  | 25640 | 1 Shee | 62.3 | 8.08 | 503.384 |  | 18368.7625 |  | 44512.1465 | 554.1448 | 15 |  | 25640 | 1 Shee | 62.3 | 13.332 | 830.5836 |  | 23140.7148 | 49611.2984 | 0
[20 empty] | cost estimator |  | 50000 |  |  |  | cost estimator |  | 50000 |  |  |  |  | 1.146 | 32050 | 1 Shee | 62.3 | 10.1 | 629.23 |  | 22960.9532 | 55640.1832 | 652.4192 | 15 |  | 32050 | 1 Shee | 62.3 | 16.665 | 1038.2295 |  | 28925.8934 | 62014.1229 |  | 32050 | 1 Shee | 62.3 | 10.1 | 629.23 |  | 22960.9532 |  | 55640.1832 | 652.4192 | 15 |  | 32050 | 1 Shee | 62.3 | 16.665 | 1038.2295 |  | 28925.8934 | 62014.1229 | 0
[20 empty] | cost estimator |  | 100000 |  |  |  | cost estimator |  | 100000 |  |  |  |  | 1.146 | 63275.09 | 1 Shee | 62.3 | 17.4688 | 1088.307 |  | 45182.2879 | 109545.6849 | 1143.7912 | 15 |  | 63275.09 | 1 Shee | 62.3 | 28.8235 | 1795.7066 |  | 56830.2851 | 121901.0817 |  | 63275.09 | 1 Shee | 62.3 | 17.4688 | 1088.307 |  | 45182.2879 |  | 109545.6849 | 1143.7912 | 15 |  | 63275.09 | 1 Shee | 62.3 | 28.8235 | 1795.7066 |  | 56830.2851 | 121901.0817 | 0
[16 empty] | DX_Economizer | Economizer | [15 empty] | 1.146 | [11 empty] | 0 | [8 empty] | 0 | [17 empty] | 0
[17 empty] | Air-side economizer suitable for a DX Packaged rooftop unit. | Aireco - rep | Carrier | Series 39M |  | 50 |  | Aireco - rep | Carrier | Carrier (pro rated- 3T) 39M |  | 50 |  |  |  |  | 1.146 | 600 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 448.518 | 1079.6368 | 134.8431 | 15 |  | 600 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 576.3095 | 1227.6556 |  | 600 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 448.518 |  | 1079.6368 | 134.8431 | 15 |  | 600 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 576.3095 | 1227.6556 | 0
[16 empty] | used for load changes |  |  |  | 3T |  | 100 |  |  |  | 3T |  | 100 |  |  |  |  | 1.146 | 700 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 518.2635 | 1249.3824 | 134.8431 | 15 |  | 700 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 663.0295 | 1414.3756 |  | 700 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 518.2635 |  | 1249.3824 | 134.8431 | 15 |  | 700 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 663.0295 | 1414.3756 | 0
[18 empty] | Vendor indicated costs varied directly with outdoor airflow in proportion to 100 cfm and 1000 cfm units up to 5,000 cfm. Cost estimator estimated larger sizes. |  | (pro rated- 3T) |  | 250 |  | Vendor indicated costs varied directly with outdoor airflow in proportion to 100 cfm and 1000 cfm units up to 5,000 cfm. Cost estimator estimated larger sizes. |  | (pro rated- 3T) |  | 250 |  |  |  |  | 1.146 | 800 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 588.009 | 1419.1279 | 134.8431 | 15 |  | 800 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 749.7496 | 1601.0957 |  | 800 | 1 Shee | 62.3 | 0.4995 | 31.1188 |  | 588.009 |  | 1419.1279 | 134.8431 | 15 |  | 800 | 1 Shee | 62.3 | 0.82417 | 51.3461 |  | 749.7496 | 1601.0957 | 0
[20 empty] | (pro rated- 3T) |  | 500 |  |  |  | (pro rated- 3T) |  | 500 |  |  |  |  | 1.146 | 950 | 1 Shee | 62.3 | 0.5715 | 35.6044 |  | 696.9581 | 1682.5626 | 134.8431 | 15 |  | 950 | 1 Shee | 62.3 | 0.94298 | 58.7473 |  | 887.9002 | 1896.6475 |  | 950 | 1 Shee | 62.3 | 0.5715 | 35.6044 |  | 696.9581 |  | 1682.5626 | 134.8431 | 15 |  | 950 | 1 Shee | 62.3 | 0.94298 | 58.7473 |  | 887.9002 | 1896.6475 | 0
[20 empty] | (pro rated- 3T) |  | 1000 |  |  |  | 3T |  | 1000 |  |  |  |  | 1.146 | 1350 | 1 Shee | 62.3 | 0.666 | 41.4918 |  | 981.6244 | 2373.1162 | 134.8431 | 15 |  | 1350 | 1 Shee | 62.3 | 1.0989 | 68.4615 |  | 1245.373 | 2663.8345 |  | 1350 | 1 Shee | 62.3 | 0.666 | 41.4918 |  | 981.6244 |  | 2373.1162 | 134.8431 | 15 |  | 1350 | 1 Shee | 62.3 | 1.0989 | 68.4615 |  | 1245.373 | 2663.8345 | 0
[20 empty] | (pro rated- 3T) |  | 2000 |  |  |  | 3T |  | 2000 |  |  |  |  | 1.146 | 1805 | 1 Shee | 62.3 | 0.7995 | 49.8088 |  | 1306.9965 | 3161.8053 | 148.1301 | 15 |  | 1805 | 1 Shee | 62.3 | 1.3192 | 82.1846 |  | 1654.9134 | 3542.098 |  | 1805 | 1 Shee | 62.3 | 0.7995 | 49.8088 |  | 1306.9965 |  | 3161.8053 | 148.1301 | 15 |  | 1805 | 1 Shee | 62.3 | 1.3192 | 82.1846 |  | 1654.9134 | 3542.098 | 0
[20 empty] | (pro rated- 3T) |  | 3000 |  |  |  | 3T |  | 3000 |  |  |  |  | 1.146 | 2137.5 | 1 Shee | 62.3 | 0.9225 | 57.4718 |  | 1546.2988 | 3741.2705 | 161.4171 | 15 |  | 2137.5 | 1 Shee | 62.3 | 1.5221 | 94.8284 |  | 1957.0447 | 4189.3731 |  | 2137.5 | 1 Shee | 62.3 | 0.9225 | 57.4718 |  | 1546.2988 |  | 3741.2705 | 161.4171 | 15 |  | 2137.5 | 1 Shee | 62.3 | 1.5221 | 94.8284 |  | 1957.0447 | 4189.3731 | 0
[20 empty] | (pro rated- 3T) |  | 4000 |  |  |  | 3T |  | 4000 |  |  |  |  | 1.146 | 2850 | 1 Shee | 62.3 | 0.666 | 41.4918 |  | 2027.8072 | 4919.299 | 174.7042 | 15 |  | 2850 | 1 Shee | 62.3 | 1.0989 | 68.4615 |  | 2546.1741 | 5464.6356 |  | 2850 | 1 Shee | 62.3 | 0.666 | 41.4918 |  | 2027.8072 |  | 4919.299 | 174.7042 | 15 |  | 2850 | 1 Shee | 62.3 | 1.0989 | 68.4615 |  | 2546.1741 | 5464.6356 | 0
[20 empty] | (pro rated- 3T) |  | 5000 |  |  |  | (pro-rated) |  | 5000 |  |  |  |  | 1.146 | 3384.375 | 1 Shee | 62.3 | 1.4145 | 88.1234 |  | 2445.532 | 5918.0303 | 214.5653 | 15 |  | 3384.375 | 1 Shee | 62.3 | 2.3339 | 145.4035 |  | 3093.4839 | 6623.2625 |  | 3384.375 | 1 Shee | 62.3 | 1.4145 | 88.1234 |  | 2445.532 |  | 5918.0303 | 214.5653 | 15 |  | 3384.375 | 1 Shee | 62.3 | 2.3339 | 145.4035 |  | 3093.4839 | 6623.2625 | 0
[20 empty] | cost estimator |  | 6000 |  |  |  | (pro-rated) |  | 6000 |  |  |  |  | 1.146 | 4061.25 | 1 Shee | 62.3 | 2.02 | 125.846 |  | 2954.0427 | 7141.1387 | 214.5653 | 15 |  | 4061.25 | 1 Shee | 62.3 | 3.333 | 207.6459 |  | 3748.341 | 8017.2369 |  | 4061.25 | 1 Shee | 62.3 | 2.02 | 125.846 |  | 2954.0427 |  | 7141.1387 | 214.5653 | 15 |  | 4061.25 | 1 Shee | 62.3 | 3.333 | 207.6459 |  | 3748.341 | 8017.2369 | 0
[20 empty] | cost estimator |  | 7000 |  |  |  | 3T |  | 7000 |  |  |  |  | 1.146 | 4738.125 | 1 Shee | 62.3 | 1.0455 | 65.1346 |  | 3367.5166 | 8170.7763 | 174.7042 | 15 |  | 4738.125 | 1 Shee | 62.3 | 1.7251 | 107.4722 |  | 4226.0956 | 9071.6928 |  | 4738.125 | 1 Shee | 62.3 | 1.0455 | 65.1346 |  | 3367.5166 |  | 8170.7763 | 174.7042 | 15 |  | 4738.125 | 1 Shee | 62.3 | 1.7251 | 107.4722 |  | 4226.0956 | 9071.6928 | 0
[20 empty] | cost estimator |  | 10000 |  |  |  | (pro-rated) |  | 10000 |  |  |  |  | 1.146 | 6410 | 1 Shee | 62.3 | 6.06 | 377.538 |  | 4835.1962 | 11622.7342 | 214.5653 | 15 |  | 6410 | 1 Shee | 62.3 | 9.999 | 622.9377 |  | 6238.0228 | 13270.9605 |  | 6410 | 1 Shee | 62.3 | 6.06 | 377.538 |  | 4835.1962 |  | 11622.7342 | 214.5653 | 15 |  | 6410 | 1 Shee | 62.3 | 9.999 | 622.9377 |  | 6238.0228 | 13270.9605 | 0
[20 empty] | cost estimator |  | 15000 |  |  |  | (pro-rated) |  | 15000 |  |  |  |  | 1.146 | 9615 | 1 Shee | 62.3 | 8.08 | 503.384 |  | 7192.043 | 17310.427 | 214.5653 | 15 |  | 9615 | 1 Shee | 62.3 | 13.332 | 830.5836 |  | 9243.8232 | 19689.4068 |  | 9615 | 1 Shee | 62.3 | 8.08 | 503.384 |  | 7192.043 |  | 17310.427 | 214.5653 | 15 |  | 9615 | 1 Shee | 62.3 | 13.332 | 830.5836 |  | 9243.8232 | 19689.4068 | 0
[20 empty] | cost estimator |  | 20000 |  |  |  | (pro-rated) |  | 20000 |  |  |  |  | 1.146 | 12820 | 1 Shee | 62.3 | 17.4688 | 1088.307 |  | 9992.123 | 23900.43 | 214.5653 | 15 |  | 12820 | 1 Shee | 62.3 | 28.8235 | 1795.7066 |  | 13075.5947 | 27691.3013 |  | 12820 | 1 Shee | 62.3 | 17.4688 | 1088.307 |  | 9992.123 |  | 23900.43 | 214.5653 | 15 |  | 12820 | 1 Shee | 62.3 | 28.8235 | 1795.7066 |  | 13075.5947 | 27691.3013 | 0
Transfer Grilles 90.1-2013 u
[16 empty] | Transfer_Door_Louvers | Addendum 90.1-2013 u requires that transfer air be generally used for restrooms, not just kitchens. In base case, restrooms will have supply air grilles connected to supply air for temperaturer control. Basis 200 cfm | Means Mechanical 2018 Diffuser: 23 37 13.10 Duct: | 6" aluminum diffuser 6" duct, 20 ft long |  |  |  | Addendum 90.1-2013 u requires that transfer air be generally used for restrooms, not just kitchens. For the prototypes analyzed; transfer air requirements can be met with door grilles to allow transfer air to enter restrooms where it is exhausted. The transfer air can be met by one 24x24" door louver being added to the restroom door. | RS Means Building 2018. 08 91 26.10 Steel louvers, painted |  | 24" x 24" | [6 empty] | 1 | 66.2 | Q-10 | 58.15 | 1.473 | 85.6549 |  | 114.5543 | 266.4092 | 0 | 30 |  | 66.2 |  |  |  | 85.6549 |  | 135.0612 | 286.9161 |  | 131 |  |  |  | 17.65 |  | 80.0781 |  | 228.7281 | 0 | 30 |  | 131 |  |  |  | 17.65 |  | 101.6869 | 250.3369 | -37.6812
90.1-07e and 90.1-07 dj | 6. HVAC | 6.5.6 | Energy recovery - yes/no | X |  | X | X | [8 empty] | Energy Recovery Adjustments for when ERV is required based on load changes | 90.1 includes criteria for when energy recovery is required that varies by climate and percentage of outside in the design supply airflow. Energy recovery units with wheel type exchange devices are priced and are commonly used. Note that the cost estimate did not identify a different cost for adding energy recovery for AHU vs. Packaged DX. Energy recovery are priced as added stand alone equipment, not manufacturer integrated add-ons. Costs shown under material include labor. Maintenance for an ERV is similar to that for a packaged DX unit and includes lubrication, checking dampers, adjusting belts, replacing filters, checking doorseals and cleaning coils. RS Means provided a rough estimate for a set of routine AC maintenace activities that total about 2.5 hours. In addition, the energy recovery wheels need to be cleaned. At least one manufacturer claims the media will last the life of the system, and cleaning can take about 15 minutes with frequency from every six months to 10 year depending on conditions, so including 15 minutes each year. | Michael J. Witte, M.J. and R.H. Henninger. 2006. ASHRAE 1254-RP Evaluating the ability of Unitary Equipment to maintain adequate space humidity levels, Phase II. Gard Analytics Park Ridge, Illinois. Approach recommended by SSPC 90.1 MSC. Maintenance RS Means Mechanical 01 93 13.15 http://www.airxchange.com/faqs.htm |  |  |  | Outside Airflow, cfm | Costs used to adjust for ERV size based on load, or when changes in load or airflow result in changed requirement for ERV. Same as base code. | Same as base code. |  |  |  | Outside Airflow, cfm |  |  |  |  | Inflation from 2012 to 2020
[16 empty] | Energy_Recovery_AHU | Energy Recovery for AHU | [5 empty] | Energy Recovery for AHU
[22 empty] | 500 | [5 empty] | 500 |  | 1.5 |  |  | 1.129 | 1875 | Q9 | 56.08 | 11.1106 | 623.08 |  | 1862.0915 | 4360.1714 | 255.0825 | 15 |  | 1875 | Q9 | 56.08 | 18.3324 | 1028.0819 |  | 2695.112 | 5598.1939 |  | 1875 | Q9 | 56.08 | 11.1106 | 623.08 |  | 1862.0915 |  | 4360.1714 | 255.0825 | 15 |  | 1875 | Q9 | 56.08 | 18.3324 | 1028.0819 |  | 2695.112 | 5598.1939 | 0
[16 empty] | used for load changes | [5 empty] | 1000 | [5 empty] | 1000 |  | 3 |  |  | 1.129 | 3750 | Q9 | 56.08 | 13.333 | 747.7146 |  | 3242.94 | 7740.6547 | 255.0825 | 15 |  | 3750 | Q9 | 56.08 | 21.9994 | 1233.7292 |  | 4493.4214 | 9477.1506 |  | 3750 | Q9 | 56.08 | 13.333 | 747.7146 |  | 3242.94 |  | 7740.6547 | 255.0825 | 15 |  | 3750 | Q9 | 56.08 | 21.9994 | 1233.7292 |  | 4493.4214 | 9477.1506 | 0
[22 empty] | 2000 | [5 empty] | 2000 |  | 5 |  |  | 1.129 | 7500 | Q9 | 56.08 | 16 | 897.28 |  | 5908.3741 | 14305.6541 | 255.0825 | 15 |  | 7500 | Q9 | 56.08 | 26.4 | 1480.512 |  | 7910.6529 | 16891.1649 |  | 7500 | Q9 | 56.08 | 16 | 897.28 |  | 5908.3741 |  | 14305.6541 | 255.0825 | 15 |  | 7500 | Q9 | 56.08 | 26.4 | 1480.512 |  | 7910.6529 | 16891.1649 | 0
[22 empty] | 4000 | [5 empty] | 4000 |  | 7.5 |  |  | 1.129 | 15000 | Q9 | 56.08 | 20 | 1121.6 |  | 11167.0133 | 27288.6133 | 255.0825 | 15 |  | 15000 | Q9 | 56.08 | 33 | 1850.64 |  | 14610.5165 | 31461.1565 |  | 15000 | Q9 | 56.08 | 20 | 1121.6 |  | 11167.0133 |  | 27288.6133 | 255.0825 | 15 |  | 15000 | Q9 | 56.08 | 33 | 1850.64 |  | 14610.5165 | 31461.1565 | 0
[22 empty] | 6000 | [5 empty] | 6000 |  | 10 |  |  | 1.129 | 22500 | Q9 | 56.08 | 22.857 | 1281.8206 |  | 16363.7654 | 40145.5859 | 255.0825 | 15 |  | 22500 | Q9 | 56.08 | 37.7141 | 2115.0039 |  | 21195.0523 | 45810.0563 |  | 22500 | Q9 | 56.08 | 22.857 | 1281.8206 |  | 16363.7654 |  | 40145.5859 | 255.0825 | 15 |  | 22500 | Q9 | 56.08 | 37.7141 | 2115.0039 |  | 21195.0523 | 45810.0563 | 0
[22 empty] | 8000 | [5 empty] | 8000 |  | 15 |  |  | 1.129 | 30000 | Q9 | 56.08 | 24 | 1345.92 |  | 21467.7136 | 52813.6336 | 255.0825 | 15 |  | 30000 | Q9 | 56.08 | 39.6 | 2220.768 |  | 27606.6471 | 59827.4151 |  | 30000 | Q9 | 56.08 | 24 | 1345.92 |  | 21467.7136 |  | 52813.6336 | 255.0825 | 15 |  | 30000 | Q9 | 56.08 | 39.6 | 2220.768 |  | 27606.6471 | 59827.4151 | 0
[22 empty] | 10000 | [5 empty] | 10000 |  | 20 |  |  | 1.129 | 37500 | Q9 | 56.08 | 26.667 | 1495.4854 |  | 26654.1782 | 65649.6635 | 255.0825 | 15 |  | 37500 | Q9 | 56.08 | 44.0005 | 2467.5508 |  | 34172.0122 | 74139.563 |  | 37500 | Q9 | 56.08 | 26.667 | 1495.4854 |  | 26654.1782 |  | 65649.6635 | 255.0825 | 15 |  | 37500 | Q9 | 56.08 | 44.0005 | 2467.5508 |  | 34172.0122 | 74139.563 | 0
[22 empty] | 15000 | [5 empty] | 15000 |  | 25 |  |  | 1.129 | 56250 | Q9 | 56.08 | 28.3335 | 1588.9427 |  | 39349.5626 | 97188.5053 | 255.0825 | 15 |  | 56250 | Q9 | 56.08 | 46.7503 | 2621.7554 |  | 50080.8283 | 108952.5837 |  | 56250 | Q9 | 56.08 | 28.3335 | 1588.9427 |  | 39349.5626 |  | 97188.5053 | 255.0825 | 15 |  | 56250 | Q9 | 56.08 | 46.7503 | 2621.7554 |  | 50080.8283 | 108952.5837 | 0
[16 empty] | Energy_Recovery_Packaged | Energy Recovery for Packaged DX Rooftop | [5 empty] | Energy Recovery for Packaged DX Rooftop | [9 empty] | 1.129 | [6 empty] | 0 | [10 empty] | 0
[22 empty] | 500 |  | Same as for AHU energy recovery |  |  |  | 500 |  | 1.5 |  |  | 1.129 | 1875 | Q9 | 56.08 | 11.1106 | 623.08 |  | 1862.0915 | 4360.1714 | 255.0825 | 15 |  | 1875 | Q9 | 56.08 | 18.3324 | 1028.0819 |  | 2695.112 | 5598.1939 |  | 1875 | Q9 | 56.08 | 11.1106 | 623.08 |  | 1862.0915 |  | 4360.1714 | 255.0825 | 15 |  | 1875 | Q9 | 56.08 | 18.3324 | 1028.0819 |  | 2695.112 | 5598.1939 | 0
[16 empty] | used for load changes | [5 empty] | 1000 |  | mechanical subcommittee |  |  |  | 1000 |  | 3 |  |  | 1.129 | 3750 | Q9 | 56.08 | 13.333 | 747.7146 |  | 3242.94 | 7740.6547 | 255.0825 | 15 |  | 3750 | Q9 | 56.08 | 21.9994 | 1233.7292 |  | 4493.4214 | 9477.1506 |  | 3750 | Q9 | 56.08 | 13.333 | 747.7146 |  | 3242.94 |  | 7740.6547 | 255.0825 | 15 |  | 3750 | Q9 | 56.08 | 21.9994 | 1233.7292 |  | 4493.4214 | 9477.1506 | 0
[22 empty] | 2000 | [5 empty] | 2000 |  | 5 |  |  | 1.129 | 7500 | Q9 | 56.08 | 16 | 897.28 |  | 5908.3741 | 14305.6541 | 255.0825 | 15 |  | 7500 | Q9 | 56.08 | 26.4 | 1480.512 |  | 7910.6529 | 16891.1649 |  | 7500 | Q9 | 56.08 | 16 | 897.28 |  | 5908.3741 |  | 14305.6541 | 255.0825 | 15 |  | 7500 | Q9 | 56.08 | 26.4 | 1480.512 |  | 7910.6529 | 16891.1649 | 0
[22 empty] | 4000 |  | Maintenance - estimated from hours for the wheel maintenance only under RS Means Facilities and Maintenance Guidebook 2004 ed. 0.5 hrs, cleaning and checking, plus 5 minutes/1000 cfm above 1,000 cfm. |  |  |  | 4000 |  | 7.5 |  |  | 1.129 | 15000 | Q9 | 56.08 | 20 | 1121.6 |  | 11167.0133 | 27288.6133 | 255.0825 | 15 |  | 15000 | Q9 | 56.08 | 33 | 1850.64 |  | 14610.5165 | 31461.1565 |  | 15000 | Q9 | 56.08 | 20 | 1121.6 |  | 11167.0133 |  | 27288.6133 | 255.0825 | 15 |  | 15000 | Q9 | 56.08 | 33 | 1850.64 |  | 14610.5165 | 31461.1565 | 0
[22 empty] | 6000 | [5 empty] | 6000 |  | 10 |  |  | 1.129 | 22500 | Q9 | 56.08 | 22.857 | 1281.8206 |  | 16363.7654 | 40145.5859 | 255.0825 | 15 |  | 22500 | Q9 | 56.08 | 37.7141 | 2115.0039 |  | 21195.0523 | 45810.0563 |  | 22500 | Q9 | 56.08 | 22.857 | 1281.8206 |  | 16363.7654 |  | 40145.5859 | 255.0825 | 15 |  | 22500 | Q9 | 56.08 | 37.7141 | 2115.0039 |  | 21195.0523 | 45810.0563 | 0
[22 empty] | 8000 | [5 empty] | 8000 |  | 15 |  |  | 1.129 | 30000 | Q9 | 56.08 | 24 | 1345.92 |  | 21467.7136 | 52813.6336 | 255.0825 | 15 |  | 30000 | Q9 | 56.08 | 39.6 | 2220.768 |  | 27606.6471 | 59827.4151 |  | 30000 | Q9 | 56.08 | 24 | 1345.92 |  | 21467.7136 |  | 52813.6336 | 255.0825 | 15 |  | 30000 | Q9 | 56.08 | 39.6 | 2220.768 |  | 27606.6471 | 59827.4151 | 0
[22 empty] | 10000 | [5 empty] | 10000 |  | 20 |  |  | 1.129 | 37500 | Q9 | 56.08 | 26.667 | 1495.4854 |  | 26654.1782 | 65649.6635 | 255.0825 | 15 |  | 37500 | Q9 | 56.08 | 44.0005 | 2467.5508 |  | 34172.0122 | 74139.563 |  | 37500 | Q9 | 56.08 | 26.667 | 1495.4854 |  | 26654.1782 |  | 65649.6635 | 255.0825 | 15 |  | 37500 | Q9 | 56.08 | 44.0005 | 2467.5508 |  | 34172.0122 | 74139.563 | 0
[22 empty] | 15000 | [5 empty] | 15000 |  | 25 |  |  | 1.129 | 56250 | Q9 | 56.08 | 28.3335 | 1588.9427 |  | 39349.5626 | 97188.5053 | 255.0825 | 15 |  | 56250 | Q9 | 56.08 | 46.7503 | 2621.7554 |  | 50080.8283 | 108952.5837 |  | 56250 | Q9 | 56.08 | 28.3335 | 1588.9427 |  | 39349.5626 |  | 97188.5053 | 255.0825 | 15 |  | 56250 | Q9 | 56.08 | 46.7503 | 2621.7554 |  | 50080.8283 | 108952.5837 | 0
[16 empty] | 90.1-16g | Occupied standby control. When a zone is scheduled to be occupied and an occupant sensor indicates zero population, the zone shall have heating and cooling thermostat setback of 1F and should completely shut off HVAC supply air within the deadband | [15 empty] | 2020 costs
[16 empty] | occ_standby | No occupied standby control installed | [5 empty] | Occupied standby control installed labor is per conditioned zone | 2020 RSMeans | [8 empty] | 1 | 0 |  |  |  | 0 |  | 0 | 0 | 0 |  |  | 0 |  |  |  | 0 |  | 0 | 0 |  | 0 | 1 elec | 61.35 | 0.25 | 15.3375 |  | 14.8082 |  | 30.1457 | 0 | 15 |  | 0 | Q5 | 61.35 | 0.4125 | 25.3069 |  | 27.5952 | 52.9021 | 30.1457
[16 empty] | 90.1-16 h & ay | Energy Recovery Ventilator for midrise apartments | [15 empty] | 2020 costs
[16 empty] | ERV_multifamily | No ERV installed. Central fan integrated (CFI) system installed with two bathroom exhaust fans. Common low-cost supply ventilation | Energy Cost Analysis for Energy Recovery Ventilation in Dwelling Units. Presentation to ASHRAE 90.1 MSC. 5-31-18 |  |  |  |  | ERV installed. Fan efficacy: 1.2 cfm/W (minimum set in IECC for residential ERVs). Displaces two bathroom exhaust fans. No: defrost, economizing, bypass Costs in Climate Zones 1-3 | Energy Cost Analysis for Energy Recovery Ventilation in Dwelling Units. Presentation to ASHRAE 90.1 MSC. 5-31-18 |  |  |  | 1 ea |  |  |  |  | 1 | 564 |  |  |  | 610 |  | 860.3445 | 2034.3445 | 0 | 15 |  | 564 |  |  |  | 610 |  | 1020.0951 | 2194.0951 |  | 1010 |  |  |  | 437 |  | 907.9303 |  | 2354.9303 | 15 | 15 |  | 1010 |  |  |  | 437 |  | 1112.1285 | 2559.1285 | 320.5858
[23 empty] | Higher costs in Climate Zones 4-8 due to ERV defrost equipment in colder climates |  |  |  |  | 1 ea |  |  |  |  | 1 | 564 |  |  |  | 610 |  | 860.3445 | 2034.3445 | 0 | 15 |  | 564 |  |  |  | 610 |  | 1020.0951 | 2194.0951 |  | 1081 |  |  |  | 437 |  | 942.0955 |  | 2460.0955 | 15 | 15 |  | 1081 |  |  |  | 437 |  | 1156.8102 | 2674.8102 | 425.751
[16 empty] | DCV_Requirement | For cases where DCV is now required due to reduction in people density threshold. | Based on staff review of recent bid and quote information | \\korea\comstd\90.1_IECC_ State_Cost_Eff\Costs and Cost-Effectiveness\HVAC\DCV\RE primary school cafeteria DCV cost.msg | [12 empty] | DCV_Requirement | 1.0903 | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 15 |  | 0 | Q9 | 0 | 1.5 | 0 |  | 0 | 0 |  | 350 | Q9 | 56.08 | 1.5 | 84.12 |  | 296.4387 |  | 730.5587 | 0 | 15 |  | 350 | Q9 | 56.08 | 1.5 | 84.12 |  | 363.4705 | 797.5905 | 730.5587
[16 empty] | Refrigeration | [15 empty] | Find
[16 empty] | 90.1-16 br | 2 refrigerators, 24 cubic feet each, which implies single door, with daily energy usage described as 0.10V + 2.04, where V is the capacity in cubic feet. | Material costs are from the appliance standard rulemaking | Various | Various |  | ea 24 cu ft refridg | 2 refrigerators, 24 cubic feet each, which implies single door, with daily energy usage described as 0.05V + 1.36, where V is the capacity in cubic feet. | Material costs are from the appliance standard rulemaking | Various | Various |  | ea 24 cu ft refridg |  |  |  | eff_Refr | 1 | 4133 | NA | 0 | 0 | 0 |  | 1988.7996 | 6121.7996 | 0 | 15 |  | 4133 | NA | 0 | 0 | 0 |  | 2600.9796 | 6733.9796 |  | 7242 | NA | 0 | 0 | 0 |  | 3484.8504 |  | 10726.8504 |  | 15 |  | 7242 | NA | 0 | 0 | 0 |  | 4557.5354 | 11799.5354 | 4605.0508
[16 empty] | 90.1-16 br | 2 freezers, 48 cubic feet each, which implies double door, with daily energy usage described as 0.40 x V + 1.38, where V is the capacity in cubic feet. | Material costs are from the appliance standard rulemaking | Various | Various |  | ea 48 cu ft freezer | 2 freezers, 48 cubic feet each, which implies double door, with daily energy usage described as 0.22 x V + 1.38, where V is the capacity in cubic feet. | Material costs are from the appliance standard rulemaking | Various | Various |  | ea 48 cu ft freezer |  |  |  | eff_Frzr | 1 | 4483 | NA | 0 | 0 | 0 |  | 2157.2196 | 6640.2196 | 0 | 15 |  | 4483 | NA | 0 | 0 | 0 |  | 2821.2416 | 7304.2416 |  | 5201 | NA | 0 | 0 | 0 |  | 2502.7212 |  | 7703.7212 |  | 15 |  | 5201 | NA | 0 | 0 | 0 |  | 3273.0933 | 8474.0933 | 1063.5016
[16 empty] | 90.1-16 cn | primary school walk-in refrigerator, COP 3.0 | Material costs are from the appliance standard rulemaking |  |  |  | 1 ea | primary school walk-in refrigerator, COP 6.98 | Material costs are from the appliance standard rulemaking |  |  |  | 1 ea |  |  |  | eff_WI_Refr | 1 | 5146 | 1 elec | 61.35 | 1.5 | 92.025 |  | 2565.1042 | 7803.1292 | 0 | 15 |  | 5146 | 1 elec | 61.35 | 2.475 | 151.8413 |  | 3404.0521 | 8701.8933 |  | 5602 | 1 elec | 61.35 | 1.5 | 92.025 |  | 2784.5314 |  | 8478.5564 |  | 15 |  | 5602 | 1 elec | 61.35 | 2.475 | 151.8413 |  | 3691.022 | 9444.8632 | 675.4272
[16 empty] | 90.1-16 cn | primary school walk-in freezer, COP 1.5 | Material costs are from the appliance standard rulemaking |  |  |  | 1 ea | primary school walk-in freezer, COP 2.32 | Material costs are from the appliance standard rulemaking |  |  |  | 1 ea |  |  |  | eff_WI_Frzr | 1 | 6422 | 1 elec | 61.35 | 1.5 | 92.025 |  | 3179.1154 | 9693.1404 | 0 | 15 |  | 6422 | 1 elec | 61.35 | 2.475 | 151.8413 |  | 4207.0644 | 10780.9056 |  | 6777 | 1 elec | 61.35 | 1.5 | 92.025 |  | 3349.9414 |  | 10218.9664 |  | 15 |  | 6777 | 1 elec | 61.35 | 2.475 | 151.8413 |  | 4430.473 | 11359.3142 | 525.826
[16 empty] | 90.1-10g | Addendum G Commercial Refrigerators for Primary School: 2 refrigerators, 24 cubic feet each, which implies single door, with daily energy usage described as 0.125V+4.22, where V is the capacity in cubic feet. | RSMeans 2014 Green Building Data plus 5 commercial refrigeration equipment websites | Various | Various |  | ea 24 cu ft refridg | 2 refrigerators, 24 cubic feet each, which implies single door, with daily energy usage described as 0.10V + 2.04, where V is the capacity in cubic feet. | RSMeans 2014 Green Building Data plus 5 commercial refrigeration equipment websites | Various | Various |  | ea 24 cu ft refridg |  |  |  | eff_Refr_OLD | 1 | 2982.56 | NA | 0 | 0 | 0 |  | 1435.2079 | 4417.7679 | 0 | 15 |  | 2982.56 | NA | 0 | 0 | 0 |  | 1876.9847 | 4859.5447 |  | 3007.85 | NA | 0 | 0 | 0 |  | 1447.3774 |  | 4455.2274 | 0 | 15 |  | 3007.85 | Q5 | 0 | 0 | 0 |  | 1892.9002 | 4900.7502 | 37.4595
[17 empty] | Addendum G Commercial Freezer for Primary School8/27/2014 2 freezers, 48 cubic feet each, which implies double door, with daily energy usage described as 0.398 V+2.83, where V is the capacity in cubic feet. | RSMeans 2014 Green Building Data plus 4 commercial refrigeration equipment websites | Various | Various |  | ea 48 cu ft freezer | 2 freezers, 48 cubic feet each, which implies double door, with daily energy usage described as 0.40 x V + 1.38, where V is the capacity in cubic feet. | RSMeans 2014 Green Building Data plus 4 commercial refrigeration equipment websites | Various | Various |  | ea 48 cu ft freezer |  |  |  | eff_Frzr_OLD | 1 | 1857.34 | NA | 0 | 0 | 0 |  | 893.752 | 2751.092 | 0 | 15 |  | 1857.34 | NA | 0 | 0 | 0 |  | 1168.8612 | 3026.2012 |  | 5385.58 | NA | 0 | 0 | 0 |  | 2591.5411 |  | 7977.1211 | 0 | 15 |  | 5385.58 | Q5 | 0 | 0 | 0 |  | 3389.2532 | 8774.8332 | 5226.0291
[16 empty] | 90.1-10ar | Addendum AR 1/20 hp motor for primary school walk-in refrigerator evaporator fan: 1/20 hp shaded pole motor | Grainger Catalog (www.grainger.com) | Dayton | 6NZR7 |  | 1 ea | 1/20 hp ECM motor for primary school walk-in refrigerator evaporator fan | Grainger Catalog (www.grainger.com) | Morrill | 12V783 |  | 1 ea |  |  |  | WI_Refr_ECM | 1 | 89.4 | 1 elec | 61.35 | 1.501 | 92.0863 |  | 131.9275 | 313.4139 | 0 | 15 |  | 89.4 | 1 elec | 61.35 | 2.4766 | 151.9425 |  | 221.9429 | 463.2854 |  | 126.85 | 1 elec | 61.35 | 1.501 | 92.0863 |  | 149.9485 |  | 368.8848 | 0 | 15 |  | 126.85 | Q5 | 61.35 | 2.4766 | 151.9425 |  | 245.511 | 524.3034 | 55.4709
[17 empty] | Addendum AR 1/40 hp motor for primary school walk-in freezer evaporator fan: 1/40 hp shaded pole motor | Grainger Catalog (www.grainger.com) | Dayton | 3M724 |  | 1 ea | 1/40 hp ECM motor for primary school walk-in freezer evaporator fan (1/40 hp ECM motor not available so cost interpolated from 1/30 and 1/50 hp motors | Grainger Catalog (www.grainger.com) | Morrill | Interpolated (See below) |  | 1 ea |  |  |  | WI_Frzr_ECM | 1 | 93.25 | 1 elec | 61.35 | 1.501 | 92.0863 |  | 133.7802 | 319.1165 | 0 | 15 |  | 93.25 | 1 elec | 61.35 | 2.4766 | 151.9425 |  | 224.3658 | 469.5583 |  | 112.98 | 1 elec | 61.35 | 1.501 | 92.0863 |  | 143.2742 |  | 348.3406 | 0 | 15 |  | 112.98 | Q5 | 61.35 | 2.4766 | 151.9425 |  | 236.7823 | 501.7048 | 29.2241
[17 empty] | No walk-in lighting controls required required in base code | Not required | Not required | NA |  | 1 ea | Low Temperature Occupancy Sensor; Addendum AR low Temperature Occupancy Sensor for walk-in refrigerator and for walk-in freezer | Grainger Catalog (www.grainger.com) | Hubbell Wiring Device- Kellems | AHP1500CRP |  | 2 ea |  |  |  | WI_OccSnsr | 1 | 0 | NA | 0 | 0 | 0 |  | 0 | 0 | 0 | 15 |  | 0 | NA | 0 | 0 | 0 |  | 0 | 0 |  | 275 | 1 elec | 61.35 | 1.143 | 70.1231 |  | 200.033 |  | 545.156 | 0 | 15 |  | 275 | Q5 | 61.35 | 1.886 | 115.703 |  | 299.2284 | 689.9314 | 545.156
|  |  | Kitchen Exhaust | [12 empty] | Kitchen Exhaust 90.1-07ax | 90.1-07 section 6.5.7.1 includes which requires at least 50% make-up air. The make-up air units are accounted for separately from the kitchen exhaust and their costs are included under the general capacity changes above. | [5 empty] | 90.1-2010 includes multiple provisions that affect the design and exhaust volume of kitchen exhaust hoods. 1) The exhaust maximum airflow values in Table 6.5.7.1.3 are 30% below the values allowed in ASHRAE Standard 154-2003. For the savings analysis, it was assumed that many systems already meet these lower exhaust airflow requirements, and the 90.1-2010 exhaust airflow is set 10% below the value inlcuded for the 90.1-2007 models. The costs in this section are for the different airflow capacity units. 2) Transfer air from surrounding spaces on the same floor as the kitchens required to be used as the first source of exhaust makeup air. No costs are identified for this, and the assumption is that this transfer can be transferred through standards doors or other openings between the spaces. Differences in the makeup air volume for the case with the use of transfer air are accounted for under the general HVAC capacity costs.
[16 empty] | Kitchen_Exhaust | [11 empty] | 3480 | [8 empty] | 25
[17 empty] | Belt drive centrifugal upblast exhaust fan with 24 in. wheel. Nominal size of selected unit is 5,400 cfm. Primary school kitchen is the only prototype affected. | Restaurant Max Inc. online http://www.restaurant-services.com/hoods.htm RS Means 2012 23 34 16 0326 for labor. |  | BDU-24 |  | 5000 | Belt drive centrifugal upblast exhaust fan with 20.75 in. wheel. Nominal airflow of selected unit is 4,500 cfm. | Restaurant Max Inc. online http://www.restaurant-services.com/hoods.htm. RS Means 2012 23 34 16 0326 for labor. |  | BDU-20 |  | 4500 |  |  |  |  | 1 | 1392 | Q-20 | 57.13 | 26.0627 | 1488.9628 |  | 2107.4061 | 4988.3688 |  | 25 |  | 1392 | Q-20 | 57.13 | 43.0035 | 2456.7886 |  | 3554.9547 | 7403.7432 |  | 1061 | Q-20 | 48 | 26.0646 | 1251.102 |  | 1718.4772 |  | 4030.5792 | 0 | 25 |  | 1061 | Q-20 | 48 | 43.0066 | 2064.3183 |  | 2918.6907 | 6044.009 | -957.7897
HVAC Plant - Capacity Change |  |  | General: Load Changes Plant Equipment and Piping | [12 empty] | HVAC Plant Capacity Costs | Costs used to account for changes in plant capacity due to changes in 90.1. Costs are base costs for system that meets 90.1 base case standard requirements before application of addenda. Difference in cost by capacity will be calculated in final summary sheet based on the base case and target case capacity for a particular prototype and climate zone. | [5 empty] | For central plants, there are separate costs where there are efficiency increases or changes in requirements. Difference in cost for capacity between base case and target case models is also accounted for on prototype sheets. Difference in cost by capacity will be calculated in final summary sheet based on the base and target capacity for a particular prototype and climate zone. | [51 empty] | 21% OHP contractor 10% overhead multiplied by 10% , 1st overhead for sub, 10% for labor and material
|  |  | Chillers |  | X | [10 empty] | Chillers Plant Capacity Adjustments | 90.1 base case chiller efficiency is the same as target case. Costs account for changes in chiller capacity due to other measures. Costs are for 90.1 base code efficiency chillers, Path A centrifugal. Chiller type modeled depending on base case capacity and all are centrifugal. Minimum efficiency for Path A Centrifugal. (only need up to 500 Tons). | Equipment information below. Labor from RS Means 2020 Mechanical Cost Data. RS Means Centrifugal Type Water Chillers 23 64 16.10 |  |  |  | Cooling Capacity, tons | 90.1 base case chiller efficiency is the same as target case. Costs account for changes in chiller capacity due to other measures. Costs are for 90.1 base code efficiency chillers, Path A centrifugal. Chiller type modeled depending on base case capacity and all are centrifugal. Minimum efficiency for Path A Centrifugal. (only need up to 500 Tons). |  |  |  |  | Cooling Capacity, tons |  |  |  |  | Inflation from 2012 to 2020
[16 empty] | Chillers same cost 2013/2015 | Manufacturer 1 | Brad Wagner (Airefco) (via Mike Rosenberg) |  |  |  |  | Manufacturer 1 | Brad Wagner (Airefco) | [47 empty] | 0
[28 empty] | 200 | [5 empty] | 85015.5568 | [19 empty] | 85015.5568
[16 empty] | Use inflation from 2012 to 2018 | minimum efficiency full load 0.559 kW/ton, IPLV 0.399 kW/ton* | NW Air reps | YORKTrane, Carrier or McQuay |  |  | 300 | minimum efficiency full load 0.559 kW/ton, IPLV 0.399 kW/ton* | Airefco | Carrier | 19XRV3031323CES64 |  | 300 |  |  |  |  | 1.007 | 104023.1 | [18 empty] | 100% | 104023.1 | [17 empty] | 0
[17 empty] | minimum efficiency full load 0.556 kW/ton, IPLV 0.384 kW/ton |  | Estimated for multiple |  |  | 400 | minimum efficiency full load 0.556 kW/ton, IPLV 0.384 kW/ton | Airefco | Carrier | 19XRV3132204BHH64 |  | 400 |  |  |  |  | 1.007 | 105130.8 | [18 empty] | 100% | 105130.8 | [17 empty] | 0
[17 empty] | minimum efficiency full load 0.545 kW/ton, IPLV 0.370 kW/ton |  | manufacturers |  |  | 500 | minimum efficiency full load 0.545 kW/ton, IPLV 0.370 kW/ton | Airefco | Carrier | 19XRV4140383CPS64 |  | 500 |  |  |  |  | 1.007 | 121847 | [18 empty] | 100% | 121847 | [17 empty] | 0
[17 empty] | *Full load kW/Ton near requirment. IPLV exceeds due to product availability (includes VFD). | [5 empty] | *Full load kW/Ton near requirment. IPLV exceeds due to product availability (includes VFD). | [30 empty] | 0 | [17 empty] | 0
[28 empty] | 200 | [5 empty] | 123000 | [19 empty] | 123000
[22 empty] | 300 | [5 empty] | 300 | [5 empty] | 150500 | [19 empty] | 150500 | [17 empty] | 0
[17 empty] | Means 2018: 23 64 16.10 |  |  |  |  | 400 | Means 23 64 16.10 |  |  |  |  | 400 | [5 empty] | 152000 | [19 empty] | 152000 | [17 empty] | 0
[22 empty] | 500 | [5 empty] | 500 | [5 empty] | 185500 | [19 empty] | 185500 | [17 empty] | 0
[16 empty] | Cent_WC_Chiller_Capacity | Average of two manufacturers (Path A Chillers) & Means 2018 | [5 empty] | Average of two manufacturers (Path A Chillers)
[17 empty] | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 200 | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 200 |  |  |  |  | 1.007 | 104007.7784 | Q7 | 62.4 | 231 | 14414.4 |  | 65043.8674 | 183466.0459 |  | 23 |  | 104007.7784 | Q7 | 62.4 | 381.15 | 23783.76 |  | 92574.7915 | 220366.3299 |  | 104007.7784 | Q7 | 62.4 | 231 | 14414.4 |  | 65043.8674 |  | 183466.0459 | 0 | 23 |  | 104007.7784 | Q7 | 62.4 | 381.15 | 23783.76 |  | 92574.7915 | 220366.3299 | 0
[17 empty] | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 300 | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 300 |  |  |  |  | 1.007 | 127261.55 | Q7 | 62.4 | 257 | 16036.8 |  | 78041.0945 | 221339.4445 |  | 23 |  | 127261.55 | Q7 | 62.4 | 424.05 | 26460.72 |  | 110393.0913 | 264115.3613 |  | 127261.55 | Q7 | 62.4 | 257 | 16036.8 |  | 78041.0945 |  | 221339.4445 | 0 | 23 |  | 127261.55 | Q7 | 62.4 | 424.05 | 26460.72 |  | 110393.0913 | 264115.3613 | 0
[17 empty] | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 400 | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 400 |  |  |  |  | 1.007 | 128565.4 | Q7 | 62.4 | 283 | 17659.2 |  | 80248.4337 | 226473.0337 |  | 23 |  | 128565.4 | Q7 | 62.4 | 466.95 | 29137.68 |  | 114147.5223 | 271850.6023 |  | 128565.4 | Q7 | 62.4 | 283 | 17659.2 |  | 80248.4337 |  | 226473.0337 | 0 | 23 |  | 128565.4 | Q7 | 62.4 | 466.95 | 29137.68 |  | 114147.5223 | 271850.6023 | 0
[17 empty] | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 500 | minimum efficiency full load 0.560 kW/ton, IPLV 0.520 kW/ton |  |  |  |  | 500 |  |  |  |  | 1.007 | 153673.5 | Q7 | 62.4 | 296 | 18470.4 |  | 93373.9861 | 265517.8861 |  | 23 |  | 153673.5 | Q7 | 62.4 | 488.4 | 30476.16 |  | 131694.4265 | 315844.0865 |  | 153673.5 | Q7 | 62.4 | 296 | 18470.4 |  | 93373.9861 |  | 265517.8861 | 0 | 23 |  | 153673.5 | Q7 | 62.4 | 488.4 | 30476.16 |  | 131694.4265 | 315844.0865 | 0
|  |  | Cooling Towers |  | X | [10 empty] | Cooling Towers Plant Capacity Changes | Same costs for both base case and target case, reflecting increase in efficiency requirements to 40.2 gpm/hp in 2013. There is also a difference in cost for capacity when there is a change in cooling capacity due to other measures. Difference in cost by capacity will be calculated in final summary sheet based on the base and target code capacity for a particular prototype and climate zone. | Equipment information below. Labor from RS Means 2020 Mechanical Cost Data. Forced-Draft Type Cooling Towers 23 65 13.10 25XX |  |  |  | Size of Chiller Cooling Load Served, tons | Same costs for both base case and target case, reflecting increase in efficiency requirements to 40.2 gpm/hp in 2013. There is also a difference in cost for capacity when there is a change in cooling capacity due to other measures. Difference in cost by capacity will be calculated in final summary sheet based on the base and target code capacity for a particular prototype and climate zone. |  |  |  |  | Size of Chiller Cooling Load Served, tons
[16 empty] | Plant Capacity difference | Required performance of 40.2 gpm/hp | [5 empty] | Required performance of 40.2 gpm/hp | [6 empty] | Base 2010 Cost (Mat) | Adder per ton
[17 empty] | Average cost increase of $1.00/Ton | NW Air Reps | BAC | S15E-1285-06JN |  | 233 | Average cost increase of $1.00/Ton | NW Air Reps | BAC | S1500 - various |  | 233 |  | 19264 | 1 |  |  | 19497 | [19 empty] | 19497
[17 empty] | Average cost increase of $0.66/Ton | NW Air Reps | BAC | S15E-1285-09LN |  | 354 | Average cost increase of $0.66/Ton | NW Air Reps | BAC | S1500 - various |  | 354 |  | 25934 | 0.66 |  |  | 26167.64 | [19 empty] | 26167.64
[17 empty] | Average cost increase of $1.04/Ton | NW Air Reps | BAC | S3E-8518-06M |  | 467 | Average cost increase of $1.04/Ton | NW Air Reps | BAC | S3000 - various |  | 467 |  | 31907 | 1.04 |  |  | 32392.68 | [19 empty] | 32392.68
[17 empty] | Required performance of 40.2 gpm/hp | [5 empty] | Required performance of 40.2 gpm/hp
[17 empty] | Average cost increase of $3.30/Ton | Trane Oregon | SPX | NC8401MAN1 |  | 233 | Average cost increase of $3.30/Ton | Trane Oregon | SPX | NC Steel- various |  | 233 |  | 46559 | 3.3 |  |  | 47327.9 | [19 empty] | 47327.9
[17 empty] | Average cost increase of $3.23/Ton | Trane Oregon | SPX | NC8402NAN1 |  | 354 | Average cost increase of $3.23/Ton | Trane Oregon | SPX | NC Steel- various |  | 354 |  | 61903 | 3.23 |  |  | 63046.42 | [19 empty] | 63046.42
[17 empty] | Average cost increase of $2.30/Ton | Trane Oregon | SPX | NC8407QLS1 |  | 467 | Average cost increase of $2.30/Ton | Trane Oregon | SPX | NC Steel- various |  | 467 |  | 88630 | 2.3 |  |  | 89704.1 | [19 empty] | 89704.1
[16 empty] | Cooling_Tower_Capacity | Required performance of 40.2 gpm/hp | [5 empty] | Required performance of 40.2 gpm/hp | [9 empty] | 2012 to 2020
[22 empty] | 233 | [5 empty] | 233 |  |  |  |  | 1.2276 | 33412.45 | Q7 | 62.4 | 39.216 | 2447.0784 |  | 29702.6135 | 65562.1419 |  | 20 |  | 33412.45 | Q7 | 62.4 | 64.7064 | 4037.6794 |  | 37818.015 | 75268.1444 |  | 33412.45 | Q7 | 62.4 | 39.216 | 2447.0784 |  | 29702.6135 |  | 65562.1419 | 0 | 20 |  | 33412.45 | Q7 | 62.4 | 64.7064 | 4037.6794 |  | 37818.015 | 75268.1444 | 0
[22 empty] | 354 | [5 empty] | 354 |  |  |  |  | 1.2276 | 44607.03 | Q7 | 62.4 | 59.259 | 3697.7616 |  | 40070.1825 | 88374.9741 |  | 20 |  | 44607.03 | Q7 | 62.4 | 97.7773 | 6101.3066 |  | 51263.756 | 101972.0926 |  | 44607.03 | Q7 | 62.4 | 59.259 | 3697.7616 |  | 40070.1825 |  | 88374.9741 | 0 | 20 |  | 44607.03 | Q7 | 62.4 | 97.7773 | 6101.3066 |  | 51263.756 | 101972.0926 | 0
[22 empty] | 467 | [5 empty] | 467 |  |  |  |  | 1.2276 | 61048.39 | Q7 | 62.4 | 100 | 6240 |  | 55977.9497 | 123266.3397 |  | 20 |  | 61048.39 | Q7 | 62.4 | 165 | 10296 |  | 72280.4795 | 143624.8695 |  | 61048.39 | Q7 | 62.4 | 100 | 6240 |  | 55977.9497 |  | 123266.3397 | 0 | 20 |  | 61048.39 | Q7 | 62.4 | 165 | 10296 |  | 72280.4795 | 143624.8695 | 0
|  |  | Boilers |  | X |  | X | [8 empty] | Boiler Capacity Adjustment | Natural gas boiler, hot water, cast iron heat exchanger. Size ranges correspond to efficiency categories in 90.1. Size <300 kBtu/h 80% AFUE 2. Size 300 kBtu/h to 2,500 kBtu/h 80% Et, size above 2,500 kBtu/h 82% Ec. Boiler capacity shown below in millions of Btu/h. | Equipment information below. Labor from RS Means 2020 Mechanical Cost Data. Gas-Fired Boilers 23 52 23.20 3020+ |  |  |  | Million Btu/h | Based on 2012 costs. Difference in cost for capacity between base code and target code. Difference in cost by capacity will be calculated in final summary sheet based on the capacity difference based on other changes affecting heating load for a particular prototype and climate zone. |  |  |  |  | Million Btu/h |  |  |  |  | 2012 to 2020 | [20 empty] | 0
Manufacturer 1
[17 empty] | 0.3 | F&G 2012 | Proctor Sales - Weil-McCain | 81% CGT-5 |  | 0.3 | [5 empty] | 0.3 |  |  |  |  | 1.327 | 4106.85 | Q7 | 62.4 | 37.778 | 2357.3472 |  | 6241.3693 | 12705.5665 |  | 35 |  | 4106.85 | Q7 | 62.4 | 62.3337 | 3889.6229 |  | 9013.9399 | 17010.4128 |  | 4106.85 | Q7 | 62.4 | 37.778 | 2357.3472 |  | 6241.3693 |  | 12705.5665 |  | 35 |  | 4106.85 | Q7 | 62.4 | 62.3337 | 3889.6229 |  | 9013.9399 | 17010.4128 | 0
[17 empty] | 2.5 | F&G 2012 | Proctor Sales - Weil-McCain | 82% H1688 |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.327 | 13987.3909 | Q7 | 62.4 | 152.1471 | 9493.9765 |  | 22671.8792 | 46153.2465 |  | 35 |  | 13987.3909 | Q7 | 62.4 | 251.0426 | 15665.0612 |  | 33336.4125 | 62988.8645 |  | 13987.3909 | Q7 | 62.4 | 152.1471 | 9493.9765 |  | 22671.8792 |  | 46153.2465 |  | 35 |  | 13987.3909 | Q7 | 62.4 | 251.0426 | 15665.0612 |  | 33336.4125 | 62988.8645 | 0
[17 empty] | 7.5 | F&G 2012 | Proctor Sales - Weil-McCain | 82% H1688 |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 1.327 | 41962.1726 | Q7 | 62.4 | 386 | 24086.4 |  | 63771.8067 | 129820.3793 |  | 35 |  | 41962.1726 | Q7 | 62.4 | 636.9 | 39742.56 |  | 92100.8027 | 173805.5353 |  | 41962.1726 | Q7 | 62.4 | 386 | 24086.4 |  | 63771.8067 |  | 129820.3793 |  | 35 |  | 41962.1726 | Q7 | 62.4 | 636.9 | 39742.56 |  | 92100.8027 | 173805.5353 | 0
[17 empty] | 15 | F&G 2012 | Proctor Sales - Hurst | fire tube |  | 15 | larger sizes not referenced in prototypes |  |  |  |  | 15 |  |  |  |  | 1.327 | 141075 | Q7 | 62.4 | 727 | 45364.8 |  | 180014.4749 | 366454.2749 |  | 35 |  | 141075 | Q7 | 62.4 | 1199.55 | 74851.92 |  | 245564.6653 | 461491.5853 |  | 141075 | Q7 | 62.4 | 727 | 45364.8 |  | 180014.4749 |  | 366454.2749 |  | 35 |  | 141075 | Q7 | 62.4 | 1199.55 | 74851.92 |  | 245564.6653 | 461491.5853 | 0
[17 empty] | 25 | F&G 2012 | Proctor Sales - Hurst | fire tube |  | 25 | larger sizes not referenced in prototypes |  |  |  |  | 25 |  |  |  |  | 1.327 | 184062.5 | Q7 | 62.4 | 1211.6667 | 75608 |  | 250720.6053 | 510391.1053 |  | 35 |  | 184062.5 | Q7 | 62.4 | 1999.25 | 124753.2 |  | 349934.3208 | 658750.0208 |  | 184062.5 | Q7 | 62.4 | 1211.6667 | 75608 |  | 250720.6053 |  | 510391.1053 |  | 35 |  | 184062.5 | Q7 | 62.4 | 1999.25 | 124753.2 |  | 349934.3208 | 658750.0208 | 0
[17 empty] | Manufacturer 2 | [27 empty] | 0
[17 empty] | 0.3 | F&G 2012 | Columbia Hydronics - Smith | 80% Et H480 |  | 0.3 | [5 empty] | 0.3 |  |  |  |  | 1.327 | 6650 | Q7 | 62.4 | 37.778 | 2357.3472 |  | 8696.9139 | 17704.2611 |  | 35 |  | 6650 | Q7 | 62.4 | 62.3337 | 3889.6229 |  | 11969.3539 | 22508.9768 |  | 6650 | Q7 | 62.4 | 37.778 | 2357.3472 |  | 8696.9139 |  | 17704.2611 |  | 35 |  | 6650 | Q7 | 62.4 | 62.3337 | 3889.6229 |  | 11969.3539 | 22508.9768 | 0
[17 empty] | 2.5 | F&G 2012 | Columbia Hydronics - Smith | 82% Ec H1688 |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.327 | 23750 | Q7 | 62.4 | 152.1471 | 9493.9765 |  | 32098.1899 | 65342.1663 |  | 35 |  | 23750 | Q7 | 62.4 | 251.0426 | 15665.0612 |  | 44681.6151 | 84096.6763 |  | 23750 | Q7 | 62.4 | 152.1471 | 9493.9765 |  | 32098.1899 |  | 65342.1663 |  | 35 |  | 23750 | Q7 | 62.4 | 251.0426 | 15665.0612 |  | 44681.6151 | 84096.6763 | 0
[17 empty] | 7.5 | F&G 2012 | Columbia Hydronics - Smith | 82% Ec H1688 |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 1.327 | 69701.087 | Q7 | 62.4 | 386 | 24086.4 |  | 90555.182 | 184342.6689 |  | 35 |  | 69701.087 | Q7 | 62.4 | 636.9 | 39742.56 |  | 124336.4069 | 233780.0539 |  | 69701.087 | Q7 | 62.4 | 386 | 24086.4 |  | 90555.182 |  | 184342.6689 |  | 35 |  | 69701.087 | Q7 | 62.4 | 636.9 | 39742.56 |  | 124336.4069 | 233780.0539 | 0
[17 empty] | 15 | F&G 2012 | costs not available for this size |  |  | 15 | larger sizes not referenced in prototypes |  |  |  |  | 15
[17 empty] | 25 | F&G 2012 | costs not available for this size |  |  | 25 | larger sizes not referenced in prototypes |  |  |  |  | 25
[16 empty] | Boiler_Capacity | Average costs from two manufacturers | [15 empty] | 1.327
[17 empty] | 0.3 |  |  |  |  | 0.3 | [5 empty] | 0.3 |  |  |  |  | 1.327 | 5378.425 | Q7 | 62.4 | 37.778 | 2357.3472 |  | 7469.1416 | 15204.9138 |  | 35 |  | 5378.425 | Q7 | 62.4 | 62.3337 | 3889.6229 |  | 10491.6469 | 19759.6948 |  | 5378.425 | Q7 | 62.4 | 37.778 | 2357.3472 |  | 7469.1416 |  | 15204.9138 |  | 35 |  | 5378.425 | Q7 | 62.4 | 62.3337 | 3889.6229 |  | 10491.6469 | 19759.6948 | 0
[17 empty] | 2.5 |  |  |  |  | 2.5 | [5 empty] | 2.5 |  |  |  |  | 1.327 | 18868.6954 | Q7 | 62.4 | 152.1471 | 9493.9765 |  | 27385.0345 | 55747.7064 |  | 35 |  | 18868.6954 | Q7 | 62.4 | 251.0426 | 15665.0612 |  | 39009.0138 | 73542.7704 |  | 18868.6954 | Q7 | 62.4 | 152.1471 | 9493.9765 |  | 27385.0345 |  | 55747.7064 |  | 35 |  | 18868.6954 | Q7 | 62.4 | 251.0426 | 15665.0612 |  | 39009.0138 | 73542.7704 | 0
[17 empty] | 7.5 |  |  |  |  | 7.5 | [5 empty] | 7.5 |  |  |  |  | 1.327 | 55831.6298 | Q7 | 62.4 | 386 | 24086.4 |  | 77163.4943 | 157081.5241 |  | 35 |  | 55831.6298 | Q7 | 62.4 | 636.9 | 39742.56 |  | 108218.6048 | 203792.7946 |  | 55831.6298 | Q7 | 62.4 | 386 | 24086.4 |  | 77163.4943 |  | 157081.5241 |  | 35 |  | 55831.6298 | Q7 | 62.4 | 636.9 | 39742.56 |  | 108218.6048 | 203792.7946 | 0
[17 empty] | 15 |  |  |  |  | 15 | [5 empty] | 15 |  |  |  |  | 1.327 | 141075 | Q7 | 62.4 | 727 | 45364.8 |  | 180014.4749 | 366454.2749 |  | 35 |  | 141075 | Q7 | 62.4 | 1199.55 | 74851.92 |  | 245564.6653 | 461491.5853 |  | 141075 | Q7 | 62.4 | 727 | 45364.8 |  | 180014.4749 |  | 366454.2749 |  | 35 |  | 141075 | Q7 | 62.4 | 1199.55 | 74851.92 |  | 245564.6653 | 461491.5853 | 0
[17 empty] | 25 |  |  |  |  | 25 | [5 empty] | 25 |  |  |  |  | 1.327 | 184062.5 | Q7 | 62.4 | 1211.6667 | 75608 |  | 250720.6053 | 510391.1053 |  | 35 |  | 184062.5 | Q7 | 62.4 | 1999.25 | 124753.2 |  | 349934.3208 | 658750.0208 |  | 184062.5 | Q7 | 62.4 | 1211.6667 | 75608 |  | 250720.6053 |  | 510391.1053 |  | 35 |  | 184062.5 | Q7 | 62.4 | 1999.25 | 124753.2 |  | 349934.3208 | 658750.0208 | 0
[16 empty] | SHW Runout Insulation 90.1-2013 - by | No runout insulation required in base code 90.1-2013 | RSMeans 2018 mechanical 22 07 19.1 | Mineral wool: 1" wall on 3/4" CU pipe (use 1/2" IPS) |  |  | ea 8' runout | Addendum by requires first 8' of SHW runout piping to be insulated on recirculation or heat traced SHW systems. Priced per runout. 1" fiberglas insulation assumed. | RSMeans 2018 mechanical 22 07 19.1 | Mineral wool: 1" wall on 3/4" CU pipe (use 1/2" IPS) | 35 year life used as CU piping assumed, and located in areas not subject to wear; likely same as building life. |  | ea 8' runout insulated |  |  |  | SHW_runout | 1 | 0 | NA | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | NA | 0 | 0 | 0 |  | 0 | 0 |  | 13.2 | Q14 | 52.78 | 0.56 | 29.5568 |  | 34.8886 |  | 77.6454 | 0 | 35 |  | 13.2 | Q5 | 52.78 | 0.924 | 48.7687 |  | 61.4856 | 123.4543 | 77.6454
|  |  | Pumps |  | X |  | X | [8 empty] | Pumps General load impact and 90.1-16 an higher pump efficiency | Pumps for chilled, condenser and heating water. Based on most common type used. Without VFD. Pump efficiency 90.0% | Equipment and Labor from RS Means 2020 Mechanical Cost Data. General Utility Pumps centrifugal, end suction, mounted on base, horizontal mounted with drip proof motor, and accessories; Assembly D3020 330 & 340 |  |  |  | Flow, GPM | Similar to Base Code but pump efficiency 90.9% | Baseline costs are adjusted based on the appliance standards rulemaking dataset to develop a material cost premium |  |  |  | Flow, GPM |  |  |  |  | 2020 costs
[16 empty] | Pump_Flow | Pumps - costs from RS Means; secondary pumps with 50-70 ft of head
[17 empty] | Means 2020 Assembly D3020 330, page 536 | Means 2020 |  |  |  | 150 | Material cost premium = |  |  |  |  | 150 |  |  |  |  | 1 | 15700 | Q1 | 58 | 77.2201 | 4478.7645 |  | 11879.0334 | 32057.7978 |  | 20 |  | 15700 | Q1 | 58 | 127.4131 | 7389.9614 |  | 17938.5153 | 41028.4766 |  | 16233.8 | Q1 | 58 | 77.2201 | 4478.7645 |  | 12135.8979 |  | 32848.4624 | 0 | 20 |  | 16233.8 | Q1 | 58 | 127.4131 | 7389.9614 |  | 18274.4463 | 41898.2077 | 790.6646
[17 empty] | Includes basemounted pump, local piping, fittings, valve, strainer, expansion joints, gauges, control & electrical connection, balancing |  |  |  |  | 200 | 3.4% |  |  |  |  | 200 |  |  |  |  | 1 | 17967 | Q1 | 58 | 88.3205 | 5122.5869 |  | 13591.5166 | 36681.1034 |  | 20 |  | 17967 | Q1 | 58 | 145.7288 | 8452.2683 |  | 20523.5487 | 46942.817 |  | 18577.878 | Q1 | 58 | 88.3205 | 5122.5869 |  | 13885.471 |  | 37585.9359 | 0 | 20 |  | 18577.878 | Q1 | 58 | 145.7288 | 8452.2683 |  | 20907.9864 | 47938.1328 | 904.8325
[18 empty] | Means 2020 |  |  |  | 300 | [5 empty] | 300 |  |  |  |  | 1 | 20660 | Q1 | 58 | 106.6602 | 6186.2934 |  | 15914.3841 | 42760.6775 |  | 20 |  | 20660 | Q1 | 58 | 175.9894 | 10207.3842 |  | 24132.1279 | 54999.512 |  | 21362.44 | Q1 | 58 | 106.6602 | 6186.2934 |  | 16252.3982 |  | 43801.1316 | 0 | 20 |  | 21362.44 | Q1 | 58 | 175.9894 | 10207.3842 |  | 24574.1874 | 56144.0116 | 1040.4541
[18 empty] | Means 2020 |  |  |  | 1500 | [5 empty] | 1500 |  |  |  |  | 1 | 42491 | Q2 | 60.15 | 155.901 | 9377.4432 |  | 29500.4781 | 81368.9213 |  | 20 |  | 42491 | Q2 | 60.15 | 257.2366 | 15472.7813 |  | 43612.3282 | 101576.1095 |  | 43935.694 | Q2 | 60.15 | 155.901 | 9377.4432 |  | 30195.6649 |  | 83508.8021 | 0 | 20 |  | 43935.694 | Q2 | 60.15 | 257.2366 | 15472.7813 |  | 44521.503 | 103929.9784 | 2139.8808
[18 empty] | Means 2020 |  |  |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1 | 52582 | Q2 | 60.15 | 188.0119 | 11308.9166 |  | 36221.0817 | 100111.9983 |  | 20 |  | 52582 | Q2 | 60.15 | 310.2197 | 18659.7124 |  | 53437.9025 | 124679.6149 |  | 54369.788 | Q2 | 60.15 | 188.0119 | 11308.9166 |  | 37081.3653 |  | 102760.0699 | 0 | 20 |  | 54369.788 | Q2 | 60.15 | 310.2197 | 18659.7124 |  | 54562.9932 | 127592.4936 | 2648.0716
[18 empty] | Means 2020 |  |  |  | 2500 | [5 empty] | 2500 |  |  |  |  | 1 | 62673 | Q2 | 60.15 | 368.5778 | 22169.9553 |  | 51563.0734 | 136406.0287 |  | 20 |  | 62673 | Q2 | 60.15 | 608.1534 | 36580.4263 |  | 79329.5471 | 178582.9734 |  | 64803.882 | Q2 | 60.15 | 368.5778 | 22169.9553 |  | 52588.4538 |  | 139562.2912 | 0 | 20 |  | 64803.882 | Q2 | 60.15 | 608.1534 | 36580.4263 |  | 80670.5538 | 182054.8621 | 3156.2624
[18 empty] | Means 2020 |  |  |  | 3000 | [5 empty] | 3000 |  |  |  |  | 1 | 72764 | Q2 | 60.15 | 411.3924 | 24745.2532 |  | 58905.2818 | 156414.535 |  | 20 |  | 72764 | Q2 | 60.15 | 678.7975 | 40829.6677 |  | 90313.4901 | 203907.1578 |  | 75237.976 | Q2 | 60.15 | 411.3924 | 24745.2532 |  | 60095.759 |  | 160078.9882 | 0 | 20 |  | 75237.976 | Q2 | 60.15 | 678.7975 | 40829.6677 |  | 91870.4127 | 207938.0564 | 3664.4533
[16 empty] | Pump_FlPri | Pumps - costs from RS Means; primary pumps with 25-40 ft of head
[17 empty] | Means 2020 Assembly D3020 340, page 536 | Prorated from 225 gpm based on Means 23 21 23.13 |  |  |  | 50 | [5 empty] | 50 |  |  |  |  | 1 | 8175 | Q1 | 58 | 57.2889 | 3322.7591 |  | 7141.894 | 18639.653 |  | 20 |  | 8175 | Q1 | 58 | 94.5268 | 5482.5524 |  | 11122.9978 | 24780.5502 |  | 8452.95 | Q1 | 58 | 57.2889 | 3322.7591 |  | 7275.6435 |  | 19051.3526 | 0 | 20 |  | 8452.95 | Q1 | 58 | 94.5268 | 5482.5524 |  | 11297.9173 | 25233.4197 | 411.6995
[17 empty] | but adjusted to smaller pump size for lower pump head required | Prorated from 225 gpm based on Means 23 21 23.13 |  |  |  | 90 | [5 empty] | 90 |  |  |  |  | 1 | 9000 | Q1 | 58 | 66.0414 | 3830.4028 |  | 8029.0079 | 20859.4107 |  | 20 |  | 9000 | Q1 | 58 | 108.9684 | 6320.1646 |  | 12555.5392 | 27875.7038 |  | 9306 | Q1 | 58 | 66.0414 | 3830.4028 |  | 8176.2551 |  | 21312.6579 | 0 | 20 |  | 9306 | Q1 | 58 | 108.9684 | 6320.1646 |  | 12748.1111 | 28374.2757 | 453.2472
[18 empty] | Means 2020 |  |  |  | 225 | [5 empty] | 225 |  |  |  |  | 1 | 11300 | Q1 | 58 | 77.2201 | 4478.7645 |  | 9761.7534 | 25540.5178 |  | 20 |  | 11300 | Q1 | 58 | 127.4131 | 7389.9614 |  | 15169.5073 | 33859.4686 |  | 11684.2 | Q1 | 58 | 77.2201 | 4478.7645 |  | 9946.6304 |  | 26109.5949 | 0 | 20 |  | 11684.2 | Q1 | 58 | 127.4131 | 7389.9614 |  | 15411.292 | 34485.4534 | 569.077
[17 empty] | Includes basemounted pump, local piping, fittings, valve, strainer, expansion joints, gauges, control & electrical connection, balancing |  |  |  |  | 350 | [5 empty] | 350 |  |  |  |  | 1 | 14100 | Q1 | 58 | 88.3205 | 5122.5869 |  | 11730.7162 | 30953.303 |  | 20 |  | 14100 | Q1 | 58 | 145.7288 | 8452.2683 |  | 18089.9683 | 40642.2366 |  | 14579.4 | Q1 | 58 | 88.3205 | 5122.5869 |  | 11961.4034 |  | 31663.3903 | 0 | 20 |  | 14579.4 | Q1 | 58 | 145.7288 | 8452.2683 |  | 18391.6643 | 41423.3326 | 710.0873
[18 empty] | Means 2020 |  |  |  | 1000 | [5 empty] | 1000 |  |  |  |  | 1 | 20900 | Q1 | 58 | 106.6602 | 6186.2934 |  | 16029.8721 | 43116.1655 |  | 20 |  | 20900 | Q1 | 58 | 175.9894 | 10207.3842 |  | 24283.1647 | 55390.5488 |  | 21610.6 | Q1 | 58 | 106.6602 | 6186.2934 |  | 16371.8128 |  | 44168.7062 | 0 | 20 |  | 21610.6 | Q1 | 58 | 175.9894 | 10207.3842 |  | 24730.3595 | 56548.3436 | 1052.5407
[18 empty] | Means 2020 |  |  |  | 2000 | [5 empty] | 2000 |  |  |  |  | 1 | 33962 | Q2 | 60.15 | 155.901 | 9377.4432 |  | 25396.3233 | 68735.7665 |  | 20 |  | 33962 | Q2 | 60.15 | 257.2366 | 15472.7813 |  | 38244.8579 | 87679.6393 |  | 35116.708 | Q2 | 60.15 | 155.901 | 9377.4432 |  | 25951.9688 |  | 70446.12 | 0 | 20 |  | 35116.708 | Q2 | 60.15 | 257.2366 | 15472.7813 |  | 38971.5388 | 89561.0281 | 1710.3535
[18 empty] | Means 2020 |  |  |  | 2750 | [5 empty] | 2750 |  |  |  |  | 1 | 46500 | Q2 | 60.15 | 188.0119 | 11308.9166 |  | 33294.4233 | 91103.3399 |  | 20 |  | 46500 | Q2 | 60.15 | 310.2197 | 18659.7124 |  | 49610.3782 | 114770.0906 |  | 48081 | Q2 | 60.15 | 188.0119 | 11308.9166 |  | 34055.2005 |  | 93445.1171 | 0 | 20 |  | 48081 | Q2 | 60.15 | 310.2197 | 18659.7124 |  | 50605.3332 | 117346.0455 | 2341.7772
|  |  | Hot water piping |  | X | [10 empty] | Heating Water Piping used for load changes | Heating water piping and insulation costs are calculated from the model output flow rates for the base and target models. The estimating process was developed in 2012, so cost factors were updated using a Means comparison from 2012 to 2020. No addenda directly affect heating water piping. The differences in cost are due just to changes in capacity. Costs were developed for a range of climates to cover the range of expected loads. Regressions are based on reheat coil flow related to total piping costs. | Solarc one line diagram component analysis. |  |  |  | Reheat coil Hot water flow, gpm Not current values; prior calculated values to develop the regressions | Cost is for all heating water piping including hot water to air handlers from boiler and terminal unit reheat. Estimate cost based on whole building prototype flow at zone reheat, air handling systems and plant equipment. No addenda directly affect this cost. Cost difference occurs only for differences in heating requirements. | Solarc one line diagram component analysis. |  |  |  | Reheat coil Hot water flow, gpm Not current values; prior calculated values to develop the regressions |  |  |  |  | Note: Inflation from 2012 to 2014 included in material and labor before regression is developed; Infl from 2014 to 2020
[17 empty] | Large Office | [6 empty] | Regression coefficents below used on prototype tab
[23 empty] | Large Office |  | y = -0.7891x2 + 1089.7x - 127182+cf_HW_Mat_I*##+cf_HW_Mat_x*##^2
[17 empty] | 1B Riyadh 90.1-2010 |  |  |  |  | 530.7 | 1B Riyadh 90.1-2013 | y = -0.7891x2 + 1089.7x - 127182 |  |  |  | 486.27 |  |  |  |  | 1.096 | 233055.3302 | Q-1 | 58 | 3587.5465 | 208077.6973 |  | 346182.094 | 787315.1216 | [12 empty] | 212559.7357 | Q-1 | 58 | 3587.5465 | 201456.4325 |  | 327012.4871 |  | 741028.6553 | [11 empty] | -46286.4663
[17 empty] | 2A Houston 90.1-2010 |  |  |  |  | 534.42 | 2A Houston 90.1-2013 | cf_HW_Mat_I | -127182 | cf_HW_Mat_I+cf_HW_Mat_x*##+cf_HW_Mat_x2*##^2 |  | 501.11 |  |  |  |  | 1.096 | 231889.7547 | Q-1 | 58 | 3579.7378 | 207624.7928 |  | 345018.2059 | 784532.7534 |  |  |  |  | Replacement values calculated on prototype tab | [7 empty] | 224336.6898 | Q-1 | 58 | 3579.7378 | 205188.7582 |  | 337957.6994 |  | 767483.1474 | [5 empty] | Replacement values calculated on prototype tab | [5 empty] | -17049.6059
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 478.42 | 3B El Paso 90.1-2013 | cf_HW_Mat_x | 1089.7 |  |  | 481.77 |  |  |  |  | 1.096 | 210170.1133 | Q-1 | 58 | 3422.7083 | 198517.0798 |  | 322684.8982 | 731372.0913 | [12 empty] | 211786.4609 | Q-1 | 58 | 3422.7083 | 201492.1395 |  | 326564.9059 |  | 739843.5063 | [11 empty] | 8471.415
[17 empty] | 3C San Francisco 90.1-2010 |  |  |  |  | 441.65 | 3C San Francisco 90.1-2013 | cf_HW_Mat_x2 | -0.7891 |  |  | 437.09 |  |  |  |  | 1.096 | 201371.7481 | Q-1 | 58 | 3372.8987 | 195628.1222 |  | 314410.7857 | 711410.656 | [12 empty] | 199674.3656 | Q-1 | 58 | 3372.8987 | 196570.0598 |  | 314262.0749 |  | 710506.5003 | [11 empty] | -904.1558
[17 empty] | 5A Chicago 90.1-2010 |  |  |  |  | 601.68 | 5A Chicago 90.1-2013 | y = 102.35x + 152141 | cf_HW_Lab_I+cf_HW_Lab_x*##+cf_HW_Lab_x2*##^2 |  |  | 576.47 |  |  |  |  | 1.096 | 242628.6199 | Q-1 | 58 | 3736.7504 | 216731.5252 |  | 360505.2038 | 819865.3489 | [12 empty] | 237810.675 | Q-1 | 58 | 3736.7504 | 212635.4103 |  | 353546.9703 |  | 803993.0555 | [11 empty] | -15872.2935
[17 empty] | 7 Duluth 90.1-2010 |  |  |  |  | 625.46 | 7 Duluth 90.1-2013 | cf_HW_Lab_I | 152141 | cf_HW_Lab_I+cf_HW_Lab_x*##+cf_HW_Lab_x2*##^2 |  | 598.02 |  |  |  |  | 1.096 | 243258.7652 | Q-1 | 58 | 3688.7314 | 213946.4217 |  | 358209.0493 | 815414.2362 | [12 empty] | 242605.0423 | Q-1 | 58 | 3688.7314 | 215264.837 |  | 359074.4358 |  | 816944.3151 | [11 empty] | 1530.0789
[17 empty] | 8 Fairbanks 90.1-2010 |  |  |  |  | 669.06 | 8 Fairbanks 90.1-2013 | cf_HW_Lab_x | 102.35 |  |  | 618.27 |  |  |  |  | 1.096 | 250198.4471 | Q-1 | 58 | 3738.3135 | 216822.1817 |  | 365311.7255 | 832332.3543 | [12 empty] | 243779.5637 | Q-1 | 58 | 3738.3135 | 215850.3634 |  | 360371.9455 |  | 820001.8726 | [11 empty] | -12330.4817
[24 empty] | cf_HW_Lab_x2 | 0
[17 empty] | Primary School |  |  |  |  | Reheat Coil GPM |  | Regression coefficents below used on prototype tab |  |  |  | Reheat Coil GPM |  |  |  |  | Note: Inflation from 2012 to 2014 included in material and labor before regression is developed; Infl from 2014 to 2020
[17 empty] | 1B Riyadh 90.1-2010 |  |  |  |  | 112.8054 | 1B Riyadh 90.1-2013 | y = 4.7569x2 - 768.94x + 63199 |  | cf_HW_PS_Mat_I+cf_HW_PS_Mat_x*##+cf_HW_PS_Mat_x2*##^2 |  | 98.4193 |  |  |  |  | 1.096 | 36699.6837 | Q-2 | 60.15 | 455.466 | 27396.2781 |  | 49329.1844 | 113425.1461 | [12 empty] | 33705.6193 | Q-2 | 60.15 | 432.8651 | 26036.8346 |  | 46150.1726 |  | 105892.6264 | [11 empty] | -7532.5197
[17 empty] | 2A Houston 90.1-2010 |  |  |  |  | 102.7261 | 2A Houston 90.1-2013 | cf_HW_PS_Mat_I | 63199 | cf_HW_PS_Mat_I+cf_HW_PS_Mat_x*##+cf_HW_PS_Mat_x2*##^2 |  | 96.5647 |  |  |  |  | 1.096 | 35914.5876 | Q-2 | 60.15 | 445.5546 | 26800.1074 |  | 48264.1636 | 110978.8586 | [12 empty] | 33468.4137 | Q-2 | 60.15 | 432.0787 | 25989.5309 |  | 45956.6287 |  | 105414.5733 | [11 empty] | -5564.2853
[17 empty] | 2B Phoenix 90.1-2010 |  |  |  |  | 109.907 | 2B Phoenix 90.1-2013 | cf_HW_PS_Mat_x | -768.94 |  |  | 96.0422 |  |  |  |  | 1.096 | 36787.6368 | Q-2 | 60.15 | 452.4241 | 27213.3088 |  | 49207.3593 | 113208.3049 |  |  |  |  | Replacement values calculated on prototype tab | [7 empty] | 33705.6193 | Q-2 | 60.15 | 432.8651 | 26036.8346 |  | 46150.1726 |  | 105892.6264 | [5 empty] | Replacement values calculated on prototype tab | [5 empty] | -7315.6785
[17 empty] | 3B El Paso 90.1-2010 |  |  |  |  | 97.518 | 3B El Paso 90.1-2013 | cf_HW_PS_Mat_x2 | 4.7569 |  |  | 86.614 |  |  |  |  | 1.096 | 32533.6186 | Q-2 | 60.15 | 438.7214 | 26389.0909 |  | 45759.6523 | 104682.3618 | [12 empty] | 32360.1153 | Q-2 | 60.15 | 426.6603 | 25663.6166 |  | 44951.0544 |  | 102974.7863 | [11 empty] | -1707.5754
[17 empty] | 3C San Francisco 90.1-2010 |  |  |  |  | 95.6616 | 3C San Francisco 90.1-2013 | y = 1.546x2 - 245.21x + 35280 |  | cf_HW_PS_Lab_I+cf_HW_PS_Lab_x*##+cf_HW_PS_Lab_x2*##^2 |  | 94.7518 |  |  |  |  | 1.096 | 33468.4137 | Q-2 | 60.15 | 432.0787 | 25989.5309 |  | 45956.6287 | 105414.5733 | [12 empty] | 32930.9133 | Q-2 | 60.15 | 430.3134 | 25883.3504 |  | 45519.0375 |  | 104333.3011 | [11 empty] | -1081.2722
[17 empty] | 5A Chicago 90.1-2010 |  |  |  |  | 105.175 | 5A Chicago 90.1-2013 | cf_HW_PS_Lab_I | 35280 | cf_HW_PS_Lab_I+cf_HW_PS_Lab_x*##+cf_HW_PS_Lab_x2*##^2 |  | 98.303 |  |  |  |  | 1.096 | 35914.5876 | Q-2 | 60.15 | 445.5546 | 26800.1074 |  | 48264.1636 | 110978.8586 | [12 empty] | 33468.4137 | Q-2 | 60.15 | 432.0787 | 25989.5309 |  | 45956.6287 |  | 105414.5733 | [11 empty] | -5564.2853
[17 empty] | 7 Duluth 90.1-2010 |  |  |  |  | 105.67 | 7 Duluth 90.1-2013 | cf_HW_PS_Lab_x | -245.21 |  |  | 97 |  |  |  |  | 1.096 | 33466.4836 | Q-2 | 60.15 | 436.449 | 26252.4087 |  | 46209.2308 | 105928.1231 | [12 empty] | 32930.9133 | Q-2 | 60.15 | 430.3134 | 25883.3504 |  | 45519.0375 |  | 104333.3011 | [11 empty] | -1594.822
[17 empty] | 8 Fairbanks 90.1-2010 |  |  |  |  | 114.124 | 8 Fairbanks 90.1-2013 | cf_HW_PS_Lab_x2 | 1.546 |  |  | 101.5412 |  |  |  |  | 1.096 | 37324.0913 | Q-2 | 60.15 | 452.9124 | 27242.683 |  | 49570.1429 | 114136.9172 | [12 empty] | 33468.4137 | Q-2 | 60.15 | 432.0787 | 25989.5309 |  | 45956.6287 |  | 105414.5733 | [11 empty] | -8722.3438
|  |  | CHW and CW piping |  | X | [10 empty] | Chilled Water and Condenser Water Piping Includes CHW and CW Flow Rates and Pipe Sizing used for load changes | Cost is for all chilled water (CHW) and condenser water (CW) piping including water to and from air handlers from chiller and cooling tower in the mechanical penthouse. No addenda directly affect this cost as pipe sizing . Cost difference occurs only for differences in cooling requirements. Note that the 90.1-2007 standard did not include requirements for sizing pipe relative to flow and they were added in 2010. Cost for piping network was increased for 2010 relative to typical practice prior to the 2010 requirements. The prior analysis by PNNL of pipe sizing relative to flow with the 2010 requirements is used for base and target costs. The 2007 numbers in the graphs are not used. Inflation factors from 2012 to 2020 are applied where used in the prototype costs | Solarc one line diagram component analysis. | Only 2010 material values are used. |  |  | flow, gpm from chilled water secondary pump | Base and target costs are the same, and in the prototype tabs, will be adjusted for change in sizing due to the changes in capacity and flow for CHW and CW piping. | Solarc one line diagram component analysis. | Only 2010 labor values are used. |  |  | flow, gpm from chilled water secondary pump |  |  |  | 2012 to 2020 Labor inflation adjustment, applied after regression results developed in 2012 | 2012 to 2020 Material inflation adjustment, applied after regression results developed in 2012 | [31 empty] | delta on size
[18 empty] | y = 97.923x - 34003 | CF_CHW_2010_Mat_I+CF_CHW_2010_Mat_x*##+CF_CHW_2010_Mat_x2*##^2 |  |  |  |  | y = 97.923x - 34003 | CF_CHW_2013_Mat_I+CF_CHW_2013_Mat_x*##+CF_CHW_2013_Mat_x2*##^2 | [9 empty] | Values shown are calculated for 2010 | [20 empty] | Values shown are calculated for 2010
[18 empty] | CF_CHW_2010_Mat_I | -34003 | CF_CHW_2010_Mat_I+CF_CHW_2010_Mat_x*##+CF_CHW_2010_Mat_x2*##^2 |  |  |  | CF_CHW_2013_Mat_I | -34003 | [6 empty] | inf_lab_CHW | inf_mat_CHW
[17 empty] | 8 Fairbanks 90.1-2010 | CF_CHW_2010_Mat_x | 97.923 |  |  | 1235 | 8 Fairbanks 90.1-2010 | CF_CHW_2013_Mat_x | 97.923 | CF_CHW_2013_Mat_I+CF_CHW_2013_Mat_x*##+CF_CHW_2013_Mat_x2*##^2 |  | 1235 |  |  |  | 1.137 | 0.619 | 90250.9795 | Q-1 | 58 | 494.2598 | 28667.066 |  | 20174.4945 | 139092.54 | [12 empty] | 90250.9795 | Q-1 | 58 | 494.2598 | 28667.066 |  | 20174.4945 |  | 139092.54 |  |  | 0 | [8 empty] | 0
[17 empty] | 3B El Paso 90.1-2010 | CF_CHW_2010_Mat_x2 | 0 |  |  | 1453 | 3B El Paso 90.1-2010 | CF_CHW_2013_Mat_x2 | 0 |  |  | 1453 |  |  |  | 1.137 | 0.619 | 103807.072 | Q-1 | 58 | 499.9812 | 28998.9095 |  | 19367.8698 | 152173.8513 | [12 empty] | 103807.072 | Q-1 | 58 | 499.9812 | 28998.9095 |  | 19367.8698 |  | 152173.8513 |  |  | 0 | [8 empty] | 0
[17 empty] | 7 Duluth 90.1-2010 | y = 1E-05x3 - 0.0854x2 + 222.14x - 160407 | CF_CHW_2010_Lab_I+CF_CHW_2010_Lab_x*##+CF_CHW_2010_Lab_x2*##^2+CF_CHW_2010_Lab_x3*##^3 |  |  | 1497 | 7 Duluth 90.1-2010 | y = 0.0028x2 - 6.6968x + 32805 | CF_CHW_2013_Lab_I+CF_CHW_2013_Lab_x*##+CF_CHW_2013_Lab_x2*##^2 |  |  | 1497 |  |  |  | 1.137 | 0.619 | 103807.072 | Q-1 | 58 | 499.9812 | 28998.9095 |  | 19367.8698 | 152173.8513 |  |  |  |  | Replacement values calculated on prototype tab | [7 empty] | 103807.072 | Q-1 | 58 | 499.9812 | 28998.9095 |  | 19367.8698 |  | 152173.8513 |  |  | 0 |  |  | Replacement values calculated on prototype tab | [5 empty] | 0
[17 empty] | 5A Chicago 90.1-2010 | CF_CHW_2010_Lab_I | 32805 | CF_CHW_2010_Lab_I+CF_CHW_2010_Lab_x*##+CF_CHW_2010_Lab_x2*##^2+CF_CHW_2010_Lab_x3*##^3 |  | 1831 | 5A Chicago 90.1-2010 | CF_CHW_2013_Lab_I | 32805 | CF_CHW_2013_Lab_I+CF_CHW_2013_Lab_x*##+CF_CHW_2013_Lab_x2*##^2 |  | 1831 |  |  |  | 1.137 | 0.619 | 158739.722 | Q-1 | 58 | 520.4424 | 30185.6595 |  | 15946.716 | 204872.0975 | [12 empty] | 158739.722 | Q-1 | 58 | 520.4424 | 30185.6595 |  | 15946.716 |  | 204872.0975 |  |  | 0 | [8 empty] | 0
[17 empty] | 3C San Francisco 90.1-2010 | CF_CHW_2010_Lab_x | -6.6968 |  |  | 1949 | 3C San Francisco 90.1-2010 | CF_CHW_2013_Lab_x | -6.6968 |  |  | 1949 |  |  |  | 1.137 | 0.619 | 157364.722 | Q-1 | 58 | 519.3217 | 30120.6595 |  | 15998.2729 | 203483.6544 | [12 empty] | 157364.722 | Q-1 | 58 | 519.3217 | 30120.6595 |  | 15998.2729 |  | 203483.6544 |  |  | 0 | [8 empty] | 0
[17 empty] | 2A Houston 90.1-2010 | CF_CHW_2010_Lab_x2 | 0.0028 |  |  | 1982 | 2A Houston 90.1-2010 | CF_CHW_2013_Lab_x2 | 0.0028 |  |  | 1982 |  |  |  | 1.137 | 0.619 | 158739.722 | Q-1 | 58 | 520.4424 | 30185.6595 |  | 15946.716 | 204872.0975 | [12 empty] | 158739.722 | Q-1 | 58 | 520.4424 | 30185.6595 |  | 15946.716 |  | 204872.0975 |  |  | 0 | [8 empty] | 0
[17 empty] | 1B Riyadh 90.1-2010 | CF_CHW_2010_Lab_x3 | 0 |  |  | 2763 | 1B Riyadh 90.1-2010 |  |  |  |  | 2763 |  |  |  | 1.137 | 0.619 | 233872.759 | Q-1 | 58 | 611.7459 | 35481.26 |  | 14813.2044 | 284167.2234 | [12 empty] | 233872.759 | Q-1 | 58 | 611.7459 | 35481.26 |  | 14813.2044 |  | 284167.2234 |  |  | 0 | [8 empty] | 0
90.1-16be | [15 empty] | CRAC efficiency 90.1-16 be | CRAC baseline efficiency CRAC units are serving the IT equipment and are hard sized based on the modeled IT equipment load basement units: 6 x 20 tons, SCOP 2.5, E+ COP 3.56 | material costs from Federal Appliance Standards rulemaking TSDs Labor from 2020 Means |  |  |  | 20 tons capacity, cost is per unit | Adds CRAC efficiency requirements CRAC units are serving the IT equipment and are hard sized based on the modeled IT equipment load basement units: 6 x 20 tons, SCOP 2.73, E+ COP 3.88 | material costs from Federal Appliance Standards rulemaking TSDs Labor from 2020 Means |  |  |  | 20 tons capacity, cost is per unit |  |  |  |  | 1 | 45178 |  |  |  | 3675 |  | 25287.822 | 74140.822 |  | 20 |  | 45178 |  |  |  | 6063.75 |  | 35043.4775 | 86285.2275 |  | 59962 |  |  |  | 3675 |  | 32401.8828 |  | 96038.8828 |  | 20 |  | 59962 |  |  |  | 6063.75 |  | 44347.3444 | 110373.0944 | 21898.0608
[17 empty] | other 12 units: 2.5 tons, SCOP 2.6, E+ COP 3.70 |  |  |  |  | 2.5 tons capacity, cost is per unit | other 12 units: 2.5 tons, SCOP 2.82, E+ COP 4.01 |  |  |  |  | 2.5 tons capacity, cost is per unit |  |  |  |  | 1 | 21974 |  |  |  | 1350 |  | 11877.2976 | 35201.2976 |  | 20 |  | 21974 |  |  |  | 2227.5 |  | 16257.5971 | 40459.0971 |  | 18421 |  |  |  | 1350 |  | 10167.594 |  | 29938.594 |  | 20 |  | 18421 |  |  |  | 2227.5 |  | 14021.6232 | 34670.1232 | -5262.7036
90.1-16bq | [15 empty] | Dry_Cooler | 90.1-16bq Dry cooler baseline efficiency Dry coolers are serving the IT equipment and are hard sized based on the modeled IT equipment load | Manufacturer on 90.1 committee estimates baseline material cost is 4% cheaper |  |  |  | 50 tons capacity | 90.1-16bq Adds dry cooler efficiency requirements Dry coolers are serving the IT equipment and are hard sized based on the modeled IT equipment load | Means 2020 Mechanical 23.65.33 Liquid Coolers |  |  |  | 50 tons capacity |  |  |  |  | 1 | 35040 | Q-6 | 61.19 | 12 | 734.28 | 0 | 17570.1865 | 53344.4665 | 0 | 20 |  | 35040 | Q-6 | 61.19 | 19.8 | 1211.562 | 0 | 23372.4891 | 59624.0511 |  | 36500 | Q-6 | 61.19 | 12 | 734.28 | 0 | 18272.7385 |  | 55507.0185 |  | 20 |  | 36500 | Q5 | 61.19 | 19.8 | 1211.562 | 0 | 24291.2963 | 62002.8583 | 2162.552
90.1-07af and 90.1-07cc | 6. HVAC | 6.5.4.5 and Table 6.5.4.5 | CHW, CW flow rates and pipe sizing |  | X | [10 empty] | CHW and CW Flow Rates and Pipe Sizing 90.1-07n and 90.1-07ca Note: Item includes no added cost in this section. Pipe sizing in general plant capacity section above includes the difference in pipe sizing between the two versions of 90.1. | 90.1 2007 does not include requirements for pipe sizing relative to design flow for chilled and condenser water piping. The baseline costs are based on an estimated typical design relationship between flow and pipe sizing which was developed for the savings analysis for 90.1-2010. | Solarc one line diagram component analysis. See Large Office HVAC example, and other worksheets |  |  |  |  | These addenda introduce pipe size requirements for different levels of chilled and condenser water flows. This applies only in the critical circuit (circuit with highest pressure drop). W174 90.1-2010 includes pipe sizing minimums relative to flow requirements. This cost estimate accounts for two changes between the 2007 and 2010 cases. 1. Change due to change in capacity and flow in the CHW and CW above under the costs associated with the change in plant capacity, using the typical practice baseline relationship between flow and pipe sizing. This isolated the capacity change related cost difference. This incremental cost will be included above on the general capacity change cost. 2. Change of cost due to change in the relationship of pipe size to flow due to addenda af/cc. This is the incremental cost between the pipe sizing for the 2010 case with the typical 2007 baseline pipe size to flow relationship, and the 2010 pipe size to flow relationship. This isolates the cost impact of the addendum. This incremental cost will be included below in this section. | [9 empty] | 1
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | Pump Differential Pressure Reset Control 90.1-07ak | Pumps are usually controlled with differential pressure control. The pressure setpoint is fixed over time after being set initially. No base cost. Individual pumps serving variable flow pumping systems with pump head exceeding 100 ft. and motor larger than 50 hp shall have controls such as VFD. VFD costs are calculated from the general load change listed VFD costs above and applied to the corresponding prototypes in the "HVAC Prototype Name" cost worksheets. . | [5 empty] | This addenda has a number of requirements that affect flow control in pumping systems for the 2010 case, primarily for chilled water pumping. Two items affect costs for the large office prototype, 1) VFDs for CHW pumps, and 2) differential pressure reset control. Differential pressure reset control means that the pumping system resets the pressure setpoint downward based on valve positions until one valve is nearly wide open. The 2007 case includes the CHW pump riding the curve providing variable flow but without a VFD and a constant differential pressure. Individual pumps serving variable flow pumping systems with motor larger than 5 hp shall have controls such as VFD. VFD costs are calculated from the general load change listed VFD costs above. | [9 empty] | 1
[16 empty] | Pump_Pressure_Control | [16 empty] | 1 | [38 empty] | 0
[23 empty] | 2 hours of programming and 2 hours of commissioning | Solarc | [8 empty] | 1 | [21 empty] | programming | 125 | 2 | 250 |  | 241.372 | 250 | 741.372 |  |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 741.372
90.1-07u | 6. HVAC | 6.5.5.3, Table 6.8.1G | Cooling tower efficiency |  | X | [9 empty] | Only need to validate two assumptions and provide cost if the assumptions are incorrect. : 1. Designers will go to axial to meet more stringent efficiency requirements. 2. Cost of axial cooling tower is less than or equal to centrifugal cooling tower same cooling capacity | Cooling Tower Efficiency 90.1-07u No added costs for this item. See descriptions. | Table 6.8.1G set minimum performance for propeller or axial fan cooling towers to 38.2 gpm per gallon. No costs shown here – see comments under 90.1-2010. | [5 empty] | This addendum increases the minimum efficiency of centrifugal fan cooling towers to 38.2 gallons/hp from 20 gpm per horsepower. This is the same efficiency required of axial fan cooling towers. According to members of the 90.1 mechanical committee the incremental cost of the change in 2010 efficiency requirement for cooling towers is negligible or a net savings, since projects will use axial fan cooling towers which will require about half the fan power, and therefore be about the same or lower cost as an equivalent capacity centrifugal fan cooling tower. Centrifugal cooling towers will continue to be used when needed for noise control, space limitations, etc. and in these cases are exempt from the higher efficiency requirements. This was confirmed by our cost estimating consultant | [9 empty] | 1 | [38 empty] | 0
90.1-07m | 6. HVAC | Table 6.8.1C | Chiller efficiency |  | X | [10 empty] | Chiller Efficiency 90.1-07m | 90.1-2007 code efficiency chillers, centrifugal. No cost shown here; accounted for under general plant capacity section above. | [5 empty] | Higher efficiency water cooled centrifugal chillers for 2010 standard. Per the Manufacture Representative, prior to (2009) 90.1 2007 implementation the chillers for that time period met the 2007 efficiencies. When 90.1 2010 went into effect, to meet the new standards VFD's were then incorporated into the chiller design. Models are based on centrifugal chillers meeting Path B efficiency. minimum 90.1-2010 Path B efficiency 0.639 kW/ton, IPLV 0.450 kWh/ton, 2010 efficiency for 150 tons to 300 tons. minimum 90.1-2010 Path B efficiency 0.600 kW/ton, IPLV 0.400 kWh/ton, 2010 efficiency for 300 tons to 600 tons Costs shown are incremental cost for chillers that meet Path B efficiency versus the 90.1-2007 efficiency requirements |  |  |  |  | Cooling Capacity |  |  |  |  | 1
[16 empty] | Cent_WC_Chiller_2010_eff | [16 empty] | 1
[24 empty] | Faithful+Gould with | Carrier | IPLV .468kW/ton 30XW |  | 200 |  |  |  |  | 1 | [20 empty] | 75000 | Labor same as for chiller with 90.1-2007 efficiency |  |  |  |  | 36090 | 0 | 111090 |  |  |  | 75000 | Q7 |  | 0 | 0 |  | 47199 | 122199 | 111090
[24 empty] | Aerco | Carrier | IPLV .468kW/ton 30XW |  | 299 |  | Are these |  |  | 1 | [20 empty] | 105000 | [5 empty] | 50526 | 0 | 155526 |  |  |  | 105000 | Q7 |  | 0 | 0 |  | 66078.6 | 171078.6 | 155526
[25 empty] | Carrier | IPLV .299kW/ton 23XRV |  | 300 |  | sizes |  |  | 1 | [20 empty] | 110000 | [5 empty] | 52932 | 0 | 162932 |  |  |  | 110000 | Q7 |  | 0 | 0 |  | 69225.2 | 179225.2 | 162932
[25 empty] | Carrier (pro rated- 450T) | IPLV .299kW/ton 23XRV |  | 400 |  | used? |  |  | 1 | [20 empty] | 133300 | [5 empty] | 64143.96 | 0 | 197443.96 |  |  |  | 133300 | Q7 |  | 0 | 0 |  | 83888.356 | 217188.356 | 197443.96
[25 empty] | Carrier (pro rated- 600T) | IPLV .299kW/ton 23XRV |  | 500 |  |  |  |  | 1 | [20 empty] | 162500 | [5 empty] | 78195 | 0 | 240695 |  |  |  | 162500 | Q7 |  | 0 | 0 |  | 102264.5 | 264764.5 | 240695
90.1-07-aj | 8. Power | 10.4.1, Tables 10.8A-C | Motor efficiency | X | X | X | X | X | X | X | X | X | X | X | X | Motor Efficiency 90.1-07aj | Fan and pump motors that just meet 90.1-2007 efficiency standards shown in 90.1-2007 Table 10.8 and under other parameters in this table. Totally enclosed, 1800 rpm motors selected for pricing. Motor HP shown under 90.1-2007 cost parameter. | Equipment information below. Labor from RS Means 2012 Electrical Cost Data, motors, 26 71 13.20 1800 rpm , totally enclosed |  | 2007 Efficiency |  | Power, HP | Fan and pump motors that just meet 90.1-2010 efficiency standards shown in 90.1-2010 Table 10.8b and in other parameters in this section. Totally enclosed, 1800 rpm motors selected for pricing. Motor HP shown under 90.1-2007 Cost Parameter. |  | type | Premium Eff. Super-E 90.1 2010 efficiency |  | Power, HP
Motor_Efficiency
[20 empty] | 82.5 |  | 1 |  | Baldor*Reliance | TEFC | 85.5 |  | 1 |  |  |  |  | 1 | 793.25 | R-1A | 55.23 | 6.132 | 338.6704 |  | 708.6941 | 1840.6144 |  | 18 |  | 793.25 | R-1A | 55.23 | 10.1178 | 558.8061 |  | 1108.5437 | 2460.5998 |  | 835 | R-1A | 55.23 | 6.132 | 338.6704 |  | 728.7842 | 0 | 1902.4545 |  | 18 |  | 835 | R-1A | 55.23 | 10.1178 | 558.8061 |  | 1134.8178 | 2528.6239 | 61.8401
[17 empty] | The Energy Independence and Security Act of 2007 (EISA) set the new efficiency requirements that are now in 90.1-2010. The cost difference for the cost-effectiveness analysis is based on the change in efficiency requirements when incorporated in 90.1. There is no current impact for the change, as motors are already meeting the Federal requirement. Motors compliant with 90.1-2007 efficiency requirement prior to requirements of EISA are estimated to be 5% less expensive than the EPACT 2005 90.1-2010 compliant motors. Quotes are for 90.1-2010 motors. | Faithful+Gould, conversation with Baldor representative. The impact when the Federal change went into effect was estimated to be about a 5% increase in price according to discussion with a Baldor representative. This was due to some increase in materials, copper, and to ramping up production of the premium efficiency motors they were already making. Cost estimate reflects a 5% discount from the current prices. |  | 84 |  | 1.5 | Because Baldor Manufacturing was producing Premium Eff Motors, (which meet the 90.1 2007 requirements) before FY 2008, there was no impact to meet 90.1 2007 eff ratings. Instituting that regulation required the public to only purchase Premium Eff. Motors. Labor from RS Means 2012 | " | TEFC | 86.5 |  | 1.5 |  |  |  |  | 1 | 831.25 | R-1A | 55.23 | 6.132 | 338.6704 |  | 726.9797 | 1896.9 |  | 18 |  | 831.25 | R-1A | 55.23 | 10.1178 | 558.8061 |  | 1132.4578 | 2522.5139 |  | 875 | R-1A | 55.23 | 6.132 | 338.6704 |  | 748.0322 | 0 | 1961.7025 |  | 18 |  | 875 | R-1A | 55.23 | 10.1178 | 558.8061 |  | 1159.9906 | 2593.7967 | 64.8025
[20 empty] | 84 |  | 2 |  | " | TEFC | 86.5 |  | 2 |  |  |  |  | 1 | 943.35 | R-1A | 55.23 | 6.475 | 357.6143 |  | 799.2123 | 2100.1765 |  | 18 |  | 943.35 | R-1A | 55.23 | 10.6837 | 590.0635 |  | 1237.0884 | 2770.502 |  | 993 | R-1A | 55.23 | 6.475 | 357.6143 |  | 823.1039 | 0 | 2173.7181 |  | 18 |  | 993 | R-1A | 55.23 | 10.6837 | 590.0635 |  | 1268.3342 | 2851.3977 | 73.5416
[20 empty] | 86.5 |  | 3 |  | " | TEFC | 89.5 |  | 3 |  |  |  |  | 1 | 965.2 | R-1A | 55.23 | 6.475 | 357.6143 |  | 809.7265 | 2132.5408 |  | 18 |  | 965.2 | R-1A | 55.23 | 10.6837 | 590.0635 |  | 1250.8391 | 2806.1026 |  | 1016 | R-1A | 55.23 | 6.475 | 357.6143 |  | 834.1715 | 0 | 2207.7857 |  | 18 |  | 1016 | R-1A | 55.23 | 10.6837 | 590.0635 |  | 1282.8085 | 2888.872 | 75.245
[20 empty] | 87.5 |  | 5 |  | " | TEFC | 89.5 |  | 5 |  |  |  |  | 1 | 1259.7 | R-1A | 55.23 | 6.475 | 357.6143 |  | 951.4399 | 2568.7542 |  | 18 |  | 1259.7 | R-1A | 55.23 | 10.6837 | 590.0635 |  | 1436.1738 | 3285.9373 |  | 1326 | R-1A | 55.23 | 6.475 | 357.6143 |  | 983.3435 | 0 | 2666.9577 |  | 18 |  | 1326 | R-1A | 55.23 | 10.6837 | 590.0635 |  | 1477.8977 | 3393.9612 | 98.2036
[20 empty] | 88.5 |  | 7.5 |  | " | TEFC | 91 |  | 7.5 |  |  |  |  | 1 | 1412.65 | R-1A | 55.23 | 6.825 | 376.9447 |  | 1043.7028 | 2833.2976 |  | 18 |  | 1412.65 | R-1A | 55.23 | 11.2613 | 621.9588 |  | 1567.2077 | 3601.8166 |  | 1487 | R-1A | 55.23 | 6.825 | 376.9447 |  | 1079.48 | 0 | 2943.4248 |  | 18 |  | 1487 | R-1A | 55.23 | 11.2613 | 621.9588 |  | 1613.9977 | 3722.9565 | 110.1272
[20 empty] | 89.5 |  | 10 |  | " | TEFC | 91.7 |  | 10 |  |  |  |  | 1 | 1935.15 | R-1A | 55.23 | 8.876 | 490.2215 |  | 1404.4971 | 3829.8686 |  | 18 |  | 1935.15 | R-1A | 55.23 | 14.6454 | 808.8654 |  | 2099.8349 | 4843.8503 |  | 2037 | R-1A | 55.23 | 8.876 | 490.2215 |  | 1453.5074 | 0 | 3980.7288 |  | 18 |  | 2037 | R-1A | 55.23 | 14.6454 | 808.8654 |  | 2163.9311 | 5009.7966 | 150.8602
[20 empty] | 91 |  | 15 |  | " | TEFC | 93 |  | 15 |  |  |  |  | 1 | 2346.5 | R-1A | 55.23 | 9.576 | 528.8825 |  | 1639.7655 | 4515.148 |  | 18 |  | 2346.5 | R-1A | 55.23 | 15.8004 | 872.6561 |  | 2428.2645 | 5647.4206 |  | 2470 | R-1A | 55.23 | 9.576 | 528.8825 |  | 1699.1937 | 0 | 4698.0762 |  | 18 |  | 2470 | R-1A | 55.23 | 15.8004 | 872.6561 |  | 2505.9855 | 5848.6416 | 182.9282
[20 empty] | 91 |  | 20 |  | " | TEFC | 93 |  | 20 |  |  |  |  | 1 | 3134.05 | R-1A | 55.23 | 10.276 | 567.5435 |  | 2056.0613 | 5757.6548 |  | 18 |  | 3134.05 | R-1A | 55.23 | 16.9554 | 936.4467 |  | 2993.4443 | 7063.9411 |  | 3299 | R-1A | 55.23 | 10.276 | 567.5435 |  | 2135.4352 | 0 | 6001.9787 |  | 18 |  | 3299 | R-1A | 55.23 | 16.9554 | 936.4467 |  | 3097.2507 | 7332.6974 | 244.3239
[20 empty] | 91.7 |  | 25 |  | " | TEFC | 93.6 |  | 25 |  |  |  |  | 1 | 3648.95 | R-1A | 55.23 | 10.5 | 579.915 |  | 2315.7757 | 6544.6407 |  | 18 |  | 3648.95 | R-1A | 55.23 | 17.325 | 956.8597 |  | 3339.7401 | 7945.5498 |  | 3841 | R-1A | 55.23 | 10.5 | 579.915 |  | 2408.1902 | 0 | 6829.1052 |  | 18 |  | 3841 | R-1A | 55.23 | 17.325 | 956.8597 |  | 3460.601 | 8258.4607 | 284.4645
[20 empty] | 92.4 |  | 30 |  | " | TEFC | 94.1 |  | 30 |  |  |  |  | 1 | 4864.95 | R-1A | 55.23 | 12.775 | 705.5633 |  | 3022.2268 | 8592.74 |  | 18 |  | 4864.95 | R-1A | 55.23 | 21.0787 | 1164.1794 |  | 4331.0595 | 10360.1888 |  | 5121 | R-1A | 55.23 | 12.775 | 705.5633 |  | 3145.4381 | 0 | 8972.0013 |  | 18 |  | 5121 | R-1A | 55.23 | 21.0787 | 1164.1794 |  | 4492.1968 | 10777.3762 | 379.2613
[20 empty] | 93 |  | 40 |  | " | TEFC | 94.1 |  | 40 |  |  |  |  | 1 | 5308.6 | R-1A | 55.23 | 14.525 | 802.2157 |  | 3329.028 | 9439.8438 |  | 18 |  | 5308.6 | R-1A | 55.23 | 23.9662 | 1323.656 |  | 4784.1544 | 11416.4104 |  | 5588 | R-1A | 55.23 | 14.525 | 802.2157 |  | 3463.4753 | 0 | 9853.691 |  | 18 |  | 5588 | R-1A | 55.23 | 23.9662 | 1323.656 |  | 4959.9864 | 11871.6424 | 413.8473
[20 empty] | 93 |  | 50 |  | " | TEFC | 94.5 |  | 50 |  |  |  |  | 1 | 7653.2 | R-1A | 55.23 | 16.275 | 898.8682 |  | 4550.5663 | 13102.6346 |  | 18 |  | 7653.2 | R-1A | 55.23 | 26.8538 | 1483.1326 |  | 6433.5552 | 15569.8878 |  | 8056 | R-1A | 55.23 | 16.275 | 898.8682 |  | 4744.3937 | 0 | 13699.262 |  | 18 |  | 8056 | R-1A | 55.23 | 26.8538 | 1483.1326 |  | 6687.0453 | 16226.1779 | 596.6274
[20 empty] | 93.6 |  | 60 |  | " | TEFC | 95 |  | 60 |  |  |  |  | 1 | 8958.5 | R-1A | 55.23 | 18.9 | 1043.847 |  | 5318.652 | 15320.999 |  | 18 |  | 8958.5 | R-1A | 55.23 | 31.185 | 1722.3475 |  | 7515.8523 | 18196.6999 |  | 9430 | R-1A | 55.23 | 18.9 | 1043.847 |  | 5545.5378 | 0 | 16019.3848 |  | 18 |  | 9430 | R-1A | 55.23 | 31.185 | 1722.3475 |  | 7812.5767 | 18964.9243 | 698.3858
[20 empty] | 94.1 |  | 75 |  | " | TEFC | 95 |  | 75 |  |  |  |  | 1 | 10850.9 | R3 | 61.12 | 23.45 | 1433.264 |  | 6605.2523 | 18889.4163 |  | 18 |  | 10850.9 | R3 | 61.12 | 38.6925 | 2364.8856 |  | 9407.4164 | 22623.202 |  | 11422 | R3 | 61.12 | 23.45 | 1433.264 |  | 6880.0656 | 0 | 19735.3296 |  | 18 |  | 11422 | R3 | 61.12 | 38.6925 | 2364.8856 |  | 9766.8211 | 23553.7067 | 845.9133
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | ECM Motors 90.1-10aj | For Stand Alone Retail, for 90.1-2010 a programmable thermostat or thermostat with a timed lockout are adequate to meet the vestibule heating control requirements. | [5 empty] | Adding an outside air lockout will not add any additional complexity if there is a DDC system in place. Otherwise, the required control can be obtained with a series outside air lockout combined with electro-mechanical controls. A setpoint limit or locking cover is also required. | [5 empty] | HP | Shaft W
[16 empty] | ECM_Motor_1/12 | Shaded Pole | Grainger |  |  |  |  | ECM motor actullly 1/10 HP | Grainger | No labor as this comes integrated into a product |  | 0.58378 |  | 0.083333 | 62.1417 |  | ECM_Motor_1/12 | 1 | 216 | 1 Elec | 61.35 | 0 | 0 |  | 103.9392 | 319.9392 |  | 15 |  | 216 | 1 Elec | 61.35 | 0 | 0 |  | 135.9331 | 351.9331 |  | 370 | 1 Elec | 61.35 | 0 | 0 |  | 178.044 |  | 548.044 | 0 | 15 |  | 370 | 1 Elec | 61.35 | 0 | 0 |  | 232.8484 | 602.8484 | 228.1048
[16 empty] | ECM_Motor_1/3 | Shaded Pole | Grainger |  |  |  |  | ECM motor | Grainger |  |  | 0.62326 |  | 0.33333 | 248.5667 |  | ECM_Motor_1/3 | 1 | 201 | 1 Elec | 61.35 | 0 | 0 |  | 96.7212 | 297.7212 |  | 15 |  | 201 | 1 Elec | 61.35 | 0 | 0 |  | 126.4933 | 327.4933 |  | 322.5 | 1 Elec | 61.35 | 0 | 0 |  | 155.187 |  | 477.687 | 0 | 15 |  | 322.5 | 1 Elec | 61.35 | 0 | 0 |  | 202.9557 | 525.4557 | 179.9658
[16 empty] | ECM_Motor_1/2 | PSC | Grainger | Marathon OEM 048A11O1062 |  |  |  | ECM motor | Grainger |  |  | 0.60352 |  | 0.5 | 372.85 |  | ECM_Motor_1/2 | 1 | 213 | 1 Elec | 61.35 | 0 | 0 |  | 102.4956 | 315.4956 |  | 15 |  | 213 | 1 Elec | 61.35 | 0 | 0 |  | 134.0452 | 347.0452 |  | 387.5 | 1 Elec | 61.35 | 0 | 0 |  | 186.465 |  | 573.965 | 0 | 15 |  | 387.5 | 1 Elec | 61.35 | 0 | 0 |  | 243.8615 | 631.3615 | 258.4694
[16 empty] | ECM_Motor_3/4 | PSC | Grainger | Marathon OEM 048A110697 |  |  |  | ECM motor | Grainger |  |  | 0.60352 |  | 0.75 | 559.275 |  | ECM_Motor_3/4 | 1 | 220.75 | 1 Elec | 61.35 | 0 | 0 |  | 106.2249 | 326.9749 |  | 15 |  | 220.75 | 1 Elec | 61.35 | 0 | 0 |  | 138.9224 | 359.6724 |  | 404.75 | 1 Elec | 61.35 | 0 | 0 |  | 194.7657 |  | 599.5157 | 0 | 15 |  | 404.75 | 1 Elec | 61.35 | 0 | 0 |  | 254.7173 | 659.4673 | 272.5408
[16 empty] | ECM_Motor_1 | PSC | Grainger | Century OLE1106H |  |  |  | ECM motor | Grainger |  |  | 0.60352 |  | 1 | 745.7 |  | ECM_Motor_1 | 1 | 386 | 1 Elec | 61.35 | 0 | 0 |  | 185.7432 | 571.7432 |  | 15 |  | 386 | 1 Elec | 61.35 | 0 | 0 |  | 242.9175 | 628.9175 |  | 518 | 1 Elec | 61.35 | 0 | 0 |  | 249.2616 |  | 767.2616 | 0 | 15 |  | 518 | 1 Elec | 61.35 | 0 | 0 |  | 325.9878 | 843.9878 | 195.5184
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | Vestibule Controls 90.1-10ca | For Stand Alone Retail, for 90.1-2010 a programmable thermostat or thermostat with a timed lockout are adequate to meet the vestibule heating control requirements. | [5 empty] | Adding an outside air lockout will not add any additional complexity if there is a DDC system in place. Otherwise, the required control can be obtained with a series outside air lockout combined with electro-mechanical controls. A setpoint limit or locking cover is also required.
[16 empty] | Vestibule_Control | Heating thermostat | 2014 Means Mechanical 23 09 53.10 |  |  |  |  | Heating thermostat with outside air lockout and wiring; locking thermostat cover | 2014 Means Mechanical 23 09 53.10 | [7 empty] | Vestibule_Control | 1 | 158 | 1 Elec | 61.35 | 1 | 61.35 |  | 135.2623 | 354.6123 |  | 15 |  | 158 | 1 Elec | 61.35 | 1.65 | 101.2275 |  | 209.8135 | 469.041 |  | 231.3 | 1 Elec | 61.35 | 2 | 122.7 |  | 229.7669 |  | 583.7669 | 0 | 15 |  | 231.3 | 1 Elec | 61.35 | 1.65 | 101.2275 |  | 255.9426 | 588.4701 | 229.1546
0
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | Optimum Start Controls & DDC 90.1-10aa 90.1-10cb | For most building prototypes, DDC controls were generally required to meet the control requirements. For Stand Alone Retail, for 90.1-2010 programmable thermostats are adequate to meet the control requirements. | [5 empty] | For most building prototypes, the increased requirements for optimum start control will not add any additional complexity if there is a DDC system in place. For Stand Alone Retail, Addendum 90.1-10aa requires DDC control of the units. While it is not appropriate to include the entire front end cost of a DDC system for the optimum start addenda, the difference in unit controls is captured. For 90.1-2013 DDC zone controllers are used for each package unit to meet the control requirements.
[16 empty] | Optimum_Start_Control | Programmable thermostat | 2014 Means Mechanical 23 09 53.10 |  |  |  |  | Zone controller adapted to unitary system | 2014 Means Mechanical 23 09 23.10 | [7 empty] | Optimum_Start_Control | 1 | 249 | 1 Elec | 61.35 | 1 | 61.35 |  | 179.0515 | 489.4015 |  | 15 |  | 249 | 1 Elec | 61.35 | 1.65 | 101.2275 |  | 267.0816 | 617.3091 |  | 660 | 1 Elec | 61.35 | 1.2225 | 75 |  | 390.0036 |  | 1125.0036 | 0 | 15 |  | 660 | 1 Elec | 61.35 | 1.65 | 101.2275 |  | 525.7321 | 1286.9596 | 635.6021
90.1-07ak | 90.1-07ak | 6. HVAC | 6.5.4.1 | [12 empty] | Door Switch Control 90.1-10ba | No requirements for door control; programmable thermostat required | [5 empty] | Add door switch. The control requirements are very similar to typical occupancy sensor controlled thermostats and the cost of a door switch (Kele) was found to be quite similar to a door switch. | PECI, and Taylor Engineering. “Light Commercial Unitary HVAC, 2013 California Building Energy Efficiency Standards, CODES AND STANDARDS ENHANCEMENT INITIATIVE (CASE).” California Utilities Statewide Codes and Standards Team for California Energy Commission, November 2011. http://www.energy.ca.gov/title24/2013standards/prerulemaking/documents/current/Reports/Nonresidential/HVAC/2013_CASE_NR_Light_Commercial_Unitary_UPDATED_Nov_2011.pdf. | Multiple | [7 empty] | Inflation adjustment only for target code
[16 empty] | Door_Switch_Control | Standard Programmable thermostat | [5 empty] | Adaptive programmable thermostat with door switch | [8 empty] | Door_Switch_Control | 1.0462 | 249 | 1 Elec | 61.35 | 1 | 61.35 |  | 179.0515 | 489.4015 |  | 15 |  | 249 | 1 Elec | 61.35 | 1.65 | 101.2275 |  | 285.8324 | 636.0599 |  | 358 | 1 Elec | 61.35 | 1.5 | 92.025 |  | 285.6269 |  | 735.6519 | 0 | 15 |  | 358 | 1 Elec | 61.35 | 1.65 | 101.2275 |  | 362.6365 | 821.864 | 246.2504
90.1-10as
[16 empty] | Humidifier_Insulation | Humidifier injector array, uninsulated |  | Dri-STEEM |  |  |  | Humidifier injector array, with insulation | [8 empty] | Humidifier_Insulation | 1 | 3300 | Q-14 | 52.78 | 4 | 211.12 |  | 1791.7938 | 5302.9138 |  | 15 |  | 3300 | Q-14 | 52.78 | 6.6 | 348.348 |  | 2456.603 | 6104.951 |  | 5300 | Q-14 | 52.78 | 4.5 | 237.51 |  | 2779.6731 |  | 8317.1831 | 0 | 15 |  | 5300 | Q-14 | 52.78 | 6.6 | 348.348 |  | 3715.243 | 9363.591 | 3014.2692
Note on R3: Reid Hart: Recommend not changing the range name extensions at right, even though they do not match the current cycle. 2007 is the base code and 2010 is the target code.
Note on BJ6: Reid Hart: For 2016, incremental Cx removed as was only in target, and not in base; include Cx in labor for controls items.

## Adm_dd_Pump_VFD (hidden)
Chilled-Water Pumps in
These Climate Zones
Heating Water Pumps in
These Climate Zones Motor Nameplate Horsepower
0A, 0B, 1A, 1B, 2B NR 2 hp
2A, 3B NR 3 hp
3A, 3C, 4A, 4B 7, 8 5 hp
4C, 5A, 5B, 5C, 6A, 6B 3C, 5A, 5C, 6A, 6B 7.5 hp
4A, 4C, 5B 10 hp
7, 8 4B 15 hp
2A, 2B, 3A, 3B 25 hp
1B 100 hp
0A, 0B, 1A 200 hp
|  |  | 1.1 | 1.1
| Pump Motor Size |  | Theoretical HP
| CHW | HW | CHW | HW
0A | 2 | 200 | 1.8182 | 181.8182
0B | 2 | 200 | 1.8182 | 181.8182
1A | 2 | 200 | 1.8182 | 181.8182
1B | 2 | 100 | 1.8182 | 90.9091
2A | 3 | 25 | 2.7273 | 22.7273
2B | 2 | 25 | 1.8182 | 22.7273
3A | 5 | 25 | 4.5455 | 22.7273
3B | 3 | 25 | 2.7273 | 22.7273
3C | 5 | 7.5 | 4.5455 | 6.8182
4A | 5 | 10 | 4.5455 | 9.0909
4B | 5 | 15 | 4.5455 | 13.6364
4C | 7.5 | 10 | 6.8182 | 9.0909
5A | 7.5 | 7.5 | 6.8182 | 6.8182
5B | 7.5 | 10 | 6.8182 | 9.0909
5C | 7.5 | 7.5 | 6.8182 | 6.8182
6A | 7.5 | 7.5 | 6.8182 | 6.8182
6B | 7.5 | 7.5 | 6.8182 | 6.8182
7 | 15 | 5 | 13.6364 | 4.5455
8 | 15 | 5 | 13.6364 | 4.5455
90.1-16 dd; VSD required on pump above thresholds above
Look_Adm_dd_pump_VFD

## HVAC_Data (hidden)
State Commercial Energy Code Cost Effectiveness - HVAC data
There are two table ranges in this sheet, upper table has current state data. |  | 2A |  | 3A |  | 3B |  | 4A |  | 5A
Current_HVAC_Data - upper table starting in column B, one set of current state HVAC data
State_HVAC_Data - lower table includes all state data - replacement data can be pasted in column B starting below Current_HVAC_ Data
Current State | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
US National |  | Climate Zone 1 |  | Climate Zone 2 |  | Climate Zone 3 |  | Climate Zone 4 |  | Climate Zone 5
US |  | ZoneXX(City) Base Code | ZoneXX(City) Target Code | ZoneXX(City) Base Code | ZoneXX(City) Target Code | ZoneXX(City) Base Code | ZoneXX(City) Target Code | ZoneXX(City) Base Code | ZoneXX(City) Target Code | ZoneXX(City) Base Code | ZoneXX(City) Target Code
OfficeSmall | OfficeSmall
Names used to place data from State_HVAC_Data to Current_State_Data
US_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0555 | 1.9588 | 1.9522 | 1.8608 | 1.8175 | 1.7154 | 1.8066 | 1.715 | 1.6903 | 1.5992
US_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9302 | 1.8385 | 1.7058 | 1.6451 | 1.7105 | 1.6322 | 1.5726 | 1.5114 | 1.4189 | 1.3589
US_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3124 | 1.2654 | 1.1625 | 1.1214 | 1.1607 | 1.1104 | 1.094 | 1.0559 | 1.0291 | 0.99128
US_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8943 | 1.8025 | 1.7056 | 1.63 | 1.7121 | 1.617 | 1.5 | 1.432 | 1.3448 | 1.2655
US_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4849 | 1.4346 | 1.3222 | 1.28 | 1.4014 | 1.348 | 1.2698 | 1.2309 | 1.2064 | 1.1677
US_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 699.2304 | 656.8528 | 783.9856 | 741.608 | 635.664 | 593.2864 | 635.664 | 593.2864
US_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 635.664 | 593.2864 | 762.7968 | 720.4192 | 572.0976 | 550.9088 | 550.9088 | 508.5312
US_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 466.1536 | 444.9648 | 529.72 | 508.5312 | 444.9648 | 423.776 | 444.9648 | 423.776
US_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 593.2864 | 762.7968 | 720.4192 | 529.72 | 508.5312 | 508.5312 | 466.1536
US_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 529.72 | 508.5312 | 635.664 | 614.4752 | 508.5312 | 487.3424 | 529.72 | 508.5312
US_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178
US_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925
US_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711
US_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925
US_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711
US_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 9.4366 | 9.4366 | 11.9094 | 11.9094 | 10.4584 | 10.4584 | 13.5199 | 13.5199 | 14.6431 | 14.6431
US_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 9.9139 | 9.5655 | 17.473 | 17.2425 | 14.1799 | 13.9661 | 19.4077 | 19.2146 | 21.004 | 20.7691
US_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 6.0234 | 5.8221 | 10.7537 | 10.6262 | 8.6701 | 8.5472 | 11.9549 | 11.848 | 12.769 | 12.6451
US_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 9.7186 | 9.4206 | 17.3127 | 17.1137 | 14.0032 | 13.8214 | 19.3277 | 19.1609 | 20.8017 | 20.6095
US_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 6.0234 | 5.8221 | 10.8068 | 10.6723 | 8.6358 | 8.5175 | 12.0086 | 11.8958 | 12.8307 | 12.7006
OfficeLarge
Zone, City, Code
US_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12014.0496 | 11166.4976 | 11886.9168 | 10996.9872 | 13391.3216 | 12395.448 | 11611.4624 | 10742.7216 | 11780.9728 | 10891.0432
US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18963.976 | 18010.48 | 19387.752 | 18413.0672 | 22036.352 | 20955.7232 | 19620.8288 | 18688.5216 | 19790.3392 | 18858.032
US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 174849.9779 | 165738.7939 | 179638.6467 | 170273.1971 | 204683.8083 | 194364.8627 | 182986.4771 | 174129.5587 | 183600.9523 | 174595.7123
US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18497.8224 | 17650.2704 | 18963.976 | 18137.6128 | 22142.296 | 21209.9888 | 18985.1648 | 18201.1792 | 19133.4864 | 18349.5008
US_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes
US_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255
US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174
US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396
US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174
US_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654
US_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 438.8299 | 391.2284 | 406.1299 | 365.9173 | 337.4605 | 311.9875 | 402.5817 | 336.3811 | 371.5931 | 339.1105
US_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 438.8299 | 391.2284 | 406.1299 | 365.9173 | 337.4605 | 311.9875 | 402.5817 | 336.3811 | 371.5931 | 339.1105
US_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 416.5333 | 371.3501 | 385.4879 | 347.3277 | 320.5792 | 296.3791 | 382.1274 | 319.2884 | 352.7198 | 321.8836
US_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 416.5333 | 371.3501 | 385.4879 | 347.3277 | 320.5792 | 296.3791 | 382.1274 | 319.2884 | 352.7198 | 321.8836
US_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.338 | 4.0326 | 5.5056 | 5.0972 | 5.0875 | 4.7251 | 5.9876 | 5.5199 | 6.4105 | 5.8555
US_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
US_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 688.9739 | 613.9337 | 639.96 | 573.7627 | 527.5495 | 487.632 | 634.3299 | 526.9345 | 585.2605 | 534.0085
US_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 688.9739 | 613.9337 | 639.96 | 573.7627 | 527.5495 | 487.632 | 634.3299 | 526.9345 | 585.2605 | 534.0085
US_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1377.9463 | 1227.8691 | 1279.9215 | 1147.5238 | 1055.1005 | 975.2656 | 1268.6614 | 1053.869 | 1170.5194 | 1068.017
US_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 890.4236 | 827.7387 | 1130.0948 | 1046.2719 | 1044.2843 | 969.886 | 1229.0404 | 1133.0413 | 1315.8368 | 1201.9189
US_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2420.9784 | 2158.497 | 2240.6017 | 2018.8557 | 1861.779 | 1721.1866 | 2221.1058 | 1855.7558 | 2050.0808 | 1870.8136
US_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.6949 | 207.8072 | 209.3162 | 208.4508 | 223.442 | 222.4688 | 207.4443 | 206.6169 | 208.9992 | 208.1591
US_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve
US_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.7168 | 3.2792 | 3.4524 | 3.0646 | 2.8459 | 2.6046 | 3.422 | 2.8145 | 3.1573 | 2.8523
US_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.7168 | 3.2792 | 3.4524 | 3.0646 | 2.8459 | 2.6046 | 3.422 | 2.8145 | 3.1573 | 2.8523
US_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.3006 | 19.675 | 20.7142 | 18.3876 | 17.0757 | 15.6274 | 20.5319 | 16.8869 | 18.9436 | 17.1136
US_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.247 | 17.7149 | 24.4277 | 22.3919 | 22.5728 | 20.7571 | 26.5664 | 24.2489 | 28.4426 | 25.7229
US_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.3467 | 38.2621 | 40.1167 | 35.7867 | 33.3337 | 30.5124 | 39.7662 | 32.898 | 36.7052 | 33.165
US_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5033 | 4.4398 | 4.5168 | 4.4535 | 4.8216 | 4.753 | 4.4764 | 4.4144 | 4.5099 | 4.4473
US_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5033 | 4.4398 | 4.5168 | 4.4535 | 4.8216 | 4.753 | 4.4764 | 4.4144 | 4.5099 | 4.4473
US_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 333.7229 | 308.8504 | 438.5215 | 420.6112 | 398.3272 | 378.7423 | 468.5349 | 451.3102 | 490.0421 | 470.7384
US_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD
US_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | VFD | No | VFD
US_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.4648 | 122.1084 | 123.007 | 122.6466 | 131.6564 | 131.2668 | 121.5049 | 121.1445 | 122.0827 | 121.7198
US_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6497 | 2.623 | 2.6194 | 2.6185 | 2.7947 | 2.7651 | 2.6393 | 2.616 | 2.6839 | 2.6602
US_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.1989 | 24.9535 | 25.17 | 24.9168 | 26.5498 | 26.2782 | 25.2438 | 25.0406 | 25.7149 | 25.5063
US_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5595 | 2.5385 | 2.5325 | 2.5129 | 2.6748 | 2.6533 | 2.5698 | 2.5501 | 2.6144 | 2.5943
RetailStandalone
Zone, City, Code
US_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.3139 | 10.9459 | 10.5812 | 10.2412 | 10.5384 | 9.9057 | 10.4557 | 10.0917 | 9.5963 | 9.1249
US_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.2004 | 48.07 | 49.7758 | 47.6959 | 47.4616 | 45.3882 | 48.0092 | 46.2465 | 44.3772 | 42.4882
US_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8904 | 6.7656 | 6.4722 | 6.314 | 6.6327 | 6.4618 | 6.3493 | 6.1924 | 5.7425 | 5.5854
US_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.674 | 5.5415 | 5.2462 | 5.0929 | 5.2991 | 5.1178 | 5.1749 | 5.0213 | 4.5449 | 4.3672
US_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4174.1936 | 3941.1168 | 4110.6272 | 3856.3616 | 4746.2912 | 4449.648 | 3983.4944 | 3729.2288 | 3771.6064 | 3474.9632
US_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15361.88 | 14429.5728 | 15446.6352 | 14514.328 | 17311.2496 | 16357.7536 | 15277.1248 | 14471.9504 | 15192.3696 | 14281.2512
US_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2267.2016 | 2309.5792 | 2224.824 | 2648.6 | 2563.8448 | 2288.3904 | 2224.824 | 2203.6352 | 2118.88
US_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1801.048 | 1737.4816 | 1758.6704 | 1673.9152 | 2055.3136 | 1970.5584 | 1758.6704 | 1695.104 | 1631.5376 | 1546.7824
US_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669
US_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282
US_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937
US_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937
US_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 170.1583 | 160.4069 | 171.6609 | 161.6468 | 174.7009 | 164.8895 | 177.1344 | 166.5616 | 169.417 | 156.6046
US_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 685.7061 | 648.3055 | 744.9252 | 707.8342 | 724.548 | 690.5645 | 798.8945 | 765.4864 | 818.6913 | 780.8617
US_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 98.7919 | 96.6704 | 101.9548 | 99.3168 | 102.0587 | 99.4843 | 108.5531 | 105.8788 | 106.1941 | 103.5014
US_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 79.1941 | 76.8838 | 82.1152 | 79.3613 | 82.4712 | 79.7979 | 88.5194 | 85.6493 | 85.2348 | 81.962
SchoolPrimary
Zone, City, Code
US_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.3372 | 18.3769 | 18.6648 | 18.1241 | 22.3173 | 21.0521 | 18.6852 | 18.1708 | 18.6048 | 18.1705
US_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.3534 | 18.3244 | 18.6162 | 18.0887 | 22.2412 | 20.7718 | 18.4688 | 18.1181 | 18.4894 | 18.1201
US_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.6857 | 16.5968 | 17.0455 | 16.154 | 20.3933 | 19.1327 | 16.9244 | 16.1545 | 16.8958 | 16.0741
US_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.3715 | 24.6347 | 25.9969 | 24.3878 | 25.9879 | 23.5162 | 25.4842 | 23.9792 | 25.5787 | 23.2415
US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3841 | 8.007 | 8.4249 | 8.1504 | 8.4035 | 8.104 | 8.1363 | 7.8751 | 7.7875 | 7.5294
US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.284 | 5.1223 | 5.2586 | 5.0915 | 5.8861 | 5.8324 | 5.2082 | 5.292 | 5.3411 | 5.318
US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074
US_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | 5593.8432 | 5445.5216 | 6695.6608 | 6314.2624 | 5615.032 | 5445.5216 | 5572.6544 | 5445.5216
US_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | 5593.8432 | 5424.3328 | 6674.472 | 6229.5072 | 5551.4656 | 5445.5216 | 5551.4656 | 5445.5216
US_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5297.2 | 4979.368 | 5106.5008 | 4852.2352 | 6123.5632 | 5742.1648 | 5085.312 | 4852.2352 | 5064.1232 | 4831.0464
US_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7903.4224 | 7394.8912 | 7797.4784 | 7310.136 | 9174.7504 | 8623.8416 | 7649.1568 | 7204.192 | 7670.3456 | 7183.0032
US_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1546.7824 | 1567.9712 | 1525.5936 | 1801.048 | 1779.8592 | 1567.9712 | 1589.16 | 1610.3488 | 1589.16
US_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2585.0336 | 2457.9008 | 2881.6768 | 2754.544 | 2521.4672 | 2415.5232 | 2563.8448 | 2457.9008
US_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312
US_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes
US_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5802.786 | 5514.5971 | 5598.6531 | 5438.7412 | 6697.0593 | 6282.2673 | 5607.1074 | 5452.747 | 5581.9563 | 5452.6622
US_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5807.5958 | 5498.8538 | 5584.5413 | 5428.1256 | 6671.103 | 6233.2788 | 5542.1849 | 5436.919 | 5548.3509 | 5437.5546
US_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5304.6161 | 4980.4486 | 5112.476 | 4847.5313 | 6119.7068 | 5422.002 | 5078.7435 | 4847.7008 | 5070.1408 | 4823.5668
US_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921
US_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343
US_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601
US_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841
US_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes
US_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.64826 | 0.6009 | 0.90587 | 0.86434 | 0.86403 | 0.80043 | 1.015 | 0.97432 | 1.1154 | 1.0753
US_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 66.5317 | 61.6715 | 92.9713 | 88.7089 | 88.677 | 82.1491 | 104.1747 | 99.9964 | 114.4758 | 110.3566
US_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.5609 | 8.1357 | 8.2632 | 8.0238 | 9.8802 | 9.32 | 8.2722 | 8.0444 | 8.2366 | 8.0443
US_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.568 | 8.1125 | 8.2417 | 8.0081 | 9.8465 | 9.1959 | 8.1764 | 8.0211 | 8.1855 | 8.022
US_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.8297 | 7.3476 | 7.5463 | 7.1516 | 9.0284 | 8.4703 | 7.4927 | 7.1518 | 7.48 | 7.1162
US_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.5866 | 10.8235 | 11.422 | 10.715 | 13.4264 | 12.6363 | 11.1967 | 10.5355 | 11.2382 | 10.51
US_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.4381 | 1.3199 | 2.0096 | 1.8985 | 1.9168 | 1.7581 | 2.2518 | 2.1401 | 2.4745 | 2.3618
US_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 191.0964 | 182.2854 | 200.3862 | 191.6855 | 199.9799 | 191.3774 | 207.8681 | 199.3018 | 212.0964 | 203.5478
US_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 95.463 | 93.6677 | 115.4488 | 113.6581 | 108.6449 | 107.927 | 129.005 | 129.936 | 139.527 | 139.2767
US_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 217.3157 | 217.3157 | 274.2625 | 274.2625 | 240.8457 | 240.8457 | 311.351 | 311.351 | 337.2181 | 337.2181
US_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 94.3097 | 93.4261 | 93.0721 | 92.1725 | 85.0563 | 84.1331 | 95.9294 | 95.578 | 94.7918 | 93.9035
HotelSmall
Zone, City, Code
US_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5999 | 2.4575 | 2.4415 | 2.3156 | 2.3849 | 2.2422 | 2.2772 | 2.1613 | 2.1107 | 1.9954
US_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2508 | 5.928 | 6.3213 | 5.9999 | 6.1359 | 5.8857 | 6.027 | 5.7233 | 5.7399 | 5.5082
US_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9807 | 2.8761 | 2.9994 | 2.9144 | 3.1725 | 3.0992 | 2.8701 | 2.7771 | 2.8701 | 2.7798
US_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.1652 | 6.1259 | 6.0419 | 6.0006 | 6.1247 | 6.0801 | 5.7874 | 5.7466 | 5.5467 | 5.5007
US_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 783.9856 | 826.3632 | 762.7968 | 953.496 | 889.9296 | 762.7968 | 720.4192 | 762.7968 | 699.2304
US_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1779.8592 | 1906.992 | 1801.048 | 2161.2576 | 2055.3136 | 1801.048 | 1716.2928 | 1801.048 | 1695.104
US_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 889.9296 | 868.7408 | 1017.0624 | 995.8736 | 868.7408 | 826.3632 | 868.7408 | 826.3632
US_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2224.824 | 2203.6352 | 2500.2784 | 2479.0896 | 2140.0688 | 2140.0688 | 2182.4464 | 2161.2576
US_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928
US_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133
US_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938
US_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629
US_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized
US_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No | No | No
US_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No | No | No
US_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb
US_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.8782 | 32.6536 | 35.3284 | 33.3906 | 35.4535 | 33.3905 | 35.7485 | 33.9662 | 35.6034 | 33.7618
US_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 85.0562 | 81.4933 | 93.0626 | 89.6407 | 91.5317 | 88.0944 | 97.5155 | 94.1622 | 100.0461 | 96.7146
US_SH_SAC_MEETINGROOM Heating Capacity [kBtu/hr] | SAC_MEETINGROOM Heating Capacity [kBtu/hr] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
US_SH_SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ApartmentMidRise
Zone, City, Code
US_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.98423 | 0.97375 | 0.86899 | 0.85871 | 0.83268 | 0.81943 | 0.83162 | 0.81763 | 0.74751 | 0.73308
US_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.94819 | 0.93774 | 0.84441 | 0.83404 | 0.82609 | 0.81272 | 0.79432 | 0.78088 | 0.70314 | 0.68933
US_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.832 | 1.7461 | 1.694 | 1.5722 | 1.8067 | 1.7039 | 1.6468 | 1.5121 | 1.5311 | 1.445
US_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84983 | 0.84053 | 0.75301 | 0.74161 | 0.73287 | 0.72042 | 0.69822 | 0.68633 | 0.59725 | 0.58515
US_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72462 | 0.71657 | 0.65014 | 0.64124 | 0.60991 | 0.59896 | 0.59683 | 0.58765 | 0.50669 | 0.49714
US_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.72294 | 0.71491 | 0.64857 | 0.63967 | 0.60819 | 0.59725 | 0.59496 | 0.58583 | 0.50447 | 0.49498
US_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.76065 | 0.75025 | 0.67117 | 0.66065 | 0.61633 | 0.604 | 0.63623 | 0.62578 | 0.55883 | 0.54822
US_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.79438 | 0.78111 | 0.70484 | 0.69203 | 0.66283 | 0.64704 | 0.67013 | 0.6531 | 0.59321 | 0.5778
US_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.022 | 1.9987 | 1.947 | 1.9263 | 1.8642 | 1.8361 | 1.9991 | 1.9677 | 1.8865 | 1.8546
US_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9548 | 1.9322 | 1.9117 | 1.8909 | 1.8413 | 1.8137 | 1.9266 | 1.8968 | 1.8064 | 1.7758
US_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8002 | 1.7769 | 1.69 | 1.671 | 1.6503 | 1.5596 | 1.7551 | 1.7277 | 1.6191 | 1.5901
US_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7014 | 1.68 | 1.6547 | 1.6357 | 1.5753 | 1.5503 | 1.6125 | 1.5831 | 1.4626 | 1.4334
US_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.41 | 1.3926 | 1.373 | 1.3558 | 1.2605 | 1.2388 | 1.3305 | 1.3128 | 1.1839 | 1.1656
US_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4057 | 1.3883 | 1.369 | 1.3518 | 1.2561 | 1.2344 | 1.3253 | 1.3077 | 1.1776 | 1.1596
US_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4829 | 1.4648 | 1.4176 | 1.4006 | 1.2684 | 1.2477 | 1.4003 | 1.3806 | 1.2774 | 1.2578
US_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4788 | 1.4608 | 1.4141 | 1.3971 | 1.2641 | 1.2439 | 1.395 | 1.3755 | 1.2719 | 1.2524
US_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.23 | 1.2184 | 1.1977 | 1.1872 | 1.2097 | 1.1951 | 1.2457 | 1.2288 | 1.1693 | 1.1503
US_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1912 | 1.1797 | 1.1706 | 1.1603 | 1.1877 | 1.1733 | 1.195 | 1.1788 | 1.119 | 1.1026
US_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1276 | 1.116 | 1.0953 | 1.0852 | 1.0764 | 1.0641 | 1.1238 | 1.1094 | 1.0384 | 1.0241
US_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0592 | 1.0483 | 1.0473 | 1.0372 | 1.0393 | 1.0271 | 1.0417 | 1.03 | 0.94186 | 0.92925
US_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.86648 | 0.85784 | 0.86073 | 0.85225 | 0.8259 | 0.81499 | 0.82875 | 0.81934 | 0.75307 | 0.74377
US_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.86163 | 0.85301 | 0.85645 | 0.84799 | 0.84338 | 0.80979 | 0.84963 | 0.83979 | 0.74635 | 0.73722
US_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.94614 | 0.93602 | 0.90692 | 0.89812 | 0.88 | 0.86952 | 0.92679 | 0.91561 | 0.85356 | 0.84165
US_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.94818 | 0.93801 | 0.90913 | 0.90029 | 0.88505 | 0.87455 | 0.9289 | 0.91764 | 0.85674 | 0.84455
US_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945
US_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824
US_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824
US_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824
US_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824
US_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824
US_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824
US_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824
US_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824
US_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372
US_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913
US_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 3.9282 | 3.9282 | 7.6025 | 7.5146 | 5.5249 | 5.4495 | 9.6714 | 9.7302 | 10.6831 | 10.7411
US_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 7.5582 | 7.4656 | 5.4771 | 5.3987 | 9.6128 | 9.6717 | 10.5764 | 10.6346
US_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 10.5443 | 10.4536 | 19.1112 | 18.9641 | 15.2889 | 15.1754 | 22.1893 | 22.2704 | 23.6446 | 23.7241
US_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 7.5341 | 7.4448 | 5.4927 | 5.4121 | 9.5913 | 9.6503 | 10.5506 | 10.6088
US_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 5.3368 | 5.2949 | 4.2004 | 4.2004 | 6.8827 | 6.9417 | 7.7778 | 7.836
US_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 5.336 | 5.2943 | 4.2004 | 4.2004 | 6.8821 | 6.941 | 7.7771 | 7.8352
US_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 5.2916 | 5.2543 | 4.2004 | 4.2004 | 6.8332 | 6.892 | 7.759 | 7.817
US_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 5.7937 | 5.7529 | 4.2547 | 4.2192 | 7.3338 | 7.3935 | 8.2708 | 8.3295
US_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 14.3321 | 14.1604 | 10.4907 | 10.3507 | 18.7007 | 18.8322 | 19.3171 | 19.4489
US_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 14.4277 | 14.2442 | 10.5561 | 10.408 | 18.7873 | 18.9187 | 19.3284 | 19.4602
US_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 14.2746 | 14.1108 | 10.5284 | 10.3832 | 18.6504 | 18.7819 | 19.2566 | 19.3885
US_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 14.3703 | 14.1947 | 10.5938 | 10.4404 | 18.737 | 18.8685 | 19.2679 | 19.3997
US_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 9.5665 | 9.5665 | 8.4009 | 8.4009 | 12.6509 | 12.7784 | 13.3899 | 13.5184
US_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 9.5665 | 9.5665 | 8.4009 | 8.4009 | 12.6495 | 12.7771 | 13.3883 | 13.5168
US_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 9.5665 | 9.5665 | 8.4009 | 8.4009 | 12.5718 | 12.6993 | 13.3871 | 13.5156
US_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 9.5665 | 9.5665 | 8.4009 | 8.4009 | 12.5705 | 12.698 | 13.3855 | 13.514
US_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 5.1234 | 5.072 | 10.5662 | 10.4816 | 8.2164 | 8.1478 | 13.0266 | 13.0892 | 13.5269 | 13.5898
US_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 5.1459 | 5.0912 | 10.6214 | 10.5309 | 8.2561 | 8.1837 | 13.0772 | 13.1398 | 13.5389 | 13.6019
US_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 5.1234 | 5.072 | 10.5363 | 10.4559 | 8.2363 | 8.1648 | 13.0006 | 13.0631 | 13.4951 | 13.558
US_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 5.1459 | 5.0912 | 10.5914 | 10.5051 | 8.276 | 8.2007 | 13.0511 | 13.1137 | 13.5071 | 13.5701
US_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 3.8207 | 3.8063 | 7.9721 | 7.9355 | 6.377 | 6.35 | 9.6197 | 9.6821 | 10.2709 | 10.3338
US_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 3.8207 | 3.8063 | 7.9712 | 7.9347 | 6.3776 | 6.3505 | 9.6189 | 9.6814 | 10.27 | 10.3329
US_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 3.7907 | 3.7901 | 7.9099 | 7.8789 | 6.3302 | 6.3069 | 9.5618 | 9.6242 | 10.2526 | 10.3154
US_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 3.7907 | 3.7901 | 7.909 | 7.8782 | 6.3308 | 6.3074 | 9.5611 | 9.6234 | 10.2517 | 10.3145
US_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes
US National | US | [10 empty] | 2020-03-25
US | 2020-03-25 | [10 empty] | 2020-03-25
| OfficeSmall | [10 empty] | 2020-03-25
|  | Zone2A(Tampa) ASHRAE901_2016 | Zone2A(Tampa) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2016 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2016 | Zone3B(ElPaso) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2016 | Zone4A(NewYork) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2016 | Zone5A(Buffalo) ASHRAE901_2019 | 2020-03-25
US_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 2.0555 | 1.9588 | 1.9522 | 1.8608 | 1.8175 | 1.7154 | 1.8066 | 1.715 | 1.6903 | 1.5992 | 2020-03-25
US_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9302 | 1.8385 | 1.7058 | 1.6451 | 1.7105 | 1.6322 | 1.5726 | 1.5114 | 1.4189 | 1.3589 | 2020-03-25
US_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3124 | 1.2654 | 1.1625 | 1.1214 | 1.1607 | 1.1104 | 1.094 | 1.0559 | 1.0291 | 0.99128 | 2020-03-25
US_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8943 | 1.8025 | 1.7056 | 1.63 | 1.7121 | 1.617 | 1.5 | 1.432 | 1.3448 | 1.2655 | 2020-03-25
US_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4849 | 1.4346 | 1.3222 | 1.28 | 1.4014 | 1.348 | 1.2698 | 1.2309 | 1.2064 | 1.1677 | 2020-03-25
US_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 699.2304 | 656.8528 | 783.9856 | 741.608 | 635.664 | 593.2864 | 635.664 | 593.2864 | 2020-03-25
US_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 635.664 | 593.2864 | 762.7968 | 720.4192 | 572.0976 | 550.9088 | 550.9088 | 508.5312 | 2020-03-25
US_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 466.1536 | 444.9648 | 529.72 | 508.5312 | 444.9648 | 423.776 | 444.9648 | 423.776 | 2020-03-25
US_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 593.2864 | 762.7968 | 720.4192 | 529.72 | 508.5312 | 508.5312 | 466.1536 | 2020-03-25
US_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 529.72 | 508.5312 | 635.664 | 614.4752 | 508.5312 | 487.3424 | 529.72 | 508.5312 | 2020-03-25
US_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 2020-03-25
US_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2020-03-25
US_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2020-03-25
US_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2020-03-25
US_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2020-03-25
US_SO_PSZ-AC:1 heating Capacity [kBtu/hr] | PSZ-AC:1 heating Capacity [kBtu/hr] | 9.4366 | 9.4366 | 11.9094 | 11.9094 | 10.4584 | 10.4584 | 13.5199 | 13.5199 | 14.6431 | 14.6431 | 2020-03-25
US_SO_PSZ-AC:2 heating Capacity [kBtu/hr] | PSZ-AC:2 heating Capacity [kBtu/hr] | 9.9139 | 9.5655 | 17.473 | 17.2425 | 14.1799 | 13.9661 | 19.4077 | 19.2146 | 21.004 | 20.7691 | 2020-03-25
US_SO_PSZ-AC:3 heating Capacity [kBtu/hr] | PSZ-AC:3 heating Capacity [kBtu/hr] | 6.0234 | 5.8221 | 10.7537 | 10.6262 | 8.6701 | 8.5472 | 11.9549 | 11.848 | 12.769 | 12.6451 | 2020-03-25
US_SO_PSZ-AC:4 heating Capacity [kBtu/hr] | PSZ-AC:4 heating Capacity [kBtu/hr] | 9.7186 | 9.4206 | 17.3127 | 17.1137 | 14.0032 | 13.8214 | 19.3277 | 19.1609 | 20.8017 | 20.6095 | 2020-03-25
US_SO_PSZ-AC:5 heating Capacity [kBtu/hr] | PSZ-AC:5 heating Capacity [kBtu/hr] | 6.0234 | 5.8221 | 10.8068 | 10.6723 | 8.6358 | 8.5175 | 12.0086 | 11.8958 | 12.8307 | 12.7006 | 2020-03-25
US_LO_OfficeLarge | OfficeLarge | [10 empty] | 2020-03-25
|  | Zone2A(Tampa) ASHRAE901_2016 | Zone2A(Tampa) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2016 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2016 | Zone3B(ElPaso) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2016 | Zone4A(NewYork) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2016 | Zone5A(Buffalo) ASHRAE901_2019 | 2020-03-25
US_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12014.0496 | 11166.4976 | 11886.9168 | 10996.9872 | 13391.3216 | 12395.448 | 11611.4624 | 10742.7216 | 11780.9728 | 10891.0432 | 2020-03-25
US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18963.976 | 18010.48 | 19387.752 | 18413.0672 | 22036.352 | 20955.7232 | 19620.8288 | 18688.5216 | 19790.3392 | 18858.032 | 2020-03-25
US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 174849.9779 | 165738.7939 | 179638.6467 | 170273.1971 | 204683.8083 | 194364.8627 | 182986.4771 | 174129.5587 | 183600.9523 | 174595.7123 | 2020-03-25
US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18497.8224 | 17650.2704 | 18963.976 | 18137.6128 | 22142.296 | 21209.9888 | 18985.1648 | 18201.1792 | 19133.4864 | 18349.5008 | 2020-03-25
US_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2020-03-25
US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 2020-03-25
US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 53777.9373 | 43021.7396 | 2020-03-25
US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 5377.8022 | 4302.174 | 2020-03-25
US_LO_AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | AIRLOOP DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 2020-03-25
US_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 438.8299 | 391.2284 | 406.1299 | 365.9173 | 337.4605 | 311.9875 | 402.5817 | 336.3811 | 371.5931 | 339.1105 | 2020-03-25
US_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 438.8299 | 391.2284 | 406.1299 | 365.9173 | 337.4605 | 311.9875 | 402.5817 | 336.3811 | 371.5931 | 339.1105 | 2020-03-25
US_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 416.5333 | 371.3501 | 385.4879 | 347.3277 | 320.5792 | 296.3791 | 382.1274 | 319.2884 | 352.7198 | 321.8836 | 2020-03-25
US_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 416.5333 | 371.3501 | 385.4879 | 347.3277 | 320.5792 | 296.3791 | 382.1274 | 319.2884 | 352.7198 | 321.8836 | 2020-03-25
US_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.338 | 4.0326 | 5.5056 | 5.0972 | 5.0875 | 4.7251 | 5.9876 | 5.5199 | 6.4105 | 5.8555 | 2020-03-25
US_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2020-03-25
US_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 688.9739 | 613.9337 | 639.96 | 573.7627 | 527.5495 | 487.632 | 634.3299 | 526.9345 | 585.2605 | 534.0085 | 2020-03-25
US_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 688.9739 | 613.9337 | 639.96 | 573.7627 | 527.5495 | 487.632 | 634.3299 | 526.9345 | 585.2605 | 534.0085 | 2020-03-25
US_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1377.9463 | 1227.8691 | 1279.9215 | 1147.5238 | 1055.1005 | 975.2656 | 1268.6614 | 1053.869 | 1170.5194 | 1068.017 | 2020-03-25
US_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 890.4236 | 827.7387 | 1130.0948 | 1046.2719 | 1044.2843 | 969.886 | 1229.0404 | 1133.0413 | 1315.8368 | 1201.9189 | 2020-03-25
US_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2420.9784 | 2158.497 | 2240.6017 | 2018.8557 | 1861.779 | 1721.1866 | 2221.1058 | 1855.7558 | 2050.0808 | 1870.8136 | 2020-03-25
US_LO_PLANT CIRC PUMP Flow Rate [gal/min] | PLANT CIRC PUMP Flow Rate [gal/min] | 208.6949 | 207.8072 | 209.3162 | 208.4508 | 223.442 | 222.4688 | 207.4443 | 206.6169 | 208.9992 | 208.1591 | 2020-03-25
US_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | pump_ride_on_curve | 2020-03-25
US_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 3.7168 | 3.2792 | 3.4524 | 3.0646 | 2.8459 | 2.6046 | 3.422 | 2.8145 | 3.1573 | 2.8523 | 2020-03-25
US_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 3.7168 | 3.2792 | 3.4524 | 3.0646 | 2.8459 | 2.6046 | 3.422 | 2.8145 | 3.1573 | 2.8523 | 2020-03-25
US_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.3006 | 19.675 | 20.7142 | 18.3876 | 17.0757 | 15.6274 | 20.5319 | 16.8869 | 18.9436 | 17.1136 | 2020-03-25
US_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.247 | 17.7149 | 24.4277 | 22.3919 | 22.5728 | 20.7571 | 26.5664 | 24.2489 | 28.4426 | 25.7229 | 2020-03-25
US_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.3467 | 38.2621 | 40.1167 | 35.7867 | 33.3337 | 30.5124 | 39.7662 | 32.898 | 36.7052 | 33.165 | 2020-03-25
US_LO_PLANT CIRC PUMP Pump Power [hp] | PLANT CIRC PUMP Pump Power [hp] | 4.5033 | 4.4398 | 4.5168 | 4.4535 | 4.8216 | 4.753 | 4.4764 | 4.4144 | 4.5099 | 4.4473 | 2020-03-25
US_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.5033 | 4.4398 | 4.5168 | 4.4535 | 4.8216 | 4.753 | 4.4764 | 4.4144 | 4.5099 | 4.4473 | 2020-03-25
US_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 333.7229 | 308.8504 | 438.5215 | 420.6112 | 398.3272 | 378.7423 | 468.5349 | 451.3102 | 490.0421 | 470.7384 | 2020-03-25
US_LO_COOLSYS1 PUMP SECONDARY VSD | COOLSYS1 PUMP SECONDARY VSD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | 2020-03-25
US_LO_HEATSYS1 PUMP VSD | HEATSYS1 PUMP VSD | No | No | No | No | No | No | No | VFD | No | VFD | 2020-03-25
US_LO_DATACENTER BASEMENT Cooling Capacity [ton] | DATACENTER BASEMENT Cooling Capacity [ton] | 122.4648 | 122.1084 | 123.007 | 122.6466 | 131.6564 | 131.2668 | 121.5049 | 121.1445 | 122.0827 | 121.7198 | 2020-03-25
US_LO_DATACENTER BOT Cooling Capacity [ton] | DATACENTER BOT Cooling Capacity [ton] | 2.6497 | 2.623 | 2.6194 | 2.6185 | 2.7947 | 2.7651 | 2.6393 | 2.616 | 2.6839 | 2.6602 | 2020-03-25
US_LO_DATACENTER MID Cooling Capacity [ton] | DATACENTER MID Cooling Capacity [ton] | 25.1989 | 24.9535 | 25.17 | 24.9168 | 26.5498 | 26.2782 | 25.2438 | 25.0406 | 25.7149 | 25.5063 | 2020-03-25
US_LO_DATACENTER TOP Cooling Capacity [ton] | DATACENTER TOP Cooling Capacity [ton] | 2.5595 | 2.5385 | 2.5325 | 2.5129 | 2.6748 | 2.6533 | 2.5698 | 2.5501 | 2.6144 | 2.5943 | 2020-03-25
US_RS_RetailStandalone | RetailStandalone | [10 empty] | 2020-03-25
|  | Zone2A(Tampa) ASHRAE901_2016 | Zone2A(Tampa) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2016 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2016 | Zone3B(ElPaso) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2016 | Zone4A(NewYork) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2016 | Zone5A(Buffalo) ASHRAE901_2019 | 2020-03-25
US_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 11.3139 | 10.9459 | 10.5812 | 10.2412 | 10.5384 | 9.9057 | 10.4557 | 10.0917 | 9.5963 | 9.1249 | 2020-03-25
US_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 51.2004 | 48.07 | 49.7758 | 47.6959 | 47.4616 | 45.3882 | 48.0092 | 46.2465 | 44.3772 | 42.4882 | 2020-03-25
US_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8904 | 6.7656 | 6.4722 | 6.314 | 6.6327 | 6.4618 | 6.3493 | 6.1924 | 5.7425 | 5.5854 | 2020-03-25
US_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.674 | 5.5415 | 5.2462 | 5.0929 | 5.2991 | 5.1178 | 5.1749 | 5.0213 | 4.5449 | 4.3672 | 2020-03-25
US_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4174.1936 | 3941.1168 | 4110.6272 | 3856.3616 | 4746.2912 | 4449.648 | 3983.4944 | 3729.2288 | 3771.6064 | 3474.9632 | 2020-03-25
US_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15361.88 | 14429.5728 | 15446.6352 | 14514.328 | 17311.2496 | 16357.7536 | 15277.1248 | 14471.9504 | 15192.3696 | 14281.2512 | 2020-03-25
US_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2267.2016 | 2309.5792 | 2224.824 | 2648.6 | 2563.8448 | 2288.3904 | 2224.824 | 2203.6352 | 2118.88 | 2020-03-25
US_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1801.048 | 1737.4816 | 1758.6704 | 1673.9152 | 2055.3136 | 1970.5584 | 1758.6704 | 1695.104 | 1631.5376 | 1546.7824 | 2020-03-25
US_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 2020-03-25
US_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 2020-03-25
US_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2020-03-25
US_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2020-03-25
US_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_RS_PSZ-AC:1 Heating Capacity [kBtu/hr] | PSZ-AC:1 Heating Capacity [kBtu/hr] | 170.1583 | 160.4069 | 171.6609 | 161.6468 | 174.7009 | 164.8895 | 177.1344 | 166.5616 | 169.417 | 156.6046 | 2020-03-25
US_RS_PSZ-AC:2 Heating Capacity [kBtu/hr] | PSZ-AC:2 Heating Capacity [kBtu/hr] | 685.7061 | 648.3055 | 744.9252 | 707.8342 | 724.548 | 690.5645 | 798.8945 | 765.4864 | 818.6913 | 780.8617 | 2020-03-25
US_RS_PSZ-AC:3 Heating Capacity [kBtu/hr] | PSZ-AC:3 Heating Capacity [kBtu/hr] | 98.7919 | 96.6704 | 101.9548 | 99.3168 | 102.0587 | 99.4843 | 108.5531 | 105.8788 | 106.1941 | 103.5014 | 2020-03-25
US_RS_PSZ-AC:4 Heating Capacity [kBtu/hr] | PSZ-AC:4 Heating Capacity [kBtu/hr] | 79.1941 | 76.8838 | 82.1152 | 79.3613 | 82.4712 | 79.7979 | 88.5194 | 85.6493 | 85.2348 | 81.962 | 2020-03-25
US_PS_SchoolPrimary | SchoolPrimary | [10 empty] | 2020-03-25
US_PS_ |  | Zone2A(Tampa) ASHRAE901_2016 | Zone2A(Tampa) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2016 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2016 | Zone3B(ElPaso) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2016 | Zone4A(NewYork) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2016 | Zone5A(Buffalo) ASHRAE901_2019 | 2020-03-25
US_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 19.3372 | 18.3769 | 18.6648 | 18.1241 | 22.3173 | 21.0521 | 18.6852 | 18.1708 | 18.6048 | 18.1705 | 2020-03-25
US_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 19.3534 | 18.3244 | 18.6162 | 18.0887 | 22.2412 | 20.7718 | 18.4688 | 18.1181 | 18.4894 | 18.1201 | 2020-03-25
US_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 17.6857 | 16.5968 | 17.0455 | 16.154 | 20.3933 | 19.1327 | 16.9244 | 16.1545 | 16.8958 | 16.0741 | 2020-03-25
US_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.3715 | 24.6347 | 25.9969 | 24.3878 | 25.9879 | 23.5162 | 25.4842 | 23.9792 | 25.5787 | 23.2415 | 2020-03-25
US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.3841 | 8.007 | 8.4249 | 8.1504 | 8.4035 | 8.104 | 8.1363 | 7.8751 | 7.7875 | 7.5294 | 2020-03-25
US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.284 | 5.1223 | 5.2586 | 5.0915 | 5.8861 | 5.8324 | 5.2082 | 5.292 | 5.3411 | 5.318 | 2020-03-25
US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 2020-03-25
US_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | 5593.8432 | 5445.5216 | 6695.6608 | 6314.2624 | 5615.032 | 5445.5216 | 5572.6544 | 5445.5216 | 2020-03-25
US_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | 5593.8432 | 5424.3328 | 6674.472 | 6229.5072 | 5551.4656 | 5445.5216 | 5551.4656 | 5445.5216 | 2020-03-25
US_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 5297.2 | 4979.368 | 5106.5008 | 4852.2352 | 6123.5632 | 5742.1648 | 5085.312 | 4852.2352 | 5064.1232 | 4831.0464 | 2020-03-25
US_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 7903.4224 | 7394.8912 | 7797.4784 | 7310.136 | 9174.7504 | 8623.8416 | 7649.1568 | 7204.192 | 7670.3456 | 7183.0032 | 2020-03-25
US_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1546.7824 | 1567.9712 | 1525.5936 | 1801.048 | 1779.8592 | 1567.9712 | 1589.16 | 1610.3488 | 1589.16 | 2020-03-25
US_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2585.0336 | 2457.9008 | 2881.6768 | 2754.544 | 2521.4672 | 2415.5232 | 2563.8448 | 2457.9008 | 2020-03-25
US_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 2020-03-25
US_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | Yes | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 5802.786 | 5514.5971 | 5598.6531 | 5438.7412 | 6697.0593 | 6282.2673 | 5607.1074 | 5452.747 | 5581.9563 | 5452.6622 | 2020-03-25
US_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 5807.5958 | 5498.8538 | 5584.5413 | 5428.1256 | 6671.103 | 6233.2788 | 5542.1849 | 5436.919 | 5548.3509 | 5437.5546 | 2020-03-25
US_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 5304.6161 | 4980.4486 | 5112.476 | 4847.5313 | 6119.7068 | 5422.002 | 5078.7435 | 4847.7008 | 5070.1408 | 4823.5668 | 2020-03-25
US_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 3736.1787 | 2988.8921 | 2020-03-25
US_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 2020-03-25
US_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 540.0601 | 2020-03-25
US_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 2020-03-25
US_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2020-03-25
US_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 0.64826 | 0.6009 | 0.90587 | 0.86434 | 0.86403 | 0.80043 | 1.015 | 0.97432 | 1.1154 | 1.0753 | 2020-03-25
US_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 66.5317 | 61.6715 | 92.9713 | 88.7089 | 88.677 | 82.1491 | 104.1747 | 99.9964 | 114.4758 | 110.3566 | 2020-03-25
US_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 8.5609 | 8.1357 | 8.2632 | 8.0238 | 9.8802 | 9.32 | 8.2722 | 8.0444 | 8.2366 | 8.0443 | 2020-03-25
US_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 8.568 | 8.1125 | 8.2417 | 8.0081 | 9.8465 | 9.1959 | 8.1764 | 8.0211 | 8.1855 | 8.022 | 2020-03-25
US_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 7.8297 | 7.3476 | 7.5463 | 7.1516 | 9.0284 | 8.4703 | 7.4927 | 7.1518 | 7.48 | 7.1162 | 2020-03-25
US_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.5866 | 10.8235 | 11.422 | 10.715 | 13.4264 | 12.6363 | 11.1967 | 10.5355 | 11.2382 | 10.51 | 2020-03-25
US_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 1.4381 | 1.3199 | 2.0096 | 1.8985 | 1.9168 | 1.7581 | 2.2518 | 2.1401 | 2.4745 | 2.3618 | 2020-03-25
US_PS_PSZ-AC_1:6 Heating Capacity [kBtu/hr] | PSZ-AC_1:6 Heating Capacity [kBtu/hr] | 191.0964 | 182.2854 | 200.3862 | 191.6855 | 199.9799 | 191.3774 | 207.8681 | 199.3018 | 212.0964 | 203.5478 | 2020-03-25
US_PS_PSZ-AC_2:5 Heating Capacity [kBtu/hr] | PSZ-AC_2:5 Heating Capacity [kBtu/hr] | 95.463 | 93.6677 | 115.4488 | 113.6581 | 108.6449 | 107.927 | 129.005 | 129.936 | 139.527 | 139.2767 | 2020-03-25
US_PS_PSZ-AC_2:7 Heating Capacity [kBtu/hr] | PSZ-AC_2:7 Heating Capacity [kBtu/hr] | 217.3157 | 217.3157 | 274.2625 | 274.2625 | 240.8457 | 240.8457 | 311.351 | 311.351 | 337.2181 | 337.2181 | 2020-03-25
US_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 94.3097 | 93.4261 | 93.0721 | 92.1725 | 85.0563 | 84.1331 | 95.9294 | 95.578 | 94.7918 | 93.9035 | 2020-03-25
US_SH_HotelSmall | HotelSmall | [10 empty] | 2020-03-25
US_SH_ |  | Zone2A(Tampa) ASHRAE901_2016 | Zone2A(Tampa) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2016 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2016 | Zone3B(ElPaso) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2016 | Zone4A(NewYork) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2016 | Zone5A(Buffalo) ASHRAE901_2019 | 2020-03-25
US_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5999 | 2.4575 | 2.4415 | 2.3156 | 2.3849 | 2.2422 | 2.2772 | 2.1613 | 2.1107 | 1.9954 | 2020-03-25
US_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2508 | 5.928 | 6.3213 | 5.9999 | 6.1359 | 5.8857 | 6.027 | 5.7233 | 5.7399 | 5.5082 | 2020-03-25
US_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9807 | 2.8761 | 2.9994 | 2.9144 | 3.1725 | 3.0992 | 2.8701 | 2.7771 | 2.8701 | 2.7798 | 2020-03-25
US_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.1652 | 6.1259 | 6.0419 | 6.0006 | 6.1247 | 6.0801 | 5.7874 | 5.7466 | 5.5467 | 5.5007 | 2020-03-25
US_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 783.9856 | 826.3632 | 762.7968 | 953.496 | 889.9296 | 762.7968 | 720.4192 | 762.7968 | 699.2304 | 2020-03-25
US_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1779.8592 | 1906.992 | 1801.048 | 2161.2576 | 2055.3136 | 1801.048 | 1716.2928 | 1801.048 | 1695.104 | 2020-03-25
US_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 889.9296 | 868.7408 | 1017.0624 | 995.8736 | 868.7408 | 826.3632 | 868.7408 | 826.3632 | 2020-03-25
US_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 2224.824 | 2203.6352 | 2500.2784 | 2479.0896 | 2140.0688 | 2140.0688 | 2182.4464 | 2161.2576 | 2020-03-25
US_SH_SAC_Exc_EmpLge_RestRm OA Rate [cfm] | SAC_Exc_EmpLge_RestRm OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 2020-03-25
US_SH_SAC_FrontLounge OA Rate [cfm] | SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 2020-03-25
US_SH_SAC_FrontOffice OA Rate [cfm] | SAC_FrontOffice OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 2020-03-25
US_SH_SAC_MeetingRoom OA Rate [cfm] | SAC_MeetingRoom OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 2020-03-25
US_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2020-03-25
US_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No | No | No | 2020-03-25
US_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No | No | No | 2020-03-25
US_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | 2020-03-25
US_SH_SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | SAC_FRONTOFFICE Heating Capacity [kBtu/hr] | 34.8782 | 32.6536 | 35.3284 | 33.3906 | 35.4535 | 33.3905 | 35.7485 | 33.9662 | 35.6034 | 33.7618 | 2020-03-25
US_SH_SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | SAC_FRONTLOUNGE Heating Capacity [kBtu/hr] | 85.0562 | 81.4933 | 93.0626 | 89.6407 | 91.5317 | 88.0944 | 97.5155 | 94.1622 | 100.0461 | 96.7146 | 2020-03-25
| SAC_MEETINGROOM Heating Capacity [kBtu/hr] | 41.5018 | 40.3471 | 45.7285 | 44.8233 | 44.6241 | 43.6721 | 48.274 | 47.2471 | 49.9326 | 48.9605
| SAC_EXC_EMPLGE_RESTRM Heating Capacity [kBtu/hr] | 86.3908 | 85.8665 | 89.217 | 88.5796 | 88.747 | 88.0979 | 91.4074 | 90.749 | 92.4616 | 91.8054
US_MA_ApartmentMidRise | ApartmentMidRise | [10 empty] | 2020-03-25
US_MA_ |  | Zone2A(Tampa) ASHRAE901_2016 | Zone2A(Tampa) ASHRAE901_2019 | Zone3A(Atlanta) ASHRAE901_2016 | Zone3A(Atlanta) ASHRAE901_2019 | Zone3B(ElPaso) ASHRAE901_2016 | Zone3B(ElPaso) ASHRAE901_2019 | Zone4A(NewYork) ASHRAE901_2016 | Zone4A(NewYork) ASHRAE901_2019 | Zone5A(Buffalo) ASHRAE901_2016 | Zone5A(Buffalo) ASHRAE901_2019 | 2020-03-25
US_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.98423 | 0.97375 | 0.86899 | 0.85871 | 0.83268 | 0.81943 | 0.83162 | 0.81763 | 0.74751 | 0.73308 | 2020-03-25
US_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.94819 | 0.93774 | 0.84441 | 0.83404 | 0.82609 | 0.81272 | 0.79432 | 0.78088 | 0.70314 | 0.68933 | 2020-03-25
US_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.832 | 1.7461 | 1.694 | 1.5722 | 1.8067 | 1.7039 | 1.6468 | 1.5121 | 1.5311 | 1.445 | 2020-03-25
US_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84983 | 0.84053 | 0.75301 | 0.74161 | 0.73287 | 0.72042 | 0.69822 | 0.68633 | 0.59725 | 0.58515 | 2020-03-25
US_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72462 | 0.71657 | 0.65014 | 0.64124 | 0.60991 | 0.59896 | 0.59683 | 0.58765 | 0.50669 | 0.49714 | 2020-03-25
US_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.72294 | 0.71491 | 0.64857 | 0.63967 | 0.60819 | 0.59725 | 0.59496 | 0.58583 | 0.50447 | 0.49498 | 2020-03-25
US_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.76065 | 0.75025 | 0.67117 | 0.66065 | 0.61633 | 0.604 | 0.63623 | 0.62578 | 0.55883 | 0.54822 | 2020-03-25
US_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.79438 | 0.78111 | 0.70484 | 0.69203 | 0.66283 | 0.64704 | 0.67013 | 0.6531 | 0.59321 | 0.5778 | 2020-03-25
US_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.022 | 1.9987 | 1.947 | 1.9263 | 1.8642 | 1.8361 | 1.9991 | 1.9677 | 1.8865 | 1.8546 | 2020-03-25
US_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.9548 | 1.9322 | 1.9117 | 1.8909 | 1.8413 | 1.8137 | 1.9266 | 1.8968 | 1.8064 | 1.7758 | 2020-03-25
US_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.8002 | 1.7769 | 1.69 | 1.671 | 1.6503 | 1.5596 | 1.7551 | 1.7277 | 1.6191 | 1.5901 | 2020-03-25
US_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7014 | 1.68 | 1.6547 | 1.6357 | 1.5753 | 1.5503 | 1.6125 | 1.5831 | 1.4626 | 1.4334 | 2020-03-25
US_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.41 | 1.3926 | 1.373 | 1.3558 | 1.2605 | 1.2388 | 1.3305 | 1.3128 | 1.1839 | 1.1656 | 2020-03-25
US_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4057 | 1.3883 | 1.369 | 1.3518 | 1.2561 | 1.2344 | 1.3253 | 1.3077 | 1.1776 | 1.1596 | 2020-03-25
US_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4829 | 1.4648 | 1.4176 | 1.4006 | 1.2684 | 1.2477 | 1.4003 | 1.3806 | 1.2774 | 1.2578 | 2020-03-25
US_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4788 | 1.4608 | 1.4141 | 1.3971 | 1.2641 | 1.2439 | 1.395 | 1.3755 | 1.2719 | 1.2524 | 2020-03-25
US_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.23 | 1.2184 | 1.1977 | 1.1872 | 1.2097 | 1.1951 | 1.2457 | 1.2288 | 1.1693 | 1.1503 | 2020-03-25
US_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1912 | 1.1797 | 1.1706 | 1.1603 | 1.1877 | 1.1733 | 1.195 | 1.1788 | 1.119 | 1.1026 | 2020-03-25
US_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1276 | 1.116 | 1.0953 | 1.0852 | 1.0764 | 1.0641 | 1.1238 | 1.1094 | 1.0384 | 1.0241 | 2020-03-25
US_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0592 | 1.0483 | 1.0473 | 1.0372 | 1.0393 | 1.0271 | 1.0417 | 1.03 | 0.94186 | 0.92925 | 2020-03-25
US_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.86648 | 0.85784 | 0.86073 | 0.85225 | 0.8259 | 0.81499 | 0.82875 | 0.81934 | 0.75307 | 0.74377 | 2020-03-25
US_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.86163 | 0.85301 | 0.85645 | 0.84799 | 0.84338 | 0.80979 | 0.84963 | 0.83979 | 0.74635 | 0.73722 | 2020-03-25
US_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.94614 | 0.93602 | 0.90692 | 0.89812 | 0.88 | 0.86952 | 0.92679 | 0.91561 | 0.85356 | 0.84165 | 2020-03-25
US_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.94818 | 0.93801 | 0.90913 | 0.90029 | 0.88505 | 0.87455 | 0.9289 | 0.91764 | 0.85674 | 0.84455 | 2020-03-25
US_MA_Split GN1 Furnace with DX Cooling OA Rate [cfm] | Split GN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split GN2 Furnace with DX Cooling OA Rate [cfm] | Split GN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split GNE Furnace with DX Cooling OA Rate [cfm] | Split GNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split GNW Furnace with DX Cooling OA Rate [cfm] | Split GNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split GS1 Furnace with DX Cooling OA Rate [cfm] | Split GS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split GS2 Furnace with DX Cooling OA Rate [cfm] | Split GS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split GSW Furnace with DX Cooling OA Rate [cfm] | Split GSW Furnace with DX Cooling OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 2020-03-25
US_MA_Split MN1 Furnace with DX Cooling OA Rate [cfm] | Split MN1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2020-03-25
US_MA_Split MN2 Furnace with DX Cooling OA Rate [cfm] | Split MN2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2020-03-25
US_MA_Split MNE Furnace with DX Cooling OA Rate [cfm] | Split MNE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2020-03-25
US_MA_Split MNW Furnace with DX Cooling OA Rate [cfm] | Split MNW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2020-03-25
US_MA_Split MS1 Furnace with DX Cooling OA Rate [cfm] | Split MS1 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2020-03-25
US_MA_Split MS2 Furnace with DX Cooling OA Rate [cfm] | Split MS2 Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2020-03-25
US_MA_Split MSE Furnace with DX Cooling OA Rate [cfm] | Split MSE Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2020-03-25
US_MA_Split MSW Furnace with DX Cooling OA Rate [cfm] | Split MSW Furnace with DX Cooling OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2020-03-25
US_MA_Split Office Furnace with DX Cooling OA Rate [cfm] | Split Office Furnace with DX Cooling OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 2020-03-25
US_MA_Split TN1 Furnace with DX Cooling OA Rate [cfm] | Split TN1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split TN2 Furnace with DX Cooling OA Rate [cfm] | Split TN2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split TNE Furnace with DX Cooling OA Rate [cfm] | Split TNE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split TNW Furnace with DX Cooling OA Rate [cfm] | Split TNW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split TS1 Furnace with DX Cooling OA Rate [cfm] | Split TS1 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split TS2 Furnace with DX Cooling OA Rate [cfm] | Split TS2 Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split TSE Furnace with DX Cooling OA Rate [cfm] | Split TSE Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_Split TSW Furnace with DX Cooling OA Rate [cfm] | Split TSW Furnace with DX Cooling OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2020-03-25
US_MA_SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GSW HEATING COIL Heating Capacity [kBtu/hr] | 3.9282 | 3.9282 | 7.6025 | 7.5146 | 5.5249 | 5.4495 | 9.6714 | 9.7302 | 10.6831 | 10.7411 | 2020-03-25
US_MA_SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNW HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 7.5582 | 7.4656 | 5.4771 | 5.3987 | 9.6128 | 9.6717 | 10.5764 | 10.6346 | 2020-03-25
US_MA_SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT OFFICE HEATING COIL Heating Capacity [kBtu/hr] | 10.5443 | 10.4536 | 19.1112 | 18.9641 | 15.2889 | 15.1754 | 22.1893 | 22.2704 | 23.6446 | 23.7241 | 2020-03-25
US_MA_SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GNE HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 7.5341 | 7.4448 | 5.4927 | 5.4121 | 9.5913 | 9.6503 | 10.5506 | 10.6088 | 2020-03-25
US_MA_SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN1 HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 5.3368 | 5.2949 | 4.2004 | 4.2004 | 6.8827 | 6.9417 | 7.7778 | 7.836 | 2020-03-25
US_MA_SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GN2 HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 5.336 | 5.2943 | 4.2004 | 4.2004 | 6.8821 | 6.941 | 7.7771 | 7.8352 | 2020-03-25
US_MA_SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS1 HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 5.2916 | 5.2543 | 4.2004 | 4.2004 | 6.8332 | 6.892 | 7.759 | 7.817 | 2020-03-25
US_MA_SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT GS2 HEATING COIL Heating Capacity [kBtu/hr] | 3.7901 | 3.7901 | 5.7937 | 5.7529 | 4.2547 | 4.2192 | 7.3338 | 7.3935 | 8.2708 | 8.3295 | 2020-03-25
US_MA_SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSW HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 14.3321 | 14.1604 | 10.4907 | 10.3507 | 18.7007 | 18.8322 | 19.3171 | 19.4489 | 2020-03-25
US_MA_SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNW HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 14.4277 | 14.2442 | 10.5561 | 10.408 | 18.7873 | 18.9187 | 19.3284 | 19.4602 | 2020-03-25
US_MA_SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MSE HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 14.2746 | 14.1108 | 10.5284 | 10.3832 | 18.6504 | 18.7819 | 19.2566 | 19.3885 | 2020-03-25
US_MA_SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MNE HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 14.3703 | 14.1947 | 10.5938 | 10.4404 | 18.737 | 18.8685 | 19.2679 | 19.3997 | 2020-03-25
US_MA_SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN1 HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 9.5665 | 9.5665 | 8.4009 | 8.4009 | 12.6509 | 12.7784 | 13.3899 | 13.5184 | 2020-03-25
US_MA_SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MN2 HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 9.5665 | 9.5665 | 8.4009 | 8.4009 | 12.6495 | 12.7771 | 13.3883 | 13.5168 | 2020-03-25
US_MA_SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS1 HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 9.5665 | 9.5665 | 8.4009 | 8.4009 | 12.5718 | 12.6993 | 13.3871 | 13.5156 | 2020-03-25
US_MA_SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT MS2 HEATING COIL Heating Capacity [kBtu/hr] | 7.5801 | 7.5801 | 9.5665 | 9.5665 | 8.4009 | 8.4009 | 12.5705 | 12.698 | 13.3855 | 13.514 | 2020-03-25
US_MA_SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSW HEATING COIL Heating Capacity [kBtu/hr] | 5.1234 | 5.072 | 10.5662 | 10.4816 | 8.2164 | 8.1478 | 13.0266 | 13.0892 | 13.5269 | 13.5898 | 2020-03-25
US_MA_SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNW HEATING COIL Heating Capacity [kBtu/hr] | 5.1459 | 5.0912 | 10.6214 | 10.5309 | 8.2561 | 8.1837 | 13.0772 | 13.1398 | 13.5389 | 13.6019 | 2020-03-25
US_MA_SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TSE HEATING COIL Heating Capacity [kBtu/hr] | 5.1234 | 5.072 | 10.5363 | 10.4559 | 8.2363 | 8.1648 | 13.0006 | 13.0631 | 13.4951 | 13.558 | 2020-03-25
US_MA_SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TNE HEATING COIL Heating Capacity [kBtu/hr] | 5.1459 | 5.0912 | 10.5914 | 10.5051 | 8.276 | 8.2007 | 13.0511 | 13.1137 | 13.5071 | 13.5701 | 2020-03-25
US_MA_SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN1 HEATING COIL Heating Capacity [kBtu/hr] | 3.8207 | 3.8063 | 7.9721 | 7.9355 | 6.377 | 6.35 | 9.6197 | 9.6821 | 10.2709 | 10.3338 | 2020-03-25
US_MA_SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TN2 HEATING COIL Heating Capacity [kBtu/hr] | 3.8207 | 3.8063 | 7.9712 | 7.9347 | 6.3776 | 6.3505 | 9.6189 | 9.6814 | 10.27 | 10.3329 | 2020-03-25
US_MA_SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS1 HEATING COIL Heating Capacity [kBtu/hr] | 3.7907 | 3.7901 | 7.9099 | 7.8789 | 6.3302 | 6.3069 | 9.5618 | 9.6242 | 10.2526 | 10.3154 | 2020-03-25
US_MA_SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | SPLIT TS2 HEATING COIL Heating Capacity [kBtu/hr] | 3.7907 | 3.7901 | 7.909 | 7.8782 | 6.3308 | 6.3074 | 9.5611 | 9.6234 | 10.2517 | 10.3145 | 2020-03-25
US_MA_Split_GSW ERV Flag | Split_GSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_GNW ERV Flag | Split_GNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_GNE ERV Flag | Split_GNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_GN1 ERV Flag | Split_GN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_GN2 ERV Flag | Split_GN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_GS1 ERV Flag | Split_GS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_GS2 ERV Flag | Split_GS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_MSW ERV Flag | Split_MSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_MNW ERV Flag | Split_MNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_MSE ERV Flag | Split_MSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_MNE ERV Flag | Split_MNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_MN1 ERV Flag | Split_MN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_MN2 ERV Flag | Split_MN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_MS1 ERV Flag | Split_MS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_MS2 ERV Flag | Split_MS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_TSW ERV Flag | Split_TSW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_TNW ERV Flag | Split_TNW ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_TSE ERV Flag | Split_TSE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_TNE ERV Flag | Split_TNE ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_TN1 ERV Flag | Split_TN1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_TN2 ERV Flag | Split_TN2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_TS1 ERV Flag | Split_TS1 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
US_MA_Split_TS2 ERV Flag | Split_TS2 ERV Flag | No | Yes | No | Yes | No | Yes | Yes | Yes | Yes | Yes | 2020-03-25
FL_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9546 | 1.8422 | 1.8743 | 1.8298 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9949 | 1.7961 | 1.9799 | 1.8292 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5271 | 1.297 | 1.5778 | 1.3354 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.9403 | 1.7739 | 1.865 | 1.7512 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7838 | 1.5092 | 1.7665 | 1.4978 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 656.8528 | 741.608 | 678.0416 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 656.8528 | 529.72 | 678.0416 | 550.9088 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 720.4192 | 635.664 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 762.7968 | 614.4752 | 762.7968 | 614.4752 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.47187 | 0.43306 | 0.44633 | 0.43064 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.53408 | 0.46221 | 0.52823 | 0.47476 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.46103 | 0.37451 | 0.48431 | 0.39013 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.5143 | 0.4549 | 0.48847 | 0.44837 | [6 empty] | 2015-03-31
FL_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.5444 | 0.4423 | 0.5396 | 0.44081 | [6 empty] | 2015-03-31
FL_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10848.6656 | 10488.456 | 10636.7776 | 10276.568 | [6 empty] | 2015-03-31
FL_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25299.4272 | 23922.1552 | 24706.1408 | 23032.2256 | [6 empty] | 2015-03-31
FL_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 205298.2835 | 191334.8643 | 196441.3651 | 181566.8275 | [6 empty] | 2015-03-31
FL_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23477.1904 | 20828.5904 | 22057.5408 | 19747.9616 | [6 empty] | 2015-03-31
FL_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2015-03-31
FL_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
FL_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
FL_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
FL_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
FL_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
FL_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
FL_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
FL_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
FL_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
FL_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
FL_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
FL_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_LO_CAV_bas (economizer) | CAV_bas (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | No | No | [6 empty] | 2015-03-31
FL_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
FL_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
FL_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
FL_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
FL_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
FL_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
FL_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
FL_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
FL_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
FL_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 434.484 | 421.2508 | 423.0847 | 408.585 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 434.484 | 421.2508 | 423.0847 | 408.585 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
FL_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 412.3878 | 399.831 | 401.5643 | 387.8035 | [6 empty] | 2015-03-31
FL_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 412.3878 | 399.831 | 401.5643 | 387.8035 | [6 empty] | 2015-03-31
FL_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.1011 | 2.9368 | 3.3974 | 3.2606 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 2045.9597 | 991.8213 | 1992.2271 | 962.0005 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 991.8213 | 0 | 962.0005 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 2045.9597 | 1983.6679 | 1992.2271 | 1924.0707 | [6 empty] | 2015-03-31
FL_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 623.585 | 590.5577 | 683.1648 | 655.6597 | [6 empty] | 2015-03-31
FL_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2387.0587 | 2305.588 | 2324.4499 | 2236.3221 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
FL_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.6408 | 11.2497 | 11.4093 | 11.0209 | [6 empty] | 2015-03-31
FL_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.3799 | 32.5564 | 35.5277 | 31.3409 | [6 empty] | 2015-03-31
FL_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 288.7145 | 254.6069 | 276.2536 | 241.6131 | [6 empty] | 2015-03-31
FL_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.7419 | 28.4925 | 31.7249 | 27.0221 | [6 empty] | 2015-03-31
FL_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.8934 | 42.8158 | 42.7971 | 42.7178 | [6 empty] | 2015-03-31
FL_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.7704 | 0.76606 | 0.76527 | 0.75852 | [6 empty] | 2015-03-31
FL_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.5684 | 9.4959 | 9.4514 | 9.3547 | [6 empty] | 2015-03-31
FL_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.64869 | 0.62234 | 0.62722 | 0.61279 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 11.0372 | 5.3505 | 10.7476 | 5.1896 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.3505 | 0 | 5.1896 | [6 empty] | 2015-03-31
FL_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 33.1117 | 32.1032 | 32.2429 | 31.1379 | [6 empty] | 2015-03-31
FL_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 13.4791 | 12.7652 | 14.767 | 14.1725 | [6 empty] | 2015-03-31
FL_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.2133 | 42.7035 | 43.0533 | 41.4195 | [6 empty] | 2015-03-31
FL_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8634 | 3.8437 | 3.8373 | 3.8232 | [6 empty] | 2015-03-31
FL_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
FL_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
FL_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
FL_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
FL_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4268.1659 | 3940.591 | 4160.3952 | 3886.2693 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 10.7116 | 10.2712 | 9.3782 | 9.3496 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 46.1369 | 40.2798 | 40.6216 | 38.3889 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.6186 | 6.2184 | 6.6953 | 6.1575 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.004 | 5.5587 | 5.9017 | 5.2971 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4047.0608 | 3919.928 | 3241.8864 | 3220.6976 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13878.664 | 12077.616 | 12183.56 | 11526.7072 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2415.5232 | 2246.0128 | 2479.0896 | 2203.6352 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2097.6912 | 1885.8032 | 2076.5024 | 1758.6704 | [6 empty] | 2015-03-31
FL_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
FL_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | Yes | Yes | Yes | [6 empty] | 2015-03-31
FL_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 1.7728 | 0.80243 | 2.4176 | 1.3637 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.7399 | 2.6571 | 2.1914 | 2.1769 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.7911 | 12.9717 | 13.0818 | 12.3627 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6949 | 1.5754 | 1.7304 | 1.5397 | [6 empty] | 2015-03-31
FL_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.477 | 1.3207 | 1.4495 | 1.2364 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.7478 | 20.699 | 26.2313 | 20.6374 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.3597 | 20.6818 | 25.8688 | 20.6561 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.9116 | 18.9437 | 23.4653 | 19.1389 | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.2963 | 26.7714 | 31.1666 | 25.9022 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.4597 | 5.4366 | 6.247 | 5.1938 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7733.912 | 6208.3184 | 7861.0448 | 6187.1296 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7606.7792 | 6208.3184 | 7755.1008 | 6208.3184 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6865.1712 | 5678.5984 | 7034.6816 | 5742.1648 | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9683.2816 | 8030.5552 | 9344.2608 | 7776.2896 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1928.1808 | 1631.5376 | 1864.6144 | 1567.9712 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
FL_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | [6 empty] | 2015-03-31
FL_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
FL_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
FL_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2015-03-31
FL_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
FL_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
FL_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
FL_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
FL_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7726.4959 | 6211.4332 | 7852.8447 | 6192.9565 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7610.0423 | 6206.2631 | 7762.8135 | 6198.5504 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 5684.7008 | 6777.6191 | 5743.2878 | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
FL_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
FL_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
FL_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
FL_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
FL_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
FL_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
FL_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.0836 | 1.0205 | 1.1773 | 1.0983 | [6 empty] | 2015-03-31
FL_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 108.9477 | 102.6041 | 118.3682 | 110.4232 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.3125 | 9.1637 | 11.525 | 9.1365 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.142 | 9.1561 | 11.3657 | 9.1447 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.0664 | 8.3866 | 10.3097 | 8.4731 | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.1897 | 11.1299 | 13.6933 | 11.3804 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3583 | 1.1432 | 1.3136 | 1.0921 | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
FL_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.355 | 2.2178 | 2.5586 | 2.3869 | [6 empty] | 2015-03-31
FL_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
FL_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
FL_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
FL_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
FL_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
FL_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 101.2403 | 96.29 | 100.9955 | 96.3704 | [6 empty] | 2015-03-31
FL_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1327 | 2.0607 | 2.2735 | 2.0766 | [6 empty] | 2015-03-31
FL_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.7107 | 5.3086 | 5.606 | 5.1942 | [6 empty] | 2015-03-31
FL_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6221 | 2.4732 | 2.5902 | 2.4192 | [6 empty] | 2015-03-31
FL_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.4042 | 4.3494 | 4.487 | 4.4246 | [6 empty] | 2015-03-31
FL_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 656.8528 | 635.664 | 720.4192 | 635.664 | [6 empty] | 2015-03-31
FL_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1716.2928 | 1589.16 | 1673.9152 | 1567.9712 | [6 empty] | 2015-03-31
FL_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 720.4192 | [6 empty] | 2015-03-31
FL_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1462.0272 | 1462.0272 | 1504.4048 | 1462.0272 | [6 empty] | 2015-03-31
FL_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
FL_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
FL_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
FL_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
FL_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
FL_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
FL_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
FL_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
FL_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
FL_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.2008 | 1.1163 | 1.1788 | 1.0922 | [6 empty] | 2015-03-31
FL_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0428 | 1.0355 | 1.0514 | 1.0436 | [6 empty] | 2015-03-31
FL_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.80246 | 0.74293 | 0.66981 | 0.62963 | [6 empty] | 2015-03-31
FL_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.79778 | 0.73924 | 0.66667 | 0.62535 | [6 empty] | 2015-03-31
FL_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 1.0076 | 0.89513 | 0.93225 | 0.79661 | [6 empty] | 2015-03-31
FL_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.2377 | 1.0958 | 1.0738 | 0.92807 | [6 empty] | 2015-03-31
FL_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.73275 | 0.68839 | 0.79236 | 0.67798 | [6 empty] | 2015-03-31
FL_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73488 | 0.69366 | 0.80426 | 0.69671 | [6 empty] | 2015-03-31
FL_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.1912 | 1.0586 | 1.1398 | 0.97643 | [6 empty] | 2015-03-31
FL_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.939 | 1.7932 | 1.6272 | 1.5508 | [6 empty] | 2015-03-31
FL_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.9313 | 1.7872 | 1.6223 | 1.5462 | [6 empty] | 2015-03-31
FL_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.444 | 2.1719 | 2.2263 | 1.9439 | [6 empty] | 2015-03-31
FL_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.9459 | 2.6099 | 2.5302 | 2.2249 | [6 empty] | 2015-03-31
FL_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7846 | 1.6792 | 1.8949 | 1.6951 | [6 empty] | 2015-03-31
FL_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7771 | 1.6735 | 1.8992 | 1.6987 | [6 empty] | 2015-03-31
FL_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3959 | 2.1301 | 2.435 | 2.1103 | [6 empty] | 2015-03-31
FL_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.8222 | 2.5096 | 2.661 | 2.3194 | [6 empty] | 2015-03-31
FL_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.323 | 2.2132 | 2.313 | 2.1631 | [6 empty] | 2015-03-31
FL_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1929 | 1.0835 | 1.0658 | 0.95206 | [6 empty] | 2015-03-31
FL_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1845 | 1.0769 | 1.0658 | 0.9467 | [6 empty] | 2015-03-31
FL_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4693 | 1.2982 | 1.331 | 1.1734 | [6 empty] | 2015-03-31
FL_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.7746 | 1.5569 | 1.5598 | 1.3581 | [6 empty] | 2015-03-31
FL_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.1744 | 1.0525 | 1.2421 | 1.0995 | [6 empty] | 2015-03-31
FL_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1758 | 1.0539 | 1.2451 | 1.102 | [6 empty] | 2015-03-31
FL_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.462 | 1.3056 | 1.499 | 1.3239 | [6 empty] | 2015-03-31
FL_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7258 | 1.5136 | 1.6473 | 1.428 | [6 empty] | 2015-03-31
FL_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
FL_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
FL_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
FL_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
FL_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
FL_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
FL_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
FL_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
FL_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
FL_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
FL_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
FL_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
FL_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 233.0768 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
FL_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 233.0768 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
FL_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 296.6432 | 317.832 | 254.2656 | [6 empty] | 2015-03-31
FL_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 381.3984 | 381.3984 | 317.832 | [6 empty] | 2015-03-31
FL_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 254.2656 | 211.888 | [6 empty] | 2015-03-31
FL_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 254.2656 | 211.888 | [6 empty] | 2015-03-31
FL_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | 402.5872 | 317.832 | [6 empty] | 2015-03-31
FL_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 529.72 | 487.3424 | [6 empty] | 2015-03-31
FL_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 529.72 | 487.3424 | [6 empty] | 2015-03-31
FL_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 741.608 | 783.9856 | 656.8528 | [6 empty] | 2015-03-31
FL_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1080.6288 | 932.3072 | 911.1184 | 762.7968 | [6 empty] | 2015-03-31
FL_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 614.4752 | 529.72 | [6 empty] | 2015-03-31
FL_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 614.4752 | 529.72 | [6 empty] | 2015-03-31
FL_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 720.4192 | 868.7408 | 720.4192 | [6 empty] | 2015-03-31
FL_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 889.9296 | 953.496 | 805.1744 | [6 empty] | 2015-03-31
FL_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 911.1184 | 974.6848 | 889.9296 | [6 empty] | 2015-03-31
FL_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 360.2096 | 317.832 | [6 empty] | 2015-03-31
FL_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | 360.2096 | 317.832 | [6 empty] | 2015-03-31
FL_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 444.9648 | 487.3424 | 402.5872 | [6 empty] | 2015-03-31
FL_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 572.0976 | 572.0976 | 487.3424 | [6 empty] | 2015-03-31
FL_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 339.0208 | 444.9648 | 381.3984 | [6 empty] | 2015-03-31
FL_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 444.9648 | 381.3984 | [6 empty] | 2015-03-31
FL_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 444.9648 | 550.9088 | 466.1536 | [6 empty] | 2015-03-31
FL_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 550.9088 | 614.4752 | 508.5312 | [6 empty] | 2015-03-31
FL_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
FL_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.18141 | 0.16307 | 0.14319 | 0.13394 | [6 empty] | 2015-03-31
FL_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.17992 | 0.1619 | 0.14222 | 0.13303 | [6 empty] | 2015-03-31
FL_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.24437 | 0.20677 | 0.22392 | 0.17874 | [6 empty] | 2015-03-31
FL_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.31627 | 0.27035 | 0.26507 | 0.2192 | [6 empty] | 2015-03-31
FL_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15891 | 0.14644 | 0.17431 | 0.14423 | [6 empty] | 2015-03-31
FL_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.1596 | 0.1484 | 0.17844 | 0.14821 | [6 empty] | 2015-03-31
FL_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.29717 | 0.2553 | 0.28178 | 0.23106 | [6 empty] | 2015-03-31
FL_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.46358 | 0.41631 | 0.3707 | 0.34797 | [6 empty] | 2015-03-31
FL_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.4611 | 0.41439 | 0.36913 | 0.34652 | [6 empty] | 2015-03-31
FL_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.61413 | 0.52518 | 0.55591 | 0.46116 | [6 empty] | 2015-03-31
FL_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.77317 | 0.66414 | 0.64354 | 0.54732 | [6 empty] | 2015-03-31
FL_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.41298 | 0.37897 | 0.4413 | 0.37701 | [6 empty] | 2015-03-31
FL_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.41062 | 0.37716 | 0.44267 | 0.3782 | [6 empty] | 2015-03-31
FL_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.59575 | 0.50803 | 0.61666 | 0.50901 | [6 empty] | 2015-03-31
FL_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.72969 | 0.63035 | 0.68322 | 0.57688 | [6 empty] | 2015-03-31
FL_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67939 | 0.6409 | 0.68377 | 0.63118 | [6 empty] | 2015-03-31
FL_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.30005 | 0.26428 | 0.25534 | 0.22619 | [6 empty] | 2015-03-31
FL_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29733 | 0.26216 | 0.25534 | 0.22447 | [6 empty] | 2015-03-31
FL_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.3786 | 0.32194 | 0.33944 | 0.2871 | [6 empty] | 2015-03-31
FL_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.4777 | 0.40601 | 0.41026 | 0.34612 | [6 empty] | 2015-03-31
FL_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.28682 | 0.24773 | 0.31144 | 0.26544 | [6 empty] | 2015-03-31
FL_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.28731 | 0.24812 | 0.31236 | 0.26626 | [6 empty] | 2015-03-31
FL_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.37431 | 0.31837 | 0.3852 | 0.32815 | [6 empty] | 2015-03-31
FL_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.45911 | 0.39104 | 0.4369 | 0.36633 | [6 empty] | 2015-03-31
HI_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.782 | 1.6794 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7944 | 1.6215 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4976 | 1.2578 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7338 | 1.5862 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7894 | 1.4801 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 635.664 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 678.0416 | 550.9088 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 805.1744 | 656.8528 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.4685 | 0.43143 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.50865 | 0.44533 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.47791 | 0.38836 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.4864 | 0.43311 | [8 empty] | 2015-03-31
HI_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.57102 | 0.46344 | [8 empty] | 2015-03-31
HI_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10827.4768 | 10467.2672 | [8 empty] | 2015-03-31
HI_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24621.3856 | 23244.1136 | [8 empty] | 2015-03-31
HI_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 196483.7427 | 183516.1971 | [8 empty] | 2015-03-31
HI_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22820.3376 | 20129.36 | [8 empty] | 2015-03-31
HI_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | [8 empty] | 2015-03-31
HI_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
HI_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
HI_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
HI_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
HI_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
HI_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
HI_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
HI_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
HI_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
HI_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
HI_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
HI_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_LO_CAV_bas (economizer) | CAV_bas (economizer) | No | No | [8 empty] | 2015-03-31
HI_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | No | No | [8 empty] | 2015-03-31
HI_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | No | No | [8 empty] | 2015-03-31
HI_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | No | No | [8 empty] | 2015-03-31
HI_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | [8 empty] | 2015-03-31
HI_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
HI_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
HI_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
HI_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
HI_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
HI_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
HI_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
HI_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
HI_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
HI_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 377.1764 | 365.4941 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 377.1764 | 365.4941 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
HI_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 357.9928 | 346.9048 | [8 empty] | 2015-03-31
HI_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 357.9928 | 346.9048 | [8 empty] | 2015-03-31
HI_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.4349 | 3.2327 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1776.0287 | 860.5442 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 860.5442 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1776.0287 | 1721.0281 | [8 empty] | 2015-03-31
HI_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 690.7079 | 650.0598 | [8 empty] | 2015-03-31
HI_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2072.2712 | 2000.4693 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
HI_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.6234 | 11.2358 | [8 empty] | 2015-03-31
HI_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.4087 | 31.6188 | [8 empty] | 2015-03-31
HI_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 276.3275 | 244.215 | [8 empty] | 2015-03-31
HI_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.7994 | 27.5419 | [8 empty] | 2015-03-31
HI_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.8485 | 42.7712 | [8 empty] | 2015-03-31
HI_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.76918 | 0.76216 | [8 empty] | 2015-03-31
HI_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.6354 | 9.4262 | [8 empty] | 2015-03-31
HI_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.65514 | 0.6263 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.5814 | 4.6423 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.6423 | [8 empty] | 2015-03-31
HI_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 28.7443 | 27.854 | [8 empty] | 2015-03-31
HI_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 14.93 | 14.0514 | [8 empty] | 2015-03-31
HI_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.3817 | 37.0513 | [8 empty] | 2015-03-31
HI_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.829 | 3.7997 | [8 empty] | 2015-03-31
HI_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | [8 empty] | 2015-03-31
HI_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
HI_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
HI_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
HI_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 3605.6892 | 3403.6064 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.2816 | 8.9617 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 42.1834 | 38.6382 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.1924 | 5.749 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6162 | 5.103 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3644.4736 | 3496.152 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14132.9296 | 12395.448 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2436.712 | 2224.824 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2140.0688 | 1885.8032 | [8 empty] | 2015-03-31
HI_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
HI_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | No | No | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | No | No | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | No | No | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | No | No | [8 empty] | 2015-03-31
HI_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | Yes | [8 empty] | 2015-03-31
HI_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 0.69995 | 0.021282 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.4618 | 2.3722 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 15.0634 | 13.3007 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7076 | 1.5523 | [8 empty] | 2015-03-31
HI_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4999 | 1.3164 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.0183 | 21.1898 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.8293 | 21.222 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.2178 | 19.1749 | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.9714 | 26.9277 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.5894 | 5.5205 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7797.4784 | 6356.64 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7755.1008 | 6377.8288 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6971.1152 | 5763.3536 | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9598.5264 | 8072.9328 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1970.5584 | 1652.7264 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
HI_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
HI_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
HI_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
HI_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | [8 empty] | 2015-03-31
HI_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
HI_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
HI_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
HI_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
HI_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7807.6702 | 6358.7165 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7750.9266 | 6368.3786 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 5754.0729 | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
HI_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | No | No | [8 empty] | 2015-03-31
HI_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | No | No | [8 empty] | 2015-03-31
HI_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | No | No | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | No | No | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | No | No | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | No | No | [8 empty] | 2015-03-31
HI_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
HI_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
HI_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
HI_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | [8 empty] | 2015-03-31
HI_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
HI_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
HI_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2473 | 1.1565 | [8 empty] | 2015-03-31
HI_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 125.4101 | 116.2791 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.4314 | 9.381 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.3483 | 9.3953 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.201 | 8.489 | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.0469 | 11.1949 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3856 | 1.1608 | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
HI_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.7108 | 2.5134 | [8 empty] | 2015-03-31
HI_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
HI_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
HI_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
HI_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | NO | NO | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | NO | NO | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | NO | YES | [8 empty] | 2015-03-31
HI_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
HI_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 101.159 | 96.2245 | [8 empty] | 2015-03-31
HI_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0473 | 1.9868 | [8 empty] | 2015-03-31
HI_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.5603 | 5.3217 | [8 empty] | 2015-03-31
HI_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5787 | 2.4989 | [8 empty] | 2015-03-31
HI_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.1604 | 4.1356 | [8 empty] | 2015-03-31
HI_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 656.8528 | [8 empty] | 2015-03-31
HI_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1673.9152 | 1589.16 | [8 empty] | 2015-03-31
HI_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | [8 empty] | 2015-03-31
HI_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1462.0272 | 1462.0272 | [8 empty] | 2015-03-31
HI_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
HI_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
HI_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
HI_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
HI_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
HI_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
HI_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | [8 empty] | 2015-03-31
HI_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
HI_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
HI_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1692 | 1.119 | [8 empty] | 2015-03-31
HI_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0406 | 1.0342 | [8 empty] | 2015-03-31
HI_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.65981 | 0.61709 | [8 empty] | 2015-03-31
HI_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.65436 | 0.6128 | [8 empty] | 2015-03-31
HI_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.89844 | 0.79226 | [8 empty] | 2015-03-31
HI_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.1284 | 1.0003 | [8 empty] | 2015-03-31
HI_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.68451 | 0.62692 | [8 empty] | 2015-03-31
HI_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.69553 | 0.63 | [8 empty] | 2015-03-31
HI_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.1502 | 1.0204 | [8 empty] | 2015-03-31
HI_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6145 | 1.5093 | [8 empty] | 2015-03-31
HI_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6055 | 1.5022 | [8 empty] | 2015-03-31
HI_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1845 | 1.9424 | [8 empty] | 2015-03-31
HI_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6928 | 2.3899 | [8 empty] | 2015-03-31
HI_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6847 | 1.5359 | [8 empty] | 2015-03-31
HI_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.6887 | 1.5294 | [8 empty] | 2015-03-31
HI_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2851 | 2.0036 | [8 empty] | 2015-03-31
HI_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.7366 | 2.4282 | [8 empty] | 2015-03-31
HI_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1944 | 2.0889 | [8 empty] | 2015-03-31
HI_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0042 | 0.92121 | [8 empty] | 2015-03-31
HI_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0173 | 0.91382 | [8 empty] | 2015-03-31
HI_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3216 | 1.1629 | [8 empty] | 2015-03-31
HI_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6277 | 1.4294 | [8 empty] | 2015-03-31
HI_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.1308 | 0.99962 | [8 empty] | 2015-03-31
HI_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1331 | 1.0016 | [8 empty] | 2015-03-31
HI_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.4167 | 1.2482 | [8 empty] | 2015-03-31
HI_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.665 | 1.4602 | [8 empty] | 2015-03-31
HI_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
HI_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
HI_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
HI_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
HI_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
HI_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
HI_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
HI_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
HI_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
HI_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
HI_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
HI_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
HI_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
HI_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | [8 empty] | 2015-03-31
HI_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 275.4544 | [8 empty] | 2015-03-31
HI_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | [8 empty] | 2015-03-31
HI_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | [8 empty] | 2015-03-31
HI_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | [8 empty] | 2015-03-31
HI_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | [8 empty] | 2015-03-31
HI_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 508.5312 | [8 empty] | 2015-03-31
HI_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 508.5312 | [8 empty] | 2015-03-31
HI_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 699.2304 | [8 empty] | 2015-03-31
HI_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 889.9296 | [8 empty] | 2015-03-31
HI_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2015-03-31
HI_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2015-03-31
HI_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 720.4192 | [8 empty] | 2015-03-31
HI_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 911.1184 | [8 empty] | 2015-03-31
HI_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 889.9296 | [8 empty] | 2015-03-31
HI_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | [8 empty] | 2015-03-31
HI_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 317.832 | [8 empty] | 2015-03-31
HI_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
HI_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 550.9088 | [8 empty] | 2015-03-31
HI_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | [8 empty] | 2015-03-31
HI_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | [8 empty] | 2015-03-31
HI_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 444.9648 | [8 empty] | 2015-03-31
HI_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 550.9088 | [8 empty] | 2015-03-31
HI_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
HI_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.1566 | 0.1435 | [8 empty] | 2015-03-31
HI_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15486 | 0.14215 | [8 empty] | 2015-03-31
HI_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.22921 | 0.19423 | [8 empty] | 2015-03-31
HI_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.30351 | 0.26091 | [8 empty] | 2015-03-31
HI_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15789 | 0.14495 | [8 empty] | 2015-03-31
HI_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16147 | 0.14596 | [8 empty] | 2015-03-31
HI_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.30759 | 0.26527 | [8 empty] | 2015-03-31
HI_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40225 | 0.36792 | [8 empty] | 2015-03-31
HI_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.39933 | 0.36566 | [8 empty] | 2015-03-31
HI_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.57351 | 0.49185 | [8 empty] | 2015-03-31
HI_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.73764 | 0.637 | [8 empty] | 2015-03-31
HI_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.41023 | 0.37428 | [8 empty] | 2015-03-31
HI_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.41156 | 0.37221 | [8 empty] | 2015-03-31
HI_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.60097 | 0.50876 | [8 empty] | 2015-03-31
HI_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.74944 | 0.64864 | [8 empty] | 2015-03-31
HI_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67212 | 0.63484 | [8 empty] | 2015-03-31
HI_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.26048 | 0.23323 | [8 empty] | 2015-03-31
HI_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.25832 | 0.23086 | [8 empty] | 2015-03-31
HI_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.35234 | 0.30032 | [8 empty] | 2015-03-31
HI_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.45319 | 0.38824 | [8 empty] | 2015-03-31
HI_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.29469 | 0.25203 | [8 empty] | 2015-03-31
HI_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.29545 | 0.25262 | [8 empty] | 2015-03-31
HI_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.37689 | 0.32168 | [8 empty] | 2015-03-31
HI_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46465 | 0.3978 | [8 empty] | 2015-03-31
AL_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8611 | 1.816 | 1.8204 | 1.7711 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9512 | 1.7955 | 1.8575 | 1.7746 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4619 | 1.2383 | 1.2887 | 1.1939 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8745 | 1.7558 | 1.7909 | 1.7301 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7511 | 1.4858 | 1.5382 | 1.4318 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 656.8528 | 720.4192 | 678.0416 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 508.5312 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 635.664 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 762.7968 | 614.4752 | 656.8528 | 614.4752 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44673 | 0.43087 | 0.4545 | 0.43579 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52349 | 0.46942 | 0.5092 | 0.47809 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.45437 | 0.36765 | 0.40406 | 0.3659 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.49689 | 0.45516 | 0.48616 | 0.46417 | [6 empty] | 2015-03-31
AL_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.53621 | 0.4388 | 0.47032 | 0.43074 | [6 empty] | 2015-03-31
AL_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10657.9664 | 10297.7568 | 10721.5328 | 10340.1344 | [6 empty] | 2015-03-31
AL_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24960.4064 | 23434.8128 | 24621.3856 | 23731.456 | [6 empty] | 2015-03-31
AL_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 200212.9715 | 185211.3011 | 197394.8611 | 187753.9571 | [6 empty] | 2015-03-31
AL_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22121.1072 | 19853.9056 | 21803.2752 | 20235.304 | [6 empty] | 2015-03-31
AL_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2015-03-31
AL_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
AL_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
AL_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
AL_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
AL_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
AL_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
AL_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
AL_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
AL_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
AL_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
AL_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
AL_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AL_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AL_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AL_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AL_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AL_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AL_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AL_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AL_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AL_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AL_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 423.1537 | 407.6999 | 398.1546 | 386.7909 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 423.1537 | 407.6999 | 398.1546 | 386.7909 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
AL_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 401.6305 | 386.9699 | 377.9063 | 367.1226 | [6 empty] | 2015-03-31
AL_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 401.6305 | 386.9699 | 377.9063 | 367.1226 | [6 empty] | 2015-03-31
AL_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.0895 | 3.9249 | 4.1822 | 4.2099 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1992.5441 | 959.9162 | 1874.9347 | 910.6867 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 959.9162 | 0 | 910.6867 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1992.5441 | 1919.7911 | 1874.9347 | 1821.3606 | [6 empty] | 2015-03-31
AL_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 822.3401 | 789.232 | 840.9864 | 846.5452 | [6 empty] | 2015-03-31
AL_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2324.9254 | 2231.4085 | 2187.5031 | 2116.9692 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AL_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.4478 | 11.057 | 11.5032 | 11.0986 | [6 empty] | 2015-03-31
AL_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.8783 | 31.8866 | 35.406 | 32.2711 | [6 empty] | 2015-03-31
AL_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 281.5583 | 246.4492 | 277.5994 | 264.0436 | [6 empty] | 2015-03-31
AL_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 31.7992 | 27.154 | 31.335 | 27.6812 | [6 empty] | 2015-03-31
AL_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.0921 | 43.0123 | 43.6898 | 43.6082 | [6 empty] | 2015-03-31
AL_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.76985 | 0.76303 | 0.78005 | 0.77398 | [6 empty] | 2015-03-31
AL_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.5034 | 9.4044 | 9.6339 | 9.5387 | [6 empty] | 2015-03-31
AL_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.62976 | 0.61615 | 0.64494 | 0.62321 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.7494 | 5.1784 | 10.1143 | 4.9128 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.1784 | 0 | 4.9128 | [6 empty] | 2015-03-31
AL_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.2482 | 31.0705 | 30.343 | 29.477 | [6 empty] | 2015-03-31
AL_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.7754 | 17.0597 | 18.1784 | 18.2986 | [6 empty] | 2015-03-31
AL_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.0604 | 41.3298 | 40.5164 | 39.2102 | [6 empty] | 2015-03-31
AL_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8356 | 3.8215 | 3.8424 | 3.8176 | [6 empty] | 2015-03-31
AL_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
AL_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
AL_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | NO | YES | [6 empty] | 2015-03-31
AL_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
AL_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4662.9491 | 4364.0259 | 4368.9293 | 4435.4881 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.3754 | 9.2997 | 9.0974 | 9.0297 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 41.4705 | 38.6657 | 39.3318 | 37.6691 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3 | 5.3632 | 6.0852 | 5.2021 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4878 | 4.9742 | 5.2636 | 4.9367 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3305.4528 | 3390.208 | 3347.8304 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12670.9024 | 11611.4624 | 12925.168 | 11802.1616 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2309.5792 | 2076.5024 | 2309.5792 | 2118.88 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1906.992 | 1652.7264 | 1885.8032 | 1716.2928 | [6 empty] | 2015-03-31
AL_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
AL_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AL_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.3696 | 2.0522 | 2.6564 | 1.7388 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.268 | 2.236 | 2.2945 | 2.2651 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.5949 | 12.4519 | 13.86 | 12.6741 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6188 | 1.4563 | 1.6113 | 1.4899 | [6 empty] | 2015-03-31
AL_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.3319 | 1.1509 | 1.3163 | 1.2015 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.2089 | 20.0436 | 23.3077 | 20.3628 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.7936 | 20.0167 | 22.9015 | 20.4031 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.4523 | 18.3866 | 20.7745 | 18.8034 | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 30.6489 | 25.4431 | 28.9607 | 25.7297 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.0572 | 5.1586 | 5.8082 | 5.0496 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7564.4016 | 6017.6192 | 6992.304 | 6102.3744 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7437.2688 | 5996.4304 | 6865.1712 | 6123.5632 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6738.0384 | 5509.088 | 6229.5072 | 5636.2208 | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9195.9392 | 7627.968 | 8687.408 | 7712.7232 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1822.2368 | 1546.7824 | 1737.4816 | 1525.5936 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
AL_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | [6 empty] | 2015-03-31
AL_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
AL_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
AL_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2015-03-31
AL_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
AL_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
AL_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
AL_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
AL_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7564.7618 | 6014.7375 | 6994.2534 | 6110.5533 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7440.1293 | 6006.6858 | 6872.3754 | 6122.6521 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6737.5723 | 5517.5212 | 6234.1052 | 5642.5986 | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AL_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AL_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AL_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AL_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AL_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AL_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2907 | 1.1837 | 1.2968 | 1.2411 | [6 empty] | 2015-03-31
AL_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 129.772 | 119.0107 | 130.38 | 124.7874 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.0758 | 8.8736 | 10.2405 | 9.0149 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.8933 | 8.8617 | 10.062 | 9.0327 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.8647 | 8.14 | 9.1972 | 8.3245 | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.4659 | 11.1787 | 12.7242 | 11.3046 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2737 | 1.0847 | 1.2213 | 1.0618 | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
AL_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8051 | 2.5725 | 2.8182 | 2.6974 | [6 empty] | 2015-03-31
AL_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AL_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AL_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AL_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AL_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AL_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 101.5172 | 96.0212 | 97.6589 | 95.6968 | [6 empty] | 2015-03-31
AL_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1796 | 2.0087 | 2.0788 | 2.0001 | [6 empty] | 2015-03-31
AL_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.6567 | 5.1838 | 5.4784 | 5.2659 | [6 empty] | 2015-03-31
AL_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6207 | 2.4351 | 2.5967 | 2.4694 | [6 empty] | 2015-03-31
AL_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.4511 | 4.3944 | 4.4217 | 4.3852 | [6 empty] | 2015-03-31
AL_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 614.4752 | 678.0416 | 635.664 | [6 empty] | 2015-03-31
AL_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1695.104 | 1546.7824 | 1652.7264 | 1589.16 | [6 empty] | 2015-03-31
AL_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 783.9856 | 741.608 | [6 empty] | 2015-03-31
AL_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1462.0272 | 1525.5936 | 1504.4048 | [6 empty] | 2015-03-31
AL_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
AL_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
AL_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
AL_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
AL_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AL_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AL_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AL_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AL_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AL_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1894 | 1.09 | 1.152 | 1.1073 | [6 empty] | 2015-03-31
AL_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0488 | 1.0434 | 1.0637 | 1.0521 | [6 empty] | 2015-03-31
AL_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.70051 | 0.65199 | 0.63224 | 0.60876 | [6 empty] | 2015-03-31
AL_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69735 | 0.64909 | 0.62915 | 0.60629 | [6 empty] | 2015-03-31
AL_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.87085 | 0.74803 | 0.74562 | 0.71826 | [6 empty] | 2015-03-31
AL_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0712 | 0.92176 | 0.90927 | 0.86213 | [6 empty] | 2015-03-31
AL_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.70908 | 0.62933 | 0.65482 | 0.62715 | [6 empty] | 2015-03-31
AL_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.72203 | 0.62717 | 0.6681 | 0.64037 | [6 empty] | 2015-03-31
AL_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0846 | 0.92833 | 0.93525 | 0.88482 | [6 empty] | 2015-03-31
AL_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7017 | 1.5987 | 1.5976 | 1.5416 | [6 empty] | 2015-03-31
AL_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6966 | 1.5939 | 1.5925 | 1.5376 | [6 empty] | 2015-03-31
AL_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0999 | 1.8821 | 1.8932 | 1.8283 | [6 empty] | 2015-03-31
AL_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.5415 | 2.2278 | 2.2567 | 2.1354 | [6 empty] | 2015-03-31
AL_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7294 | 1.5504 | 1.6589 | 1.5924 | [6 empty] | 2015-03-31
AL_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.733 | 1.5457 | 1.6625 | 1.5955 | [6 empty] | 2015-03-31
AL_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.1887 | 1.9203 | 2.1009 | 1.9941 | [6 empty] | 2015-03-31
AL_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5565 | 2.2293 | 2.3069 | 2.1783 | [6 empty] | 2015-03-31
AL_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2485 | 2.0543 | 2.1222 | 2.0737 | [6 empty] | 2015-03-31
AL_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0563 | 0.96996 | 1.0032 | 0.94353 | [6 empty] | 2015-03-31
AL_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0504 | 0.96449 | 1.035 | 0.93871 | [6 empty] | 2015-03-31
AL_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2657 | 1.1733 | 1.2601 | 1.1644 | [6 empty] | 2015-03-31
AL_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5643 | 1.3615 | 1.4314 | 1.3169 | [6 empty] | 2015-03-31
AL_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.16 | 1.0372 | 1.1392 | 1.0524 | [6 empty] | 2015-03-31
AL_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1621 | 1.0372 | 1.1414 | 1.0544 | [6 empty] | 2015-03-31
AL_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3993 | 1.2436 | 1.3701 | 1.2646 | [6 empty] | 2015-03-31
AL_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.5865 | 1.3769 | 1.4881 | 1.3703 | [6 empty] | 2015-03-31
AL_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AL_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
AL_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AL_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AL_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AL_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AL_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AL_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AL_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AL_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AL_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
AL_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AL_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
AL_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
AL_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 233.0768 | 254.2656 | 233.0768 | [6 empty] | 2015-03-31
AL_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 317.832 | 317.832 | 296.6432 | [6 empty] | 2015-03-31
AL_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
AL_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
AL_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 317.832 | 339.0208 | 296.6432 | [6 empty] | 2015-03-31
AL_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
AL_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
AL_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 635.664 | 699.2304 | 656.8528 | [6 empty] | 2015-03-31
AL_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 783.9856 | 847.552 | 783.9856 | [6 empty] | 2015-03-31
AL_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 508.5312 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
AL_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 508.5312 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
AL_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 656.8528 | 741.608 | 699.2304 | [6 empty] | 2015-03-31
AL_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 783.9856 | 847.552 | 805.1744 | [6 empty] | 2015-03-31
AL_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 868.7408 | 911.1184 | 889.9296 | [6 empty] | 2015-03-31
AL_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 360.2096 | 339.0208 | [6 empty] | 2015-03-31
AL_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 360.2096 | 339.0208 | [6 empty] | 2015-03-31
AL_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 402.5872 | 466.1536 | 423.776 | [6 empty] | 2015-03-31
AL_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 508.5312 | 550.9088 | 487.3424 | [6 empty] | 2015-03-31
AL_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 423.776 | 381.3984 | [6 empty] | 2015-03-31
AL_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 423.776 | 381.3984 | [6 empty] | 2015-03-31
AL_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 508.5312 | 466.1536 | [6 empty] | 2015-03-31
AL_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 508.5312 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
AL_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AL_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15595 | 0.14138 | 0.14502 | 0.13741 | [6 empty] | 2015-03-31
AL_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15494 | 0.14047 | 0.14403 | 0.13662 | [6 empty] | 2015-03-31
AL_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.21434 | 0.1715 | 0.18235 | 0.16906 | [6 empty] | 2015-03-31
AL_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.27018 | 0.22234 | 0.22972 | 0.21423 | [6 empty] | 2015-03-31
AL_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15231 | 0.13387 | 0.14399 | 0.13522 | [6 empty] | 2015-03-31
AL_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15646 | 0.1359 | 0.14825 | 0.13945 | [6 empty] | 2015-03-31
AL_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.26929 | 0.21951 | 0.23303 | 0.2166 | [6 empty] | 2015-03-31
AL_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40421 | 0.37063 | 0.39242 | 0.37404 | [6 empty] | 2015-03-31
AL_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40255 | 0.3691 | 0.39076 | 0.37272 | [6 empty] | 2015-03-31
AL_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.53941 | 0.4519 | 0.49186 | 0.45937 | [6 empty] | 2015-03-31
AL_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.66158 | 0.56095 | 0.59641 | 0.55632 | [6 empty] | 2015-03-31
AL_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.39873 | 0.35577 | 0.3948 | 0.37345 | [6 empty] | 2015-03-31
AL_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.39991 | 0.35426 | 0.39598 | 0.37447 | [6 empty] | 2015-03-31
AL_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.55643 | 0.46509 | 0.52964 | 0.49505 | [6 empty] | 2015-03-31
AL_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.6604 | 0.55571 | 0.60605 | 0.56381 | [6 empty] | 2015-03-31
AL_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67515 | 0.60886 | 0.6532 | 0.6359 | [6 empty] | 2015-03-31
AL_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.26575 | 0.23841 | 0.26056 | 0.24081 | [6 empty] | 2015-03-31
AL_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.26385 | 0.23664 | 0.26014 | 0.23922 | [6 empty] | 2015-03-31
AL_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.32969 | 0.28617 | 0.32658 | 0.29559 | [6 empty] | 2015-03-31
AL_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.41987 | 0.35333 | 0.38911 | 0.35265 | [6 empty] | 2015-03-31
AL_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.29036 | 0.25017 | 0.29466 | 0.26645 | [6 empty] | 2015-03-31
AL_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.29104 | 0.2507 | 0.2954 | 0.26712 | [6 empty] | 2015-03-31
AL_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.36029 | 0.30935 | 0.36397 | 0.3296 | [6 empty] | 2015-03-31
AL_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.42472 | 0.3573 | 0.40402 | 0.36544 | [6 empty] | 2015-03-31
GA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8894 | 1.8441 | 1.7741 | 1.7264 | 1.7674 | 1.6619 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0216 | 1.8569 | 1.8135 | 1.7417 | 1.845 | 1.6951 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5421 | 1.3046 | 1.3343 | 1.2355 | 1.4033 | 1.3326 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.938 | 1.8113 | 1.7469 | 1.6869 | 1.7666 | 1.632 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7706 | 1.5039 | 1.5075 | 1.4001 | 1.5863 | 1.4875 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 656.8528 | 614.4752 | 635.664 | 572.0976 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 678.0416 | 720.4192 | 678.0416 | 720.4192 | 635.664 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 656.8528 | 529.72 | 593.2864 | 529.72 | 614.4752 | 593.2864 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 699.2304 | 656.8528 | 678.0416 | 614.4752 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 762.7968 | 614.4752 | 678.0416 | 614.4752 | 699.2304 | 656.8528 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44863 | 0.43288 | 0.46039 | 0.44159 | 0.44762 | 0.40978 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.53896 | 0.48258 | 0.5124 | 0.4838 | 0.51259 | 0.45572 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.47278 | 0.38196 | 0.4216 | 0.38194 | 0.44042 | 0.41529 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.51033 | 0.46639 | 0.48879 | 0.46664 | 0.48619 | 0.43709 |  |  |  |  | 2015-03-31
GA_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.53602 | 0.4396 | 0.47637 | 0.43547 | 0.50008 | 0.46141 |  |  |  |  | 2015-03-31
GA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10615.5888 | 10255.3792 | 10869.8544 | 10488.456 | 10509.6448 | 9916.3584 |  |  |  |  | 2015-03-31
GA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24833.2736 | 23328.8688 | 24621.3856 | 23731.456 | 24600.1968 | 24197.6096 |  |  |  |  | 2015-03-31
GA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 199704.4403 | 184639.2035 | 196017.5891 | 186758.0835 | 197543.1827 | 193708.0099 |  |  |  |  | 2015-03-31
GA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22417.7504 | 20108.1712 | 21866.8416 | 20298.8704 | 23731.456 | 21824.464 |  |  |  |  | 2015-03-31
GA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2015-03-31
GA_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
GA_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
GA_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
GA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
GA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
GA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
GA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
GA_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
GA_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
GA_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
GA_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
GA_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
GA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
GA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
GA_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
GA_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
GA_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
GA_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 426.3793 | 410.5491 | 384.0412 | 373.2622 | 394.1629 | 388.5394 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 426.3793 | 410.5491 | 384.0412 | 373.2622 | 394.1629 | 388.5394 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
GA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 404.7002 | 389.6692 | 364.516 | 354.2748 | 374.1221 | 368.7766 |  |  |  |  | 2015-03-31
GA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 404.7002 | 389.6692 | 364.516 | 354.2748 | 374.1221 | 368.7766 |  |  |  |  | 2015-03-31
GA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.0483 | 3.8936 | 4.1285 | 4.1635 | 4.203 | 4.105 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 2007.7604 | 966.624 | 1808.3634 | 878.8338 | 1856.0728 | 914.803 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 966.624 | 0 | 878.8338 | 0 | 914.803 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 2007.7604 | 1933.2639 | 1808.3634 | 1757.6423 | 1856.0728 | 1829.6028 |  |  |  |  | 2015-03-31
GA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 814.0631 | 782.9457 | 830.1765 | 837.2188 | 845.1693 | 825.4595 |  |  |  |  | 2015-03-31
GA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2342.6778 | 2247.1003 | 2109.995 | 2042.9481 | 2165.6297 | 2126.6379 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
GA_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.3861 | 10.9987 | 11.6553 | 11.2483 | 11.2765 | 10.6346 |  |  |  |  | 2015-03-31
GA_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.7157 | 31.7277 | 35.3879 | 32.2741 | 35.3797 | 32.9159 |  |  |  |  | 2015-03-31
GA_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 280.8513 | 245.6971 | 275.6639 | 262.6445 | 277.7936 | 272.4055 |  |  |  |  | 2015-03-31
GA_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.2381 | 27.4871 | 31.4286 | 27.7487 | 34.131 | 29.6894 |  |  |  |  | 2015-03-31
GA_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.8312 | 42.752 | 44.3165 | 44.233 | 43.69 | 43.4979 |  |  |  |  | 2015-03-31
GA_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.7663 | 0.75957 | 0.79148 | 0.78529 | 0.79347 | 0.78156 |  |  |  |  | 2015-03-31
GA_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.4685 | 9.3716 | 9.7783 | 9.6807 | 9.9218 | 9.8128 |  |  |  |  | 2015-03-31
GA_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.62661 | 0.61328 | 0.65382 | 0.633 | 0.68463 | 0.6636 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.8313 | 5.2146 | 9.7558 | 4.741 | 10.0129 | 4.935 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.2146 | 0 | 4.741 | 0 | 4.935 |  |  |  |  | 2015-03-31
GA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.494 | 31.2876 | 29.2675 | 28.446 | 30.0388 | 29.6103 |  |  |  |  | 2015-03-31
GA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.5964 | 16.9238 | 17.9447 | 18.097 | 18.2688 | 17.8428 |  |  |  |  | 2015-03-31
GA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.3886 | 41.6186 | 39.0802 | 37.8387 | 40.1102 | 39.3874 |  |  |  |  | 2015-03-31
GA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8325 | 3.8186 | 3.8424 | 3.8279 | 3.8629 | 3.8344 |  |  |  |  | 2015-03-31
GA_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | NO | YES |  |  |  |  | 2015-03-31
GA_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO |  |  |  |  | 2015-03-31
GA_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
GA_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO |  |  |  |  | 2015-03-31
GA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4587.8494 | 4299.6183 | 4367.5548 | 4439.8967 | 4303.9356 | 4195.4987 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.3413 | 9.2904 | 8.8807 | 8.8459 | 8.9353 | 8.8672 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 41.0078 | 38.3631 | 38.0939 | 36.9119 | 42.0265 | 37.0054 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.6216 | 6.1086 | 6.0119 | 5.7564 | 6.3928 | 6.1118 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.8125 | 5.2334 | 5.1919 | 4.8668 | 5.5529 | 5.1983 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3305.4528 | 3347.8304 | 3326.6416 | 3284.264 | 3263.0752 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12395.448 | 11505.5184 | 12628.5248 | 11802.1616 | 13200.6224 | 11632.6512 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2415.5232 | 2140.0688 | 2309.5792 | 2182.4464 | 2457.9008 | 2309.5792 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2012.936 | 1716.2928 | 1885.8032 | 1716.2928 | 2012.936 | 1843.4256 |  |  |  |  | 2015-03-31
GA_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
GA_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
GA_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.3529 | 2.0399 | 2.5967 | 1.6903 | 2.7562 | 1.8148 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2618 | 2.2394 | 2.2709 | 2.2541 | 2.224 | 2.2032 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.2966 | 12.3544 | 13.5615 | 12.6678 | 14.1727 | 12.4881 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6855 | 1.5067 | 1.6235 | 1.531 | 1.7169 | 1.6196 |  |  |  |  | 2015-03-31
GA_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4041 | 1.2029 | 1.3255 | 1.2098 | 1.4172 | 1.2948 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.931 | 20.5984 | 23.5036 | 20.5266 | 25.8465 | 21.8341 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.5071 | 20.5762 | 23.106 | 20.5875 | 25.3676 | 21.451 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.1456 | 18.9166 | 20.952 | 18.9655 | 23.0602 | 20.1476 |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.3852 | 25.931 | 29.2424 | 25.9787 | 32.4725 | 27.4175 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | 11.1636 | 11.1636 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.2891 | 5.1997 | 6.0267 | 5.2473 | 6.6779 | 5.6737 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7776.2896 | 6187.1296 | 7055.8704 | 6165.9408 | 7755.1008 | 6547.3392 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7649.1568 | 6165.9408 | 6928.7376 | 6187.1296 | 7606.7792 | 6441.3952 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6949.9264 | 5678.5984 | 6293.0736 | 5699.7872 | 6928.7376 | 6038.808 |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9407.8272 | 7776.2896 | 8772.1632 | 7797.4784 | 9746.848 | 8221.2544 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | 3347.8304 | 3347.8304 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1885.8032 | 1567.9712 | 1801.048 | 1567.9712 | 2012.936 | 1695.104 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
GA_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | n/a | VFD |  |  |  |  | 2015-03-31
GA_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
GA_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
GA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2015-03-31
GA_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7781.4809 | 6181.2391 | 7053.0523 | 6159.6901 | 7756.1179 | 6552.0643 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7654.2633 | 6174.5858 | 6933.7382 | 6177.976 | 7612.3942 | 6437.0939 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 5676.5855 | 6287.3314 | 5691.2269 | 6777.6191 | 6045.9698 |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
GA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
GA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
GA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | No | No |  |  |  |  | 2015-03-31
GA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
GA_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
GA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.3078 | 1.1956 | 1.2749 | 1.2208 | 1.3748 | 1.2693 |  |  |  |  | 2015-03-31
GA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 131.4906 | 120.2096 | 128.1786 | 122.7405 | 138.2221 | 127.6239 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.393 | 9.1192 | 10.3265 | 9.0874 | 11.3559 | 9.6662 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.2068 | 9.1094 | 10.1519 | 9.1144 | 11.1455 | 9.4966 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.1693 | 8.3746 | 9.2757 | 8.3963 | 10.1317 | 8.9196 |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.7894 | 11.393 | 12.8479 | 11.414 | 14.2671 | 12.0461 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | 2.2687 | 2.2687 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3224 | 1.0934 | 1.2673 | 1.1034 | 1.4042 | 1.193 |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
GA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8422 | 2.5984 | 2.7707 | 2.6531 | 2.9878 | 2.7587 |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
GA_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
GA_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
GA_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
GA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.4582 | 96.642 | 96.6208 | 94.6858 | 100.0373 | 95.1256 |  |  |  |  | 2015-03-31
GA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2813 | 2.09 | 2.0624 | 1.9847 | 2.029 | 1.8908 |  |  |  |  | 2015-03-31
GA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.7322 | 5.2366 | 5.5534 | 5.3405 | 5.367 | 5.1777 |  |  |  |  | 2015-03-31
GA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6365 | 2.4458 | 2.627 | 2.5009 | 2.5648 | 2.3871 |  |  |  |  | 2015-03-31
GA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5584 | 4.4875 | 4.3712 | 4.3349 | 4.3807 | 4.355 |  |  |  |  | 2015-03-31
GA_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 720.4192 | 635.664 | 678.0416 | 656.8528 | 656.8528 | 593.2864 |  |  |  |  | 2015-03-31
GA_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1716.2928 | 1567.9712 | 1673.9152 | 1610.3488 | 1610.3488 | 1546.7824 |  |  |  |  | 2015-03-31
GA_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 741.608 | 762.7968 | 720.4192 |  |  |  |  | 2015-03-31
GA_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | 1546.7824 | 1525.5936 | 1525.5936 | 1504.4048 |  |  |  |  | 2015-03-31
GA_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
GA_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
GA_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
GA_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
GA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
GA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy |  |  |  |  | 2015-03-31
GA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | No | No | No | No | No |  |  |  |  | 2015-03-31
GA_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.2053 | 1.1011 | 1.1677 | 1.123 | 1.1285 | 1.0887 |  |  |  |  | 2015-03-31
GA_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0558 | 1.0472 | 1.0798 | 1.0677 | 1.0637 | 1.0522 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72592 | 0.67621 | 0.6301 | 0.60647 | 0.62076 | 0.6139 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.72293 | 0.67347 | 0.62681 | 0.60386 | 0.61643 | 0.60982 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.94068 | 0.80506 | 0.77009 | 0.72886 | 0.77313 | 0.77443 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.1137 | 0.96751 | 0.92505 | 0.87661 | 0.94536 | 0.94076 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.76648 | 0.667 | 0.63413 | 0.60617 | 0.63281 | 0.62692 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.77797 | 0.66663 | 0.63332 | 0.6067 | 0.63028 | 0.62458 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.1342 | 0.97607 | 0.93981 | 0.88983 | 0.9693 | 0.96252 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.758 | 1.6448 | 1.5797 | 1.5234 | 1.6137 | 1.5868 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7534 | 1.6405 | 1.5745 | 1.5193 | 1.6066 | 1.5802 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2642 | 1.9917 | 1.9548 | 1.8467 | 2.0463 | 2.0291 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6318 | 2.3219 | 2.2838 | 2.1599 | 2.4163 | 2.3846 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.856 | 1.6387 | 1.6049 | 1.5445 | 1.6682 | 1.6352 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8601 | 1.6346 | 1.6003 | 1.5409 | 1.6617 | 1.696 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.385 | 2.0798 | 2.0707 | 1.9671 | 2.1912 | 2.1693 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.6677 | 2.3363 | 2.3203 | 2.1845 | 2.4688 | 2.4309 |  |  |  |  | 2015-03-31
GA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2861 | 2.1423 | 2.0806 | 2.0345 | 2.0751 | 2.0807 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1102 | 1.0218 | 1.0155 | 0.95239 | 1.1357 | 1.0101 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1047 | 1.0167 | 1.0098 | 0.94779 | 1.1382 | 1.0028 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3693 | 1.243 | 1.2232 | 1.1286 | 1.3941 | 1.2555 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6211 | 1.4152 | 1.4251 | 1.3178 | 1.5856 | 1.4754 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.24 | 1.1024 | 1.1293 | 1.0428 | 1.2717 | 1.1418 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2424 | 1.1048 | 1.1318 | 1.0451 | 1.2748 | 1.145 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5091 | 1.3375 | 1.3686 | 1.2629 | 1.536 | 1.4045 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6638 | 1.4472 | 1.4743 | 1.3527 | 1.6481 | 1.5218 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
GA_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 211.888 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 190.6992 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 254.2656 | 275.4544 | 254.2656 | 275.4544 | 275.4544 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 339.0208 | 339.0208 | 317.832 | 339.0208 | 339.0208 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 190.6992 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 211.888 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 339.0208 | 339.0208 | 317.832 | 360.2096 | 360.2096 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 572.0976 | 550.9088 | 593.2864 | 572.0976 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 572.0976 | 550.9088 | 572.0976 | 572.0976 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 678.0416 | 720.4192 | 678.0416 | 762.7968 | 741.608 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 826.3632 | 868.7408 | 826.3632 | 932.3072 | 911.1184 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 572.0976 | 550.9088 | 593.2864 | 572.0976 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 529.72 | 572.0976 | 550.9088 | 593.2864 | 572.0976 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 699.2304 | 762.7968 | 720.4192 | 805.1744 | 805.1744 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 974.6848 | 826.3632 | 889.9296 | 826.3632 | 953.496 | 932.3072 |  |  |  |  | 2015-03-31
GA_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 889.9296 | 911.1184 | 889.9296 | 911.1184 | 911.1184 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 381.3984 | 360.2096 | 423.776 | 381.3984 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | 381.3984 | 360.2096 | 423.776 | 381.3984 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 423.776 | 466.1536 | 423.776 | 529.72 | 487.3424 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 508.5312 | 572.0976 | 508.5312 | 635.664 | 593.2864 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 381.3984 | 423.776 | 381.3984 | 487.3424 | 423.776 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 381.3984 | 423.776 | 381.3984 | 487.3424 | 423.776 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 466.1536 | 529.72 | 466.1536 | 593.2864 | 529.72 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 529.72 | 572.0976 | 529.72 | 656.8528 | 593.2864 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.1632 | 0.14846 | 0.15104 | 0.14321 | 0.1469 | 0.14463 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.16226 | 0.14759 | 0.14995 | 0.14236 | 0.14549 | 0.1433 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.22937 | 0.18391 | 0.19126 | 0.17748 | 0.18943 | 0.1899 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.2808 | 0.23438 | 0.24264 | 0.22638 | 0.24633 | 0.2448 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16535 | 0.14357 | 0.14955 | 0.14134 | 0.14746 | 0.14444 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16941 | 0.14573 | 0.15143 | 0.14365 | 0.14908 | 0.14608 |  |  |  |  | 2015-03-31
GA_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.28167 | 0.23296 | 0.24585 | 0.2291 | 0.25245 | 0.25021 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.41683 | 0.38318 | 0.40434 | 0.38544 | 0.41387 | 0.40488 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.41535 | 0.3818 | 0.40262 | 0.38408 | 0.41151 | 0.40267 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.57453 | 0.47904 | 0.5135 | 0.47726 | 0.53868 | 0.53298 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.68321 | 0.58465 | 0.62286 | 0.58109 | 0.66127 | 0.65064 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.42681 | 0.37675 | 0.40626 | 0.38611 | 0.4214 | 0.41049 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.42811 | 0.37547 | 0.40472 | 0.38491 | 0.41928 | 0.40904 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.60353 | 0.50243 | 0.54525 | 0.50846 | 0.57602 | 0.56881 |  |  |  |  | 2015-03-31
GA_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.68753 | 0.58514 | 0.63335 | 0.58988 | 0.67928 | 0.6666 |  |  |  |  | 2015-03-31
GA_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67921 | 0.62897 | 0.65006 | 0.63339 | 0.64236 | 0.64436 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.2792 | 0.2505 | 0.27193 | 0.25065 | 0.29874 | 0.26704 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27744 | 0.24889 | 0.27001 | 0.24914 | 0.29859 | 0.26461 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.35398 | 0.3015 | 0.33098 | 0.29934 | 0.3742 | 0.34018 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.4328 | 0.3674 | 0.40139 | 0.36516 | 0.45062 | 0.41506 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.30862 | 0.26495 | 0.29863 | 0.2701 | 0.34047 | 0.29791 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.3094 | 0.26564 | 0.29948 | 0.27086 | 0.3415 | 0.29897 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.38675 | 0.33134 | 0.37038 | 0.33546 | 0.42073 | 0.37758 |  |  |  |  | 2015-03-31
GA_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.44259 | 0.3739 | 0.41302 | 0.37451 | 0.46696 | 0.42758 |  |  |  |  | 2015-03-31
LA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.892 | 1.8469 | 1.8808 | 1.8285 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9847 | 1.8297 | 1.9234 | 1.8453 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5298 | 1.2936 | 1.3818 | 1.2807 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.9177 | 1.793 | 1.8729 | 1.8144 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7721 | 1.5054 | 1.637 | 1.5243 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 656.8528 | 720.4192 | 678.0416 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 656.8528 | 529.72 | 593.2864 | 529.72 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 699.2304 | 656.8528 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 762.7968 | 614.4752 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44561 | 0.42985 | 0.45369 | 0.43559 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52462 | 0.47024 | 0.51078 | 0.48321 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.47023 | 0.3794 | 0.42113 | 0.38119 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.50064 | 0.45815 | 0.49295 | 0.47231 | [6 empty] | 2015-03-31
LA_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.53598 | 0.43877 | 0.49352 | 0.45234 | [6 empty] | 2015-03-31
LA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10615.5888 | 10255.3792 | 10594.4 | 10213.0016 | [6 empty] | 2015-03-31
LA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24960.4064 | 23413.624 | 24473.064 | 23561.9456 | [6 empty] | 2015-03-31
LA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 200827.4467 | 185507.9443 | 196441.3651 | 186927.5939 | [6 empty] | 2015-03-31
LA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22184.6736 | 19896.2832 | 21845.6528 | 20298.8704 | [6 empty] | 2015-03-31
LA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2015-03-31
LA_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
LA_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
LA_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
LA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
LA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
LA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
LA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
LA_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
LA_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
LA_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
LA_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
LA_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | No | No | [6 empty] | 2015-03-31
LA_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
LA_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
LA_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
LA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
LA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
LA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
LA_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
LA_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
LA_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
LA_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 434.5863 | 418.6343 | 413.335 | 401.5727 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 434.5863 | 418.6343 | 413.335 | 401.5727 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
LA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 412.4804 | 397.3435 | 392.3155 | 381.1481 | [6 empty] | 2015-03-31
LA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 412.4804 | 397.3435 | 392.3155 | 381.1481 | [6 empty] | 2015-03-31
LA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.0314 | 3.8766 | 3.9922 | 4.0171 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 2046.4352 | 985.6619 | 1946.4197 | 945.4908 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 985.6619 | 0 | 945.4908 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 2046.4352 | 1971.3047 | 1946.4197 | 1890.9436 | [6 empty] | 2015-03-31
LA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 810.6632 | 779.5205 | 802.7761 | 807.7864 | [6 empty] | 2015-03-31
LA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2387.6927 | 2291.3227 | 2270.8758 | 2197.9643 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
LA_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.3905 | 11.0026 | 11.3653 | 10.9677 | [6 empty] | 2015-03-31
LA_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.8748 | 31.8502 | 35.1743 | 32.055 | [6 empty] | 2015-03-31
LA_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 282.4322 | 246.8477 | 276.2547 | 262.8773 | [6 empty] | 2015-03-31
LA_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 31.8865 | 27.2162 | 31.3977 | 27.755 | [6 empty] | 2015-03-31
LA_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.8595 | 42.7803 | 43.1193 | 43.0383 | [6 empty] | 2015-03-31
LA_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.76633 | 0.75958 | 0.77162 | 0.76568 | [6 empty] | 2015-03-31
LA_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.4648 | 9.3674 | 9.5449 | 9.4519 | [6 empty] | 2015-03-31
LA_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.62712 | 0.61362 | 0.64655 | 0.62079 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 11.0398 | 5.3173 | 10.5 | 5.1006 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.3173 | 0 | 5.1006 | [6 empty] | 2015-03-31
LA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 33.1195 | 31.9038 | 31.4999 | 30.6035 | [6 empty] | 2015-03-31
LA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.5229 | 16.8498 | 17.3525 | 17.4608 | [6 empty] | 2015-03-31
LA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 44.2237 | 42.4383 | 42.0612 | 40.7087 | [6 empty] | 2015-03-31
LA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8378 | 3.8238 | 3.8394 | 3.815 | [6 empty] | 2015-03-31
LA_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
LA_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
LA_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | NO | YES | [6 empty] | 2015-03-31
LA_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
LA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4588.6292 | 4298.1093 | 4269.877 | 4328.0561 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.4888 | 9.4242 | 9.2818 | 9.2255 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 41.8626 | 38.5713 | 40.1338 | 38.8643 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4023 | 5.4305 | 6.2834 | 5.3052 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5973 | 5.0866 | 5.4357 | 5.1295 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3305.4528 | 3432.5856 | 3390.208 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12564.9584 | 11569.0848 | 12755.6576 | 11908.1056 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2309.5792 | 2055.3136 | 2267.2016 | 2097.6912 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1906.992 | 1631.5376 | 1843.4256 | 1695.104 | [6 empty] | 2015-03-31
LA_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
LA_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
LA_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.3227 | 2.0864 | 2.4193 | 1.5496 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2729 | 2.2453 | 2.3233 | 2.2986 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.4814 | 12.4215 | 13.6801 | 12.7813 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.612 | 1.4442 | 1.5878 | 1.4723 | [6 empty] | 2015-03-31
LA_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.3306 | 1.1503 | 1.2965 | 1.1926 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.3102 | 20.1189 | 23.7652 | 20.8112 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.8961 | 20.102 | 23.4618 | 20.8373 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.5422 | 18.4601 | 21.1287 | 19.0748 | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 30.8649 | 25.5575 | 29.4876 | 26.3476 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.2184 | 5.22 | 6.0812 | 5.3098 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7585.5904 | 6038.808 | 7140.6256 | 6250.696 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7479.6464 | 6038.808 | 7034.6816 | 6250.696 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6759.2272 | 5530.2768 | 6335.4512 | 5720.976 | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9259.5056 | 7670.3456 | 8856.9184 | 7903.4224 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1864.6144 | 1567.9712 | 1822.2368 | 1589.16 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
LA_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | [6 empty] | 2015-03-31
LA_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
LA_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
LA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2015-03-31
LA_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
LA_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
LA_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
LA_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
LA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7595.1889 | 6037.3672 | 7131.5356 | 6245.1234 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7470.8954 | 6032.2819 | 7040.5085 | 6252.9632 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6764.5456 | 5539.5575 | 6340.367 | 5724.0272 | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
LA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
LA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
LA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
LA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
LA_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
LA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2913 | 1.1856 | 1.2783 | 1.2248 | [6 empty] | 2015-03-31
LA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 129.8359 | 119.2043 | 128.5269 | 123.1445 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.1203 | 8.9069 | 10.4415 | 9.2134 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.9383 | 8.8994 | 10.3082 | 9.225 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.9041 | 8.1725 | 9.354 | 8.4447 | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.5608 | 11.2289 | 12.9557 | 11.5761 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3076 | 1.0976 | 1.2787 | 1.1165 | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
LA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8065 | 2.5767 | 2.7782 | 2.6618 | [6 empty] | 2015-03-31
LA_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
LA_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
LA_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
LA_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
LA_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
LA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 101.835 | 96.4393 | 98.6589 | 96.5648 | [6 empty] | 2015-03-31
LA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2031 | 2.0329 | 2.1351 | 2.0661 | [6 empty] | 2015-03-31
LA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.6663 | 5.1833 | 5.4901 | 5.3033 | [6 empty] | 2015-03-31
LA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6159 | 2.4283 | 2.586 | 2.4619 | [6 empty] | 2015-03-31
LA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.4984 | 4.4441 | 4.5332 | 4.4997 | [6 empty] | 2015-03-31
LA_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 614.4752 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
LA_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1695.104 | 1546.7824 | 1652.7264 | 1589.16 | [6 empty] | 2015-03-31
LA_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 783.9856 | 741.608 | [6 empty] | 2015-03-31
LA_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1483.216 | 1462.0272 | 1504.4048 | 1483.216 | [6 empty] | 2015-03-31
LA_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
LA_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
LA_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
LA_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
LA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
LA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
LA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
LA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
LA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | DifferentialEnthalpy | No | [6 empty] | 2015-03-31
LA_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1915 | 1.0899 | 1.1544 | 1.1151 | [6 empty] | 2015-03-31
LA_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0547 | 1.0376 | 1.0524 | 1.0539 | [6 empty] | 2015-03-31
LA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72326 | 0.67372 | 0.68134 | 0.65802 | [6 empty] | 2015-03-31
LA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.72022 | 0.6709 | 0.67761 | 0.65499 | [6 empty] | 2015-03-31
LA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.91826 | 0.78498 | 0.80778 | 0.77827 | [6 empty] | 2015-03-31
LA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.1012 | 0.94891 | 1.0071 | 0.95774 | [6 empty] | 2015-03-31
LA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.71146 | 0.63824 | 0.66065 | 0.63354 | [6 empty] | 2015-03-31
LA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73077 | 0.64786 | 0.65895 | 0.63359 | [6 empty] | 2015-03-31
LA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.1054 | 0.94682 | 1.0043 | 0.9504 | [6 empty] | 2015-03-31
LA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7483 | 1.6352 | 1.6966 | 1.6415 | [6 empty] | 2015-03-31
LA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7436 | 1.6307 | 1.6904 | 1.6365 | [6 empty] | 2015-03-31
LA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2169 | 1.9397 | 2.0334 | 1.9566 | [6 empty] | 2015-03-31
LA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6029 | 2.2828 | 2.4647 | 2.3381 | [6 empty] | 2015-03-31
LA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7532 | 1.5884 | 1.6609 | 1.606 | [6 empty] | 2015-03-31
LA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7572 | 1.584 | 1.655 | 1.6012 | [6 empty] | 2015-03-31
LA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2728 | 1.9897 | 2.1242 | 2.0167 | [6 empty] | 2015-03-31
LA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5967 | 2.2659 | 2.4511 | 2.3221 | [6 empty] | 2015-03-31
LA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.289 | 2.148 | 2.1642 | 2.1154 | [6 empty] | 2015-03-31
LA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0865 | 1.0019 | 1.0934 | 1.0288 | [6 empty] | 2015-03-31
LA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0841 | 0.99667 | 1.0865 | 1.0232 | [6 empty] | 2015-03-31
LA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3336 | 1.2126 | 1.3419 | 1.2419 | [6 empty] | 2015-03-31
LA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6014 | 1.3898 | 1.5461 | 1.4279 | [6 empty] | 2015-03-31
LA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.1784 | 1.0535 | 1.1838 | 1.0955 | [6 empty] | 2015-03-31
LA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1789 | 1.0554 | 1.186 | 1.0974 | [6 empty] | 2015-03-31
LA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.4334 | 1.2736 | 1.4273 | 1.3198 | [6 empty] | 2015-03-31
LA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6123 | 1.404 | 1.5632 | 1.4437 | [6 empty] | 2015-03-31
LA_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
LA_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
LA_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
LA_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
LA_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
LA_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
LA_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
LA_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
LA_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
LA_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
LA_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
LA_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
LA_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
LA_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
LA_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 254.2656 | 275.4544 | 254.2656 | [6 empty] | 2015-03-31
LA_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 317.832 | 360.2096 | 339.0208 | [6 empty] | 2015-03-31
LA_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
LA_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
LA_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 317.832 | 360.2096 | 317.832 | [6 empty] | 2015-03-31
LA_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
LA_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
LA_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 656.8528 | 720.4192 | 678.0416 | [6 empty] | 2015-03-31
LA_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 805.1744 | 911.1184 | 847.552 | [6 empty] | 2015-03-31
LA_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
LA_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
LA_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 678.0416 | 741.608 | 699.2304 | [6 empty] | 2015-03-31
LA_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 783.9856 | 889.9296 | 847.552 | [6 empty] | 2015-03-31
LA_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 889.9296 | 911.1184 | 889.9296 | [6 empty] | 2015-03-31
LA_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
LA_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
LA_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 402.5872 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
LA_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 508.5312 | 593.2864 | 529.72 | [6 empty] | 2015-03-31
LA_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 423.776 | 381.3984 | [6 empty] | 2015-03-31
LA_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 423.776 | 381.3984 | [6 empty] | 2015-03-31
LA_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 508.5312 | 466.1536 | [6 empty] | 2015-03-31
LA_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 508.5312 | 593.2864 | 529.72 | [6 empty] | 2015-03-31
LA_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
LA_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15863 | 0.14391 | 0.1558 | 0.14834 | [6 empty] | 2015-03-31
LA_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15768 | 0.14302 | 0.15461 | 0.14738 | [6 empty] | 2015-03-31
LA_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.22363 | 0.1787 | 0.19287 | 0.18129 | [6 empty] | 2015-03-31
LA_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.27427 | 0.22677 | 0.25344 | 0.23747 | [6 empty] | 2015-03-31
LA_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15135 | 0.13578 | 0.14686 | 0.13963 | [6 empty] | 2015-03-31
LA_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15546 | 0.13809 | 0.14891 | 0.14216 | [6 empty] | 2015-03-31
LA_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.27121 | 0.22189 | 0.24805 | 0.23192 | [6 empty] | 2015-03-31
LA_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40919 | 0.37502 | 0.41243 | 0.39464 | [6 empty] | 2015-03-31
LA_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40767 | 0.3736 | 0.41045 | 0.39303 | [6 empty] | 2015-03-31
LA_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.56111 | 0.46708 | 0.51487 | 0.48439 | [6 empty] | 2015-03-31
LA_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.66932 | 0.56937 | 0.64572 | 0.60456 | [6 empty] | 2015-03-31
LA_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.39528 | 0.35843 | 0.39552 | 0.37794 | [6 empty] | 2015-03-31
LA_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.39655 | 0.35705 | 0.39364 | 0.37645 | [6 empty] | 2015-03-31
LA_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.57266 | 0.47706 | 0.53068 | 0.49614 | [6 empty] | 2015-03-31
LA_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.66328 | 0.55993 | 0.63607 | 0.59442 | [6 empty] | 2015-03-31
LA_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67868 | 0.62923 | 0.64724 | 0.63023 | [6 empty] | 2015-03-31
LA_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.27105 | 0.24344 | 0.28034 | 0.25935 | [6 empty] | 2015-03-31
LA_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.26924 | 0.24175 | 0.27811 | 0.25756 | [6 empty] | 2015-03-31
LA_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.34403 | 0.29288 | 0.33914 | 0.30763 | [6 empty] | 2015-03-31
LA_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.42508 | 0.35836 | 0.41793 | 0.38106 | [6 empty] | 2015-03-31
LA_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.28973 | 0.24989 | 0.29545 | 0.26757 | [6 empty] | 2015-03-31
LA_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.29048 | 0.25044 | 0.29614 | 0.26818 | [6 empty] | 2015-03-31
LA_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.36411 | 0.31293 | 0.36615 | 0.33217 | [6 empty] | 2015-03-31
LA_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.42742 | 0.3597 | 0.41872 | 0.38019 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8611 | 1.816 | 1.8778 | 1.8258 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9512 | 1.7955 | 1.8916 | 1.8186 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4619 | 1.2383 | 1.3237 | 1.2263 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8745 | 1.7558 | 1.8338 | 1.7746 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7511 | 1.4858 | 1.5902 | 1.4844 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 656.8528 | 699.2304 | 678.0416 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 508.5312 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 635.664 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 762.7968 | 614.4752 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44673 | 0.43087 | 0.44985 | 0.43166 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52349 | 0.46942 | 0.49957 | 0.47346 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.45437 | 0.36765 | 0.4016 | 0.3628 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.49689 | 0.45516 | 0.48005 | 0.45891 | [6 empty] | 2015-03-31
MS_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.53621 | 0.4388 | 0.47604 | 0.43593 | [6 empty] | 2015-03-31
MS_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10657.9664 | 10297.7568 | 10594.4 | 10213.0016 | [6 empty] | 2015-03-31
MS_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24960.4064 | 23434.8128 | 24261.176 | 23371.2464 | [6 empty] | 2015-03-31
MS_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 200212.9715 | 185211.3011 | 193962.2755 | 184427.3155 | [6 empty] | 2015-03-31
MS_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22121.1072 | 19853.9056 | 21506.632 | 19981.0384 | [6 empty] | 2015-03-31
MS_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2015-03-31
MS_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
MS_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
MS_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
MS_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
MS_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
MS_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
MS_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
MS_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
MS_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
MS_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
MS_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
MS_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MS_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MS_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MS_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MS_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MS_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MS_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MS_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MS_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MS_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MS_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 423.1537 | 407.6999 | 417.0657 | 405.3895 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 423.1537 | 407.6999 | 417.0657 | 405.3895 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
MS_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 401.6305 | 386.9699 | 395.8616 | 384.7735 | [6 empty] | 2015-03-31
MS_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 401.6305 | 386.9699 | 395.8616 | 384.7735 | [6 empty] | 2015-03-31
MS_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.0895 | 3.9249 | 4.0753 | 4.0966 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1992.5441 | 959.9162 | 1964.0135 | 954.4763 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 959.9162 | 0 | 954.4763 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1992.5441 | 1919.7911 | 1964.0135 | 1909.0129 | [6 empty] | 2015-03-31
MS_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 822.3401 | 789.232 | 819.476 | 823.7587 | [6 empty] | 2015-03-31
MS_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2324.9254 | 2231.4085 | 2291.4812 | 2218.7282 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MS_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.4478 | 11.057 | 11.3708 | 10.9713 | [6 empty] | 2015-03-31
MS_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.8783 | 31.8866 | 34.8797 | 31.7803 | [6 empty] | 2015-03-31
MS_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 281.5583 | 246.4492 | 272.7669 | 259.3526 | [6 empty] | 2015-03-31
MS_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 31.7992 | 27.154 | 30.922 | 27.3188 | [6 empty] | 2015-03-31
MS_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.0921 | 43.0123 | 43.2 | 43.1191 | [6 empty] | 2015-03-31
MS_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.76985 | 0.76303 | 0.77134 | 0.76536 | [6 empty] | 2015-03-31
MS_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.5034 | 9.4044 | 9.5272 | 9.4332 | [6 empty] | 2015-03-31
MS_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.62976 | 0.61615 | 0.6415 | 0.61789 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.7494 | 5.1784 | 10.5947 | 5.1491 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.1784 | 0 | 5.1491 | [6 empty] | 2015-03-31
MS_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.2482 | 31.0705 | 31.7842 | 30.8944 | [6 empty] | 2015-03-31
MS_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.7754 | 17.0597 | 17.7135 | 17.806 | [6 empty] | 2015-03-31
MS_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.0604 | 41.3298 | 42.4408 | 41.0956 | [6 empty] | 2015-03-31
MS_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8356 | 3.8215 | 3.8452 | 3.8205 | [6 empty] | 2015-03-31
MS_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
MS_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
MS_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
MS_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
MS_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4662.9491 | 4364.0259 | 4285.3236 | 4345.9835 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.3754 | 9.2997 | 9.2829 | 9.226 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 41.4705 | 38.6657 | 40.7731 | 38.9924 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3 | 5.3632 | 6.1965 | 5.3074 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4878 | 4.9742 | 5.3552 | 5.0558 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3305.4528 | 3326.6416 | 3305.4528 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12670.9024 | 11611.4624 | 12713.28 | 11696.2176 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2309.5792 | 2076.5024 | 2224.824 | 2076.5024 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1906.992 | 1652.7264 | 1822.2368 | 1673.9152 | [6 empty] | 2015-03-31
MS_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MS_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MS_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.3696 | 2.0522 | 2.5212 | 1.6312 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.268 | 2.236 | 2.257 | 2.2325 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.5949 | 12.4519 | 13.6534 | 12.5571 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6188 | 1.4563 | 1.5657 | 1.4573 | [6 empty] | 2015-03-31
MS_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.3319 | 1.1509 | 1.2722 | 1.1664 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.2089 | 20.0436 | 23.0465 | 20.2692 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.7936 | 20.0167 | 22.7027 | 20.2643 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.4523 | 18.3866 | 20.5214 | 18.6008 | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 30.6489 | 25.4431 | 28.7418 | 25.6174 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.0572 | 5.1586 | 5.7954 | 5.1838 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7564.4016 | 6017.6192 | 6907.5488 | 6081.1856 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7437.2688 | 5996.4304 | 6822.7936 | 6081.1856 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6738.0384 | 5509.088 | 6165.9408 | 5572.6544 | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9195.9392 | 7627.968 | 8623.8416 | 7691.5344 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1822.2368 | 1546.7824 | 1737.4816 | 1546.7824 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
MS_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | [6 empty] | 2015-03-31
MS_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MS_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MS_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | No | No | [6 empty] | 2015-03-31
MS_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
MS_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
MS_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
MS_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
MS_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7564.7618 | 6014.7375 | 6915.876 | 6082.4357 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7440.1293 | 6006.6858 | 6812.7077 | 6080.9949 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6737.5723 | 5517.5212 | 6158.1221 | 5581.7868 | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MS_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MS_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MS_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MS_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MS_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MS_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2907 | 1.1837 | 1.2803 | 1.229 | [6 empty] | 2015-03-31
MS_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 129.772 | 119.0107 | 128.7273 | 123.5634 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.0758 | 8.8736 | 10.1257 | 8.9734 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.8933 | 8.8617 | 9.9746 | 8.9713 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.8647 | 8.14 | 9.0851 | 8.2348 | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.4659 | 11.1787 | 12.628 | 11.2553 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2737 | 1.0847 | 1.2186 | 1.09 | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
MS_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8051 | 2.5725 | 2.7825 | 2.6709 | [6 empty] | 2015-03-31
MS_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MS_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MS_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MS_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MS_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MS_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 101.5172 | 96.0212 | 98.1184 | 96.2601 | [6 empty] | 2015-03-31
MS_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1796 | 2.0087 | 2.1125 | 2.036 | [6 empty] | 2015-03-31
MS_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.6567 | 5.1838 | 5.4006 | 5.2101 | [6 empty] | 2015-03-31
MS_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6207 | 2.4351 | 2.5627 | 2.4385 | [6 empty] | 2015-03-31
MS_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.4511 | 4.3944 | 4.5004 | 4.4617 | [6 empty] | 2015-03-31
MS_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 614.4752 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
MS_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1695.104 | 1546.7824 | 1610.3488 | 1567.9712 | [6 empty] | 2015-03-31
MS_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 762.7968 | 741.608 | [6 empty] | 2015-03-31
MS_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1462.0272 | 1504.4048 | 1483.216 | [6 empty] | 2015-03-31
MS_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
MS_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
MS_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
MS_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
MS_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MS_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MS_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
MS_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MS_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MS_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1894 | 1.09 | 1.1356 | 1.0955 | [6 empty] | 2015-03-31
MS_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0488 | 1.0434 | 1.0498 | 1.0511 | [6 empty] | 2015-03-31
MS_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.70051 | 0.65199 | 0.66494 | 0.63739 | [6 empty] | 2015-03-31
MS_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69735 | 0.64909 | 0.65731 | 0.6346 | [6 empty] | 2015-03-31
MS_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.87085 | 0.74803 | 0.76977 | 0.75064 | [6 empty] | 2015-03-31
MS_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0712 | 0.92176 | 0.95612 | 0.90821 | [6 empty] | 2015-03-31
MS_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.70908 | 0.62933 | 0.65023 | 0.62665 | [6 empty] | 2015-03-31
MS_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.72203 | 0.62717 | 0.64751 | 0.62179 | [6 empty] | 2015-03-31
MS_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0846 | 0.92833 | 0.96678 | 0.91685 | [6 empty] | 2015-03-31
MS_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7017 | 1.5987 | 1.6534 | 1.5977 | [6 empty] | 2015-03-31
MS_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6966 | 1.5939 | 1.6477 | 1.5931 | [6 empty] | 2015-03-31
MS_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0999 | 1.8821 | 1.977 | 1.8932 | [6 empty] | 2015-03-31
MS_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.5415 | 2.2278 | 2.3515 | 2.2282 | [6 empty] | 2015-03-31
MS_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7294 | 1.5504 | 1.6303 | 1.5744 | [6 empty] | 2015-03-31
MS_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.733 | 1.5457 | 1.6247 | 1.5699 | [6 empty] | 2015-03-31
MS_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.1887 | 1.9203 | 2.1093 | 2.0106 | [6 empty] | 2015-03-31
MS_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5565 | 2.2293 | 2.3668 | 2.2394 | [6 empty] | 2015-03-31
MS_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2485 | 2.0543 | 2.1395 | 2.0913 | [6 empty] | 2015-03-31
MS_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0563 | 0.96996 | 1.0449 | 0.9849 | [6 empty] | 2015-03-31
MS_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0504 | 0.96449 | 1.0384 | 0.97955 | [6 empty] | 2015-03-31
MS_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2657 | 1.1733 | 1.289 | 1.1918 | [6 empty] | 2015-03-31
MS_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5643 | 1.3615 | 1.4786 | 1.3643 | [6 empty] | 2015-03-31
MS_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.16 | 1.0372 | 1.1562 | 1.0704 | [6 empty] | 2015-03-31
MS_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1621 | 1.0372 | 1.1582 | 1.0722 | [6 empty] | 2015-03-31
MS_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3993 | 1.2436 | 1.3828 | 1.2783 | [6 empty] | 2015-03-31
MS_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.5865 | 1.3769 | 1.5144 | 1.3981 | [6 empty] | 2015-03-31
MS_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MS_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
MS_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MS_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MS_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MS_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MS_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MS_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MS_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MS_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MS_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
MS_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MS_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
MS_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
MS_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 233.0768 | 254.2656 | 233.0768 | [6 empty] | 2015-03-31
MS_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 317.832 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
MS_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
MS_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
MS_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 317.832 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
MS_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
MS_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
MS_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 635.664 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
MS_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 783.9856 | 847.552 | 805.1744 | [6 empty] | 2015-03-31
MS_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 508.5312 | 550.9088 | 508.5312 | [6 empty] | 2015-03-31
MS_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 508.5312 | 529.72 | 508.5312 | [6 empty] | 2015-03-31
MS_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 656.8528 | 720.4192 | 678.0416 | [6 empty] | 2015-03-31
MS_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 783.9856 | 847.552 | 805.1744 | [6 empty] | 2015-03-31
MS_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 868.7408 | 911.1184 | 868.7408 | [6 empty] | 2015-03-31
MS_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 381.3984 | 339.0208 | [6 empty] | 2015-03-31
MS_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 360.2096 | 339.0208 | [6 empty] | 2015-03-31
MS_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 402.5872 | 444.9648 | 402.5872 | [6 empty] | 2015-03-31
MS_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 508.5312 | 550.9088 | 508.5312 | [6 empty] | 2015-03-31
MS_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
MS_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
MS_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
MS_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 508.5312 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
MS_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MS_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15595 | 0.14138 | 0.14633 | 0.13884 | [6 empty] | 2015-03-31
MS_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15494 | 0.14047 | 0.14523 | 0.13795 | [6 empty] | 2015-03-31
MS_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.21434 | 0.1715 | 0.18019 | 0.1696 | [6 empty] | 2015-03-31
MS_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.27018 | 0.22234 | 0.23507 | 0.21949 | [6 empty] | 2015-03-31
MS_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15231 | 0.13387 | 0.14082 | 0.13335 | [6 empty] | 2015-03-31
MS_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15646 | 0.1359 | 0.14238 | 0.1354 | [6 empty] | 2015-03-31
MS_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.26929 | 0.21951 | 0.23401 | 0.21789 | [6 empty] | 2015-03-31
MS_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40421 | 0.37063 | 0.39279 | 0.37472 | [6 empty] | 2015-03-31
MS_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40255 | 0.3691 | 0.39093 | 0.37323 | [6 empty] | 2015-03-31
MS_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.53941 | 0.4519 | 0.48548 | 0.45825 | [6 empty] | 2015-03-31
MS_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.66158 | 0.56095 | 0.6055 | 0.56517 | [6 empty] | 2015-03-31
MS_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.39873 | 0.35577 | 0.38325 | 0.36519 | [6 empty] | 2015-03-31
MS_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.39991 | 0.35426 | 0.38143 | 0.36373 | [6 empty] | 2015-03-31
MS_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.55643 | 0.46509 | 0.50862 | 0.47586 | [6 empty] | 2015-03-31
MS_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.6604 | 0.55571 | 0.60553 | 0.56407 | [6 empty] | 2015-03-31
MS_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67515 | 0.60886 | 0.63982 | 0.62277 | [6 empty] | 2015-03-31
MS_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.26575 | 0.23841 | 0.26398 | 0.24429 | [6 empty] | 2015-03-31
MS_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.26385 | 0.23664 | 0.26185 | 0.24256 | [6 empty] | 2015-03-31
MS_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.32969 | 0.28617 | 0.32266 | 0.29169 | [6 empty] | 2015-03-31
MS_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.41987 | 0.35333 | 0.39343 | 0.35736 | [6 empty] | 2015-03-31
MS_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.29036 | 0.25017 | 0.28713 | 0.2597 | [6 empty] | 2015-03-31
MS_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.29104 | 0.2507 | 0.2878 | 0.26029 | [6 empty] | 2015-03-31
MS_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.36029 | 0.30935 | 0.35356 | 0.32003 | [6 empty] | 2015-03-31
MS_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.42472 | 0.3573 | 0.40235 | 0.3645 | [6 empty] | 2015-03-31
TX_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8836 | 1.8385 | 1.8558 | 1.8105 | 1.8673 | 1.8141 | 1.6572 | 1.59 | 1.5876 | 1.4524 | 2015-03-31
TX_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0185 | 1.8567 | 2.1042 | 1.9273 | 1.9788 | 1.9002 | 1.9201 | 1.8051 | 1.8131 | 1.6179 | 2015-03-31
TX_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5462 | 1.3054 | 1.6092 | 1.3244 | 1.4305 | 1.3183 | 1.458 | 1.3239 | 1.6608 | 1.5601 | 2015-03-31
TX_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.955 | 1.8262 | 1.9394 | 1.8081 | 1.9146 | 1.8558 | 1.8472 | 1.7669 | 1.7281 | 1.5548 | 2015-03-31
TX_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.8225 | 1.542 | 1.928 | 1.5956 | 1.685 | 1.5676 | 1.7291 | 1.5879 | 1.8924 | 1.7406 | 2015-03-31
TX_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 678.0416 | 656.8528 | 656.8528 | 635.664 | 741.608 | 720.4192 | 720.4192 | 656.8528 | 2015-03-31
TX_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 678.0416 | 847.552 | 762.7968 | 762.7968 | 720.4192 | 868.7408 | 805.1744 | 826.3632 | 720.4192 | 2015-03-31
TX_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 678.0416 | 550.9088 | 720.4192 | 593.2864 | 635.664 | 572.0976 | 656.8528 | 593.2864 | 741.608 | 699.2304 | 2015-03-31
TX_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 741.608 | 678.0416 | 783.9856 | 720.4192 | 741.608 | 699.2304 | 826.3632 | 805.1744 | 783.9856 | 699.2304 | 2015-03-31
TX_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 783.9856 | 635.664 | 868.7408 | 720.4192 | 741.608 | 678.0416 | 783.9856 | 720.4192 | 847.552 | 783.9856 | 2015-03-31
TX_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 2015-03-31
TX_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2015-03-31
TX_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2015-03-31
TX_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2015-03-31
TX_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2015-03-31
TX_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | 2015-03-31
TX_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | 2015-03-31
TX_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | 2015-03-31
TX_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | 2015-03-31
TX_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | 2015-03-31
TX_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.4514 | 0.43578 | 0.48611 | 0.47006 | 0.46732 | 0.44897 | 0.52883 | 0.50742 | 0.50664 | 0.46229 | 2015-03-31
TX_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.541 | 0.48487 | 0.60456 | 0.54113 | 0.54214 | 0.51458 | 0.61277 | 0.57606 | 0.5786 | 0.51632 | 2015-03-31
TX_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.47887 | 0.3867 | 0.51352 | 0.41692 | 0.4459 | 0.4042 | 0.46527 | 0.42249 | 0.53 | 0.49788 | 2015-03-31
TX_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.51849 | 0.4741 | 0.54964 | 0.50512 | 0.52108 | 0.50046 | 0.58947 | 0.56385 | 0.55147 | 0.49618 | 2015-03-31
TX_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.55778 | 0.45662 | 0.61527 | 0.50337 | 0.51995 | 0.47723 | 0.5518 | 0.50673 | 0.60392 | 0.55545 | 2015-03-31
TX_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10636.7776 | 10276.568 | 11145.3088 | 10763.9104 | 10806.288 | 10424.8896 | 12183.56 | 11759.784 | 11717.4064 | 11039.3648 | 2015-03-31
TX_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25108.728 | 23540.7568 | 26104.6016 | 24028.0992 | 25151.1056 | 24218.7984 | 27905.6496 | 26888.5872 | 27566.6288 | 27100.4752 | 2015-03-31
TX_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 202247.0963 | 186758.0835 | 206675.5555 | 189364.3059 | 202628.4947 | 193008.7795 | 223584.2179 | 212905.0627 | 221783.1699 | 217291.1443 | 2015-03-31
TX_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22629.6384 | 20256.4928 | 24006.9104 | 21337.1216 | 22799.1488 | 21209.9888 | 25447.7488 | 23625.512 | 26591.944 | 24409.4976 | 2015-03-31
TX_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2015-03-31
TX_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 2015-03-31
TX_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 2015-03-31
TX_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 2015-03-31
TX_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2015-03-31
TX_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 2015-03-31
TX_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 2015-03-31
TX_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 2015-03-31
TX_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 2015-03-31
TX_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 2015-03-31
TX_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 2015-03-31
TX_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 2015-03-31
TX_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | No | No | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
TX_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
TX_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
TX_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | No | No | Yes | No | No | No | No | 2015-03-31
TX_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | No | No | Yes | No | No | No | No | 2015-03-31
TX_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | No | No | Yes | No | No | No | No | 2015-03-31
TX_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
TX_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
TX_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
TX_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
TX_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 422.2669 | 406.9937 | 381.5212 | 363.9037 | 394.3568 | 382.5561 | 314.5024 | 303.2871 | 331.5652 | 325.6491 | 2015-03-31
TX_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 422.2669 | 406.9937 | 381.5212 | 363.9037 | 394.3568 | 382.5561 | 314.5024 | 303.2871 | 331.5652 | 325.6491 | 2015-03-31
TX_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | 2015-03-31
TX_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | 2015-03-31
TX_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 400.7969 | 386.2951 | 362.1211 | 345.3964 | 374.3074 | 363.1002 | 298.5038 | 287.8656 | 314.6992 | 309.089 | 2015-03-31
TX_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 400.7969 | 386.2951 | 362.1211 | 345.3964 | 374.3074 | 363.1002 | 298.5038 | 287.8656 | 314.6992 | 309.089 | 2015-03-31
TX_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.9399 | 3.7919 | 4.0309 | 3.8665 | 4.0726 | 4.1 | 3.7034 | 3.7279 | 4.5234 | 4.3974 | 2015-03-31
TX_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-03-31
TX_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1988.423 | 958.2535 | 1796.6341 | 856.8003 | 1857.0239 | 900.7168 | 1480.9718 | 714.0792 | 1561.3186 | 766.7309 | 2015-03-31
TX_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 958.2535 | 0 | 856.8003 | 0 | 900.7168 | 0 | 714.0792 | 0 | 766.7309 | 2015-03-31
TX_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1988.423 | 1916.4626 | 1796.6341 | 1713.5784 | 1857.0239 | 1801.3892 | 1480.9718 | 1428.1601 | 1561.3186 | 1533.4601 | 2015-03-31
TX_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 792.2515 | 762.4925 | 810.5538 | 777.5059 | 818.945 | 824.445 | 744.7084 | 749.6188 | 909.5898 | 884.2531 | 2015-03-31
TX_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2320.0118 | 2227.6044 | 2096.2052 | 1991.7516 | 2166.7392 | 2093.8277 | 1728.0022 | 1660.0043 | 1821.6776 | 1782.3688 | 2015-03-31
TX_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
TX_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.4144 | 11.0267 | 11.9549 | 11.5568 | 11.5885 | 11.1851 | 13.0763 | 12.6235 | 12.5706 | 11.8528 | 2015-03-31
TX_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.0977 | 32.023 | 37.5148 | 32.7013 | 36.1474 | 32.9449 | 39.9427 | 36.5756 | 39.4567 | 36.8591 | 2015-03-31
TX_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 284.4222 | 248.5154 | 290.6538 | 251.9713 | 284.9414 | 271.4405 | 314.4176 | 283.314 | 311.8881 | 289.1569 | 2015-03-31
TX_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.5214 | 27.7076 | 34.5195 | 29.1698 | 32.7878 | 29.0105 | 36.5937 | 32.1444 | 38.2454 | 33.1942 | 2015-03-31
TX_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.9101 | 42.8309 | 44.1218 | 44.04 | 43.8973 | 43.8146 | 49.1659 | 49.0743 | 48.3652 | 48.1501 | 2015-03-31
TX_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.76845 | 0.76175 | 0.78947 | 0.78254 | 0.78729 | 0.78127 | 0.88304 | 0.8762 | 0.91346 | 0.89572 | 2015-03-31
TX_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.5006 | 9.4049 | 9.759 | 9.6592 | 9.7535 | 9.6599 | 10.8315 | 10.7252 | 11.5148 | 11.2324 | 2015-03-31
TX_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.63232 | 0.61809 | 0.65686 | 0.64086 | 0.66395 | 0.63607 | 0.73358 | 0.70971 | 0.79221 | 0.76418 | 2015-03-31
TX_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.7269 | 5.1694 | 9.6918 | 4.6221 | 10.0179 | 4.859 | 7.9893 | 3.8522 | 8.4228 | 4.1362 | 2015-03-31
TX_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.1694 | 0 | 4.6221 | 0 | 4.859 | 0 | 3.8522 | 0 | 4.1362 | 2015-03-31
TX_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.1806 | 31.0166 | 29.0754 | 27.7328 | 30.0536 | 29.1543 | 23.968 | 23.1133 | 25.2683 | 24.8174 | 2015-03-31
TX_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.125 | 16.4817 | 17.5206 | 16.8062 | 17.702 | 17.8208 | 16.0973 | 16.2035 | 19.6613 | 19.1136 | 2015-03-31
TX_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 42.9701 | 41.2582 | 38.8238 | 36.89 | 40.13 | 38.7809 | 32.0039 | 30.7451 | 33.7402 | 33.012 | 2015-03-31
TX_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.83 | 3.8161 | 3.8451 | 3.821 | 3.8441 | 3.8192 | 4.0673 | 4.0399 | 4.1163 | 4.0798 | 2015-03-31
TX_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | 2015-03-31
TX_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | 2015-03-31
TX_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | YES | NO | NO | NO | NO | 2015-03-31
TX_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | 2015-03-31
TX_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4537.3536 | 4260.0063 | 4611.2325 | 4315.8147 | 4328.2131 | 4392.0566 | 4016.3273 | 4078.0435 | 4519.3832 | 4394.6963 | 2015-03-31
TX_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.3521 | 9.3027 | 8.7799 | 8.7488 | 9.0706 | 9.0319 | 8.618 | 8.5327 | 8.0665 | 8.0798 | 2015-03-31
TX_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 40.5724 | 39.0862 | 36.9065 | 36.006 | 38.0915 | 37.0933 | 32.5293 | 31.0145 | 39.5178 | 32.0693 | 2015-03-31
TX_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4541 | 5.3363 | 6.8769 | 6.2741 | 6.4421 | 6.1971 | 6.0353 | 5.7475 | 6.2511 | 5.9603 | 2015-03-31
TX_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6323 | 5.1101 | 6.0535 | 5.3654 | 5.5744 | 5.2573 | 5.1175 | 4.7551 | 5.3544 | 4.9834 | 2015-03-31
TX_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3432.5856 | 3390.208 | 3474.9632 | 3453.7744 | 3580.9072 | 3538.5296 | 3877.5504 | 3835.1728 | 3623.2848 | 3602.096 | 2015-03-31
TX_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12522.5808 | 11738.5952 | 12776.8464 | 12077.616 | 13031.112 | 12268.3152 | 14471.9504 | 13285.3776 | 14895.7264 | 13052.3008 | 2015-03-31
TX_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2076.5024 | 2712.1664 | 2415.5232 | 2394.3344 | 2267.2016 | 2648.6 | 2500.2784 | 2712.1664 | 2563.8448 | 2015-03-31
TX_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1928.1808 | 1673.9152 | 2309.5792 | 1949.3696 | 1970.5584 | 1822.2368 | 2161.2576 | 1970.5584 | 2246.0128 | 2055.3136 | 2015-03-31
TX_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD | 2015-03-31
TX_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | 2015-03-31
TX_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 2015-03-31
TX_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 2015-03-31
TX_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2015-03-31
TX_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2015-03-31
TX_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | No | No | Yes | Yes | No | No | No | No | 2015-03-31
TX_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.1872 | 1.9781 | 3.3407 | 2.0993 | 2.5434 | 1.6482 | 2.4894 | 1.5992 | 3.3947 | 2.242 | 2015-03-31
TX_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3223 | 2.3008 | 2.3577 | 2.3413 | 2.4238 | 2.4026 | 2.6273 | 2.6013 | 2.4544 | 2.4446 | 2015-03-31
TX_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.4425 | 12.5873 | 13.704 | 12.9629 | 13.9821 | 13.1648 | 15.4202 | 14.2535 | 15.8859 | 13.9997 | 2015-03-31
TX_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6391 | 1.4561 | 1.9073 | 1.6908 | 1.6766 | 1.5927 | 1.8514 | 1.7467 | 1.8981 | 1.791 | 2015-03-31
TX_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.3554 | 1.1749 | 1.6134 | 1.3733 | 1.3807 | 1.2737 | 1.5184 | 1.3878 | 1.569 | 1.4338 | 2015-03-31
TX_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.2663 | 20.7361 | 29.3502 | 23.0974 | 25.1192 | 22.0886 | 27.7626 | 24.2408 | 29.0258 | 24.8772 | 2015-03-31
TX_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.9115 | 20.7583 | 29.0225 | 23.1511 | 24.861 | 22.1364 | 27.2651 | 24.3048 | 28.6615 | 24.8225 | 2015-03-31
TX_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.3546 | 18.9906 | 26.3273 | 21.3937 | 22.3916 | 20.3735 | 24.718 | 22.3646 | 25.9091 | 22.9941 | 2015-03-31
TX_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.8212 | 26.3537 | 34.3772 | 28.6359 | 31.001 | 27.907 | 26.7347 | 24.7724 | 29.75 | 26.9942 | 2015-03-31
TX_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 8.9125 | 8.8534 | 11.1636 | 11.1636 | 8.2559 | 8.2617 | 8.5685 | 8.5176 | 2015-03-31
TX_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.3644 | 5.347 | 6.7844 | 5.6695 | 6.3748 | 5.5954 | 6.1887 | 5.5937 | 7.0159 | 6.3185 | 2015-03-31
TX_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 2015-03-31
TX_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7882.2336 | 6229.5072 | 8814.5408 | 6928.7376 | 7543.2128 | 6632.0944 | 8327.1984 | 7267.7584 | 8708.5968 | 7458.4576 | 2015-03-31
TX_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7776.2896 | 6229.5072 | 8708.5968 | 6949.9264 | 7458.4576 | 6653.2832 | 8178.8768 | 7288.9472 | 8602.6528 | 7458.4576 | 2015-03-31
TX_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7013.4928 | 5699.7872 | 7903.4224 | 6420.2064 | 6716.8496 | 6123.5632 | 7416.08 | 6716.8496 | 7776.2896 | 6907.5488 | 2015-03-31
TX_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9556.1488 | 7903.4224 | 10318.9456 | 8602.6528 | 9301.8832 | 8369.576 | 10318.9456 | 9195.9392 | 10954.6096 | 9365.4496 | 2015-03-31
TX_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 2902.8656 | 2860.488 | 3347.8304 | 3347.8304 | 3178.32 | 3178.32 | 3263.0752 | 3220.6976 | 2015-03-31
TX_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1906.992 | 1610.3488 | 2034.1248 | 1695.104 | 1906.992 | 1673.9152 | 2076.5024 | 1801.048 | 2309.5792 | 1949.3696 | 2015-03-31
TX_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 2015-03-31
TX_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD | 2015-03-31
TX_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | n/a | VFD | VFD | VFD | n/a | VFD | n/a | VFD | 2015-03-31
TX_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | 2015-03-31
TX_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2015-03-31
TX_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | Yes | Yes | No | No | Yes | Yes | Yes | Yes | 2015-03-31
TX_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | No | No | No | Yes | No | Yes | 2015-03-31
TX_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | No | No | No | Yes | No | Yes | 2015-03-31
TX_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | No | No | No | Yes | No | Yes | 2015-03-31
TX_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 6222.5573 | 7852.8447 | 6931.1531 | 7537.852 | 6628.4287 | 7852.8447 | 7274.2846 | 7852.8447 | 7465.238 | 2015-03-31
TX_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7775.6116 | 6229.2106 | 7852.8447 | 6947.2566 | 7460.3858 | 6642.7524 | 7852.8447 | 7293.4604 | 7852.8447 | 7448.8379 | 2015-03-31
TX_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 5698.7701 | 6777.6191 | 6419.9098 | 6719.3287 | 6113.774 | 6777.6191 | 6711.2558 | 6777.6191 | 6777.6191 | 2015-03-31
TX_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 2015-03-31
TX_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 825.0071 | 825.0071 | 1434.9903 | 1434.9903 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 2015-03-31
TX_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 2015-03-31
TX_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 2015-03-31
TX_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 2015-03-31
TX_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 2015-03-31
TX_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | No | 2015-03-31
TX_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | No | No | Yes | Yes | No | No | No | No | 2015-03-31
TX_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | No | No | No | No | No | No | No | 2015-03-31
TX_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | No | No | Yes | Yes | No | No | No | No | 2015-03-31
TX_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 2015-03-31
TX_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
TX_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2929 | 1.1798 | 1.3749 | 1.2013 | 1.3105 | 1.2484 | 1.2293 | 1.1405 | 1.4823 | 1.3274 | 2015-03-31
TX_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 129.9923 | 118.6181 | 138.2324 | 120.7861 | 131.7615 | 125.5173 | 123.5997 | 114.6671 | 149.0385 | 133.4632 | 2015-03-31
TX_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.5404 | 9.1801 | 12.8953 | 10.1481 | 11.0363 | 9.7789 | 12.1978 | 10.6504 | 12.7528 | 10.9301 | 2015-03-31
TX_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.3845 | 9.19 | 12.7513 | 10.1717 | 10.9229 | 9.8001 | 11.9792 | 10.6785 | 12.5927 | 10.906 | 2015-03-31
TX_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.2611 | 8.4074 | 11.5672 | 9.4713 | 9.913 | 9.0196 | 10.8601 | 9.9011 | 11.3834 | 10.1027 | 2015-03-31
TX_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.9809 | 11.5787 | 15.0065 | 12.5815 | 13.6206 | 12.2612 | 15.0245 | 13.4585 | 15.9337 | 13.6987 | 2015-03-31
TX_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.038 | 2.0089 | 2.2687 | 2.2687 | 2.1587 | 2.1519 | 2.2086 | 2.1827 | 2015-03-31
TX_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3383 | 1.1243 | 1.4266 | 1.1921 | 1.3404 | 1.1766 | 1.4504 | 1.2597 | 1.6126 | 1.3705 | 2015-03-31
TX_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2015-03-31
TX_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8099 | 2.564 | 2.988 | 2.6109 | 2.8481 | 2.7131 | 2.6717 | 2.4786 | 3.2216 | 2.8849 | 2015-03-31
TX_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
TX_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
TX_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
TX_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
TX_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | NO | NO | YES | YES | NO | NO | NO | NO | 2015-03-31
TX_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
TX_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
TX_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.7164 | 96.5544 | 106.7049 | 95.295 | 98.6219 | 95.8616 | 92.0499 | 86.6053 | 99.2825 | 90.4291 | 2015-03-31
TX_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2294 | 2.067 | 2.3659 | 2.1342 | 2.2181 | 2.1512 | 1.9359 | 1.8348 | 1.9332 | 1.8489 | 2015-03-31
TX_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.7731 | 5.3122 | 6.0252 | 5.5628 | 5.7674 | 5.5703 | 5.3446 | 5.1847 | 5.3472 | 5.2131 | 2015-03-31
TX_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6586 | 2.4631 | 2.7699 | 2.6125 | 2.6923 | 2.5953 | 2.7771 | 2.6463 | 2.7682 | 2.647 | 2015-03-31
TX_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5303 | 4.4686 | 4.5674 | 4.4885 | 4.6111 | 4.5751 | 4.2742 | 4.2282 | 4.2083 | 4.172 | 2015-03-31
TX_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 635.664 | 805.1744 | 699.2304 | 720.4192 | 678.0416 | 783.9856 | 741.608 | 762.7968 | 720.4192 | 2015-03-31
TX_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1737.4816 | 1589.16 | 1801.048 | 1673.9152 | 1737.4816 | 1673.9152 | 1906.992 | 1843.4256 | 1864.6144 | 1801.048 | 2015-03-31
TX_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 805.1744 | 741.608 | 826.3632 | 783.9856 | 805.1744 | 783.9856 | 911.1184 | 847.552 | 889.9296 | 826.3632 | 2015-03-31
TX_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | 1589.16 | 1546.7824 | 1546.7824 | 1525.5936 | 1737.4816 | 1716.2928 | 1695.104 | 1673.9152 | 2015-03-31
TX_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 2015-03-31
TX_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 2015-03-31
TX_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 2015-03-31
TX_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 2015-03-31
TX_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
TX_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
TX_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
TX_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
TX_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | No | DifferentialDryBulb | No | DifferentialEnthalpy | DifferentialEnthalpy | No | No | No | No | 2015-03-31
TX_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.2139 | 1.117 | 1.2669 | 1.1697 | 1.2127 | 1.1713 | 1.3387 | 1.2891 | 1.3099 | 1.268 | 2015-03-31
TX_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0517 | 1.0459 | 1.1135 | 1.0883 | 1.0853 | 1.0743 | 1.214 | 1.2004 | 1.1909 | 1.1785 | 2015-03-31
TX_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.7401 | 0.68934 | 0.67943 | 0.64196 | 0.7013 | 0.67785 | 0.56466 | 0.53365 | 0.5479 | 0.54191 | 2015-03-31
TX_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.73674 | 0.6862 | 0.67559 | 0.63844 | 0.69728 | 0.67462 | 0.56109 | 0.53082 | 0.54185 | 0.53624 | 2015-03-31
TX_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.9362 | 0.80779 | 0.92987 | 0.79921 | 0.8481 | 0.81167 | 0.70947 | 0.66851 | 0.71226 | 0.71323 | 2015-03-31
TX_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.152 | 0.99266 | 1.1478 | 0.98101 | 1.0604 | 1.0089 | 0.88883 | 0.82828 | 0.95293 | 0.94621 | 2015-03-31
TX_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.72863 | 0.65303 | 0.84501 | 0.73546 | 0.67687 | 0.6542 | 0.55136 | 0.52031 | 0.54865 | 0.53788 | 2015-03-31
TX_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73972 | 0.65732 | 0.85503 | 0.74682 | 0.67874 | 0.65725 | 0.55625 | 0.52693 | 0.54248 | 0.53215 | 2015-03-31
TX_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.139 | 0.97615 | 1.2293 | 1.0358 | 1.054 | 1.0026 | 0.89163 | 0.82916 | 0.96238 | 0.95053 | 2015-03-31
TX_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.777 | 1.6645 | 1.5887 | 1.51 | 1.7379 | 1.683 | 1.4791 | 1.4116 | 1.511 | 1.4845 | 2015-03-31
TX_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7715 | 1.6595 | 1.5824 | 1.5041 | 1.7314 | 1.6777 | 1.4734 | 1.4071 | 1.5011 | 1.4754 | 2015-03-31
TX_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2614 | 1.9956 | 2.1897 | 1.9074 | 2.1614 | 2.0568 | 1.8724 | 1.771 | 2.0052 | 1.9812 | 2015-03-31
TX_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.7135 | 2.3764 | 2.65 | 2.3047 | 2.5985 | 2.4677 | 2.2587 | 2.1124 | 2.5113 | 2.4687 | 2015-03-31
TX_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7706 | 1.6076 | 1.9657 | 1.7348 | 1.722 | 1.6668 | 1.4568 | 1.3888 | 1.5071 | 1.4653 | 2015-03-31
TX_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7744 | 1.6028 | 1.9693 | 1.7377 | 1.7161 | 1.6621 | 1.4511 | 1.3843 | 1.4993 | 1.5363 | 2015-03-31
TX_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3011 | 2.013 | 2.4738 | 2.1275 | 2.2572 | 2.1468 | 1.9554 | 1.8344 | 2.1121 | 2.0765 | 2015-03-31
TX_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.6727 | 2.3373 | 2.8248 | 2.4197 | 2.5764 | 2.4445 | 2.2693 | 2.1188 | 2.5478 | 2.4924 | 2015-03-31
TX_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2822 | 2.1403 | 2.2848 | 2.1293 | 2.1886 | 2.139 | 2.3196 | 2.2552 | 2.2734 | 2.2779 | 2015-03-31
TX_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.135 | 1.0398 | 1.1055 | 0.96245 | 1.1473 | 1.078 | 1.0067 | 0.92889 | 1.0775 | 0.96885 | 2015-03-31
TX_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1289 | 1.0342 | 1.1078 | 0.99403 | 1.1403 | 1.0723 | 1.002 | 0.92345 | 1.0764 | 0.95908 | 2015-03-31
TX_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3733 | 1.2509 | 1.3409 | 1.2287 | 1.4371 | 1.3327 | 1.2669 | 1.1514 | 1.3811 | 1.2524 | 2015-03-31
TX_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6711 | 1.4523 | 1.6637 | 1.4351 | 1.6399 | 1.5162 | 1.4905 | 1.3543 | 1.6892 | 1.5678 | 2015-03-31
TX_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2048 | 1.0754 | 1.3149 | 1.1509 | 1.2553 | 1.1621 | 1.0854 | 0.98204 | 1.2079 | 1.0687 | 2015-03-31
TX_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.207 | 1.0769 | 1.3174 | 1.1527 | 1.2575 | 1.164 | 1.0872 | 0.98376 | 1.2119 | 1.0724 | 2015-03-31
TX_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.4694 | 1.3033 | 1.591 | 1.3895 | 1.5335 | 1.4206 | 1.3588 | 1.2336 | 1.5289 | 1.376 | 2015-03-31
TX_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6675 | 1.4457 | 1.7774 | 1.5211 | 1.656 | 1.5322 | 1.518 | 1.377 | 1.7212 | 1.5851 | 2015-03-31
TX_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
TX_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 2015-03-31
TX_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
TX_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
TX_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
TX_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
TX_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
TX_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
TX_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
TX_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
TX_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 2015-03-31
TX_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
TX_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 233.0768 | 233.0768 | 233.0768 | 233.0768 | 254.2656 | 233.0768 | 254.2656 | 254.2656 | 2015-03-31
TX_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 233.0768 | 211.888 | 233.0768 | 233.0768 | 254.2656 | 233.0768 | 254.2656 | 233.0768 | 2015-03-31
TX_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 275.4544 | 360.2096 | 296.6432 | 296.6432 | 275.4544 | 317.832 | 296.6432 | 317.832 | 317.832 | 2015-03-31
TX_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 339.0208 | 444.9648 | 360.2096 | 402.5872 | 360.2096 | 402.5872 | 381.3984 | 423.776 | 423.776 | 2015-03-31
TX_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 296.6432 | 254.2656 | 233.0768 | 211.888 | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 2015-03-31
TX_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 296.6432 | 254.2656 | 233.0768 | 211.888 | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 2015-03-31
TX_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 339.0208 | 466.1536 | 381.3984 | 381.3984 | 360.2096 | 402.5872 | 381.3984 | 423.776 | 423.776 | 2015-03-31
TX_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 572.0976 | 550.9088 | 635.664 | 614.4752 | 656.8528 | 635.664 | 678.0416 | 678.0416 | 2015-03-31
TX_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 572.0976 | 550.9088 | 635.664 | 593.2864 | 656.8528 | 635.664 | 678.0416 | 656.8528 | 2015-03-31
TX_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 678.0416 | 847.552 | 699.2304 | 805.1744 | 762.7968 | 847.552 | 805.1744 | 911.1184 | 889.9296 | 2015-03-31
TX_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 868.7408 | 1038.2512 | 889.9296 | 995.8736 | 932.3072 | 1017.0624 | 953.496 | 1123.0064 | 1101.8176 | 2015-03-31
TX_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 699.2304 | 593.2864 | 614.4752 | 593.2864 | 656.8528 | 635.664 | 678.0416 | 656.8528 | 2015-03-31
TX_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 699.2304 | 614.4752 | 614.4752 | 572.0976 | 656.8528 | 614.4752 | 678.0416 | 656.8528 | 2015-03-31
TX_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 699.2304 | 953.496 | 805.1744 | 826.3632 | 783.9856 | 889.9296 | 826.3632 | 953.496 | 932.3072 | 2015-03-31
TX_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 974.6848 | 826.3632 | 1101.8176 | 932.3072 | 974.6848 | 932.3072 | 1017.0624 | 953.496 | 1144.1952 | 1123.0064 | 2015-03-31
TX_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 889.9296 | 1017.0624 | 932.3072 | 953.496 | 932.3072 | 1038.2512 | 1017.0624 | 1017.0624 | 1017.0624 | 2015-03-31
TX_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | 423.776 | 402.5872 | 444.9648 | 423.776 | 487.3424 | 444.9648 | 2015-03-31
TX_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | 423.776 | 402.5872 | 444.9648 | 423.776 | 487.3424 | 423.776 | 2015-03-31
TX_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 423.776 | 529.72 | 444.9648 | 529.72 | 487.3424 | 572.0976 | 508.5312 | 614.4752 | 572.0976 | 2015-03-31
TX_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 550.9088 | 678.0416 | 572.0976 | 635.664 | 593.2864 | 678.0416 | 614.4752 | 762.7968 | 699.2304 | 2015-03-31
TX_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | 508.5312 | 423.776 | 444.9648 | 423.776 | 487.3424 | 444.9648 | 550.9088 | 466.1536 | 2015-03-31
TX_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | 508.5312 | 423.776 | 466.1536 | 423.776 | 487.3424 | 444.9648 | 550.9088 | 487.3424 | 2015-03-31
TX_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 614.4752 | 529.72 | 572.0976 | 529.72 | 614.4752 | 550.9088 | 678.0416 | 614.4752 | 2015-03-31
TX_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 529.72 | 720.4192 | 593.2864 | 635.664 | 593.2864 | 678.0416 | 614.4752 | 783.9856 | 720.4192 | 2015-03-31
TX_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
TX_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.17067 | 0.15441 | 0.16964 | 0.15872 | 0.17082 | 0.16328 | 0.18019 | 0.1703 | 0.17484 | 0.17294 | 2015-03-31
TX_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.1696 | 0.15343 | 0.16839 | 0.15758 | 0.16955 | 0.16225 | 0.17905 | 0.1694 | 0.17291 | 0.17113 | 2015-03-31
TX_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.23303 | 0.18777 | 0.25029 | 0.20323 | 0.21259 | 0.20215 | 0.2264 | 0.21334 | 0.2273 | 0.22761 | 2015-03-31
TX_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.2963 | 0.24577 | 0.31489 | 0.26271 | 0.27842 | 0.26179 | 0.28365 | 0.26433 | 0.3041 | 0.30196 | 2015-03-31
TX_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15608 | 0.14323 | 0.20831 | 0.17361 | 0.16173 | 0.15449 | 0.17596 | 0.16605 | 0.17109 | 0.16721 | 2015-03-31
TX_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16001 | 0.1457 | 0.2122 | 0.17722 | 0.16385 | 0.15695 | 0.17751 | 0.16815 | 0.17255 | 0.16881 | 2015-03-31
TX_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.28735 | 0.23728 | 0.33527 | 0.27624 | 0.27461 | 0.25801 | 0.28454 | 0.2646 | 0.30712 | 0.30334 | 2015-03-31
TX_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.4324 | 0.39606 | 0.41121 | 0.38528 | 0.44656 | 0.42874 | 0.47203 | 0.45049 | 0.48219 | 0.47376 | 2015-03-31
TX_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.43066 | 0.39445 | 0.40915 | 0.38336 | 0.44445 | 0.42705 | 0.47019 | 0.44904 | 0.47904 | 0.47082 | 2015-03-31
TX_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.58178 | 0.48702 | 0.59948 | 0.50181 | 0.56436 | 0.53377 | 0.59753 | 0.56517 | 0.63991 | 0.63224 | 2015-03-31
TX_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.7169 | 0.6099 | 0.73959 | 0.62881 | 0.70469 | 0.66228 | 0.7208 | 0.6741 | 0.80141 | 0.78781 | 2015-03-31
TX_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.40538 | 0.37303 | 0.50084 | 0.42733 | 0.43091 | 0.41324 | 0.46491 | 0.44318 | 0.48096 | 0.46763 | 2015-03-31
TX_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.40657 | 0.37153 | 0.50201 | 0.42827 | 0.42905 | 0.41175 | 0.46308 | 0.44175 | 0.47845 | 0.4665 | 2015-03-31
TX_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.5866 | 0.49106 | 0.68148 | 0.56468 | 0.58451 | 0.54928 | 0.624 | 0.5854 | 0.67404 | 0.66265 | 2015-03-31
TX_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.69838 | 0.59277 | 0.78733 | 0.6639 | 0.69788 | 0.65516 | 0.72419 | 0.67616 | 0.81306 | 0.79537 | 2015-03-31
TX_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.68216 | 0.63273 | 0.72284 | 0.66771 | 0.67105 | 0.65375 | 0.74024 | 0.71969 | 0.72551 | 0.72691 | 2015-03-31
TX_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.29061 | 0.25976 | 0.28974 | 0.25568 | 0.30559 | 0.28314 | 0.32126 | 0.29643 | 0.34384 | 0.30919 | 2015-03-31
TX_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.28864 | 0.25795 | 0.28943 | 0.25398 | 0.30335 | 0.28133 | 0.31977 | 0.29469 | 0.34349 | 0.30606 | 2015-03-31
TX_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.35962 | 0.30776 | 0.37137 | 0.32164 | 0.3736 | 0.341 | 0.4043 | 0.36744 | 0.44073 | 0.39966 | 2015-03-31
TX_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.45294 | 0.38357 | 0.47394 | 0.40056 | 0.45719 | 0.41916 | 0.47563 | 0.43217 | 0.53908 | 0.50032 | 2015-03-31
TX_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.30015 | 0.25926 | 0.35483 | 0.30219 | 0.32249 | 0.29335 | 0.34637 | 0.3134 | 0.38548 | 0.33796 | 2015-03-31
TX_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.30083 | 0.25974 | 0.35563 | 0.30275 | 0.32317 | 0.29395 | 0.34696 | 0.31395 | 0.38674 | 0.33925 | 2015-03-31
TX_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.37683 | 0.32425 | 0.4378 | 0.37307 | 0.40378 | 0.36843 | 0.43362 | 0.39368 | 0.48789 | 0.43913 | 2015-03-31
TX_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.44893 | 0.37868 | 0.50577 | 0.4239 | 0.45809 | 0.41825 | 0.48442 | 0.43944 | 0.54928 | 0.50583 | 2015-03-31
AZ_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9023 | 1.8533 | 1.6276 | 1.5633 | 1.666 | 1.5219 | 1.623 | 1.4875 |  |  | 2015-03-31
AZ_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.3789 | 2.1535 | 1.8939 | 1.7995 | 1.853 | 1.6605 | 1.8165 | 1.646 |  |  | 2015-03-31
AZ_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.7373 | 1.4289 | 1.5288 | 1.3822 | 1.6592 | 1.5687 | 1.5935 | 1.5296 |  |  | 2015-03-31
AZ_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 2.2474 | 2.067 | 1.8056 | 1.7298 | 1.7711 | 1.5946 | 1.725 | 1.5662 |  |  | 2015-03-31
AZ_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 2.0157 | 1.6935 | 1.7713 | 1.6211 | 1.9424 | 1.7912 | 1.8789 | 1.7604 |  |  | 2015-03-31
AZ_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 741.608 | 699.2304 | 741.608 | 678.0416 | 720.4192 | 678.0416 |  |  | 2015-03-31
AZ_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 974.6848 | 847.552 | 847.552 | 805.1744 | 826.3632 | 741.608 | 826.3632 | 741.608 |  |  | 2015-03-31
AZ_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 783.9856 | 635.664 | 678.0416 | 614.4752 | 741.608 | 699.2304 | 720.4192 | 678.0416 |  |  | 2015-03-31
AZ_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 911.1184 | 826.3632 | 805.1744 | 783.9856 | 805.1744 | 720.4192 | 783.9856 | 699.2304 |  |  | 2015-03-31
AZ_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 889.9296 | 741.608 | 805.1744 | 720.4192 | 868.7408 | 805.1744 | 847.552 | 783.9856 |  |  | 2015-03-31
AZ_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  | 2015-03-31
AZ_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2015-03-31
AZ_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2015-03-31
AZ_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2015-03-31
AZ_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2015-03-31
AZ_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.50636 | 0.49016 | 0.51942 | 0.4989 | 0.53166 | 0.48566 | 0.51793 | 0.47468 |  |  | 2015-03-31
AZ_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.68518 | 0.6081 | 0.60439 | 0.57427 | 0.59132 | 0.5299 | 0.5797 | 0.52528 |  |  | 2015-03-31
AZ_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.55442 | 0.45356 | 0.48789 | 0.44109 | 0.52948 | 0.5006 | 0.50854 | 0.48813 |  |  | 2015-03-31
AZ_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.64338 | 0.58517 | 0.57621 | 0.552 | 0.56519 | 0.50886 | 0.55048 | 0.49981 |  |  | 2015-03-31
AZ_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.62894 | 0.52065 | 0.56527 | 0.51734 | 0.61986 | 0.57162 | 0.59958 | 0.56178 |  |  | 2015-03-31
AZ_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11293.6304 | 10933.4208 | 11950.4832 | 11547.896 | 12374.2592 | 11675.0288 | 11717.4064 | 11293.6304 |  |  | 2015-03-31
AZ_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 27778.5168 | 25744.392 | 27227.608 | 26210.5456 | 28795.5792 | 28371.8032 | 28647.2576 | 28265.8592 |  |  | 2015-03-31
AZ_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 226529.4611 | 209048.7011 | 217693.7315 | 206929.8211 | 230682.4659 | 226487.0835 | 231063.8643 | 226698.9715 |  |  | 2015-03-31
AZ_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 26464.8112 | 23583.1344 | 24981.5952 | 23180.5472 | 27587.8176 | 25384.1824 | 27948.0272 | 25638.448 |  |  | 2015-03-31
AZ_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2015-03-31
AZ_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2015-03-31
AZ_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2015-03-31
AZ_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2015-03-31
AZ_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  | 2015-03-31
AZ_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  | 2015-03-31
AZ_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  | 2015-03-31
AZ_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  | 2015-03-31
AZ_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  | 2015-03-31
AZ_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  | 2015-03-31
AZ_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  | 2015-03-31
AZ_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  | 2015-03-31
AZ_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
AZ_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
AZ_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
AZ_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
AZ_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 366.3357 | 347.8436 | 309.9703 | 298.3117 | 287.4423 | 281.8768 | 291.1032 | 285.6514 |  |  | 2015-03-31
AZ_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 366.3357 | 347.8436 | 309.9703 | 298.3117 | 287.4423 | 281.8768 | 291.1032 | 285.6514 |  |  | 2015-03-31
AZ_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  | 2015-03-31
AZ_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  | 2015-03-31
AZ_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 347.7119 | 330.1537 | 294.2035 | 283.142 | 272.8214 | 267.542 | 276.3013 | 271.1277 |  |  | 2015-03-31
AZ_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 347.7119 | 330.1537 | 294.2035 | 283.142 | 272.8214 | 267.542 | 276.3013 | 271.1277 |  |  | 2015-03-31
AZ_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.3222 | 3.1787 | 3.6752 | 3.6857 | 3.8167 | 3.7214 | 4.083 | 3.967 |  |  | 2015-03-31
AZ_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2015-03-31
AZ_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1724.9907 | 818.9862 | 1459.6309 | 702.3659 | 1353.5479 | 663.6705 | 1370.7867 | 672.5577 |  |  | 2015-03-31
AZ_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 818.9862 | 0 | 702.3659 | 0 | 663.6705 | 0 | 672.5577 |  |  | 2015-03-31
AZ_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1724.9907 | 1637.9724 | 1459.6309 | 1404.7301 | 1353.5479 | 1327.3393 | 1370.7867 | 1345.1139 |  |  | 2015-03-31
AZ_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 668.0483 | 639.1849 | 739.0277 | 741.1437 | 767.4806 | 748.3286 | 821.0277 | 797.7056 |  |  | 2015-03-31
AZ_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2012.674 | 1903.7823 | 1702.9587 | 1653.0302 | 1601.6752 | 1561.9194 | 1622.1221 | 1582.8339 |  |  | 2015-03-31
AZ_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
AZ_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 12.1301 | 11.7379 | 12.8326 | 12.3871 | 13.2806 | 12.525 | 12.5726 | 12.1296 |  |  | 2015-03-31
AZ_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 39.7679 | 35.0357 | 38.9849 | 35.6438 | 41.2335 | 38.5946 | 41.0217 | 38.4596 |  |  | 2015-03-31
AZ_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 318.5569 | 278.1736 | 306.1346 | 275.369 | 324.4105 | 301.3931 | 324.9407 | 318.7986 |  |  | 2015-03-31
AZ_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 38.0535 | 32.07 | 35.9189 | 31.5483 | 39.5009 | 34.5359 | 40.0029 | 34.8836 |  |  | 2015-03-31
AZ_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 44.612 | 44.5317 | 48.2631 | 48.1711 | 51.2041 | 50.9775 | 50.651 | 50.563 |  |  | 2015-03-31
AZ_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.8057 | 0.79926 | 0.86646 | 0.85957 | 0.95601 | 0.93896 | 0.95037 | 0.9342 |  |  | 2015-03-31
AZ_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.9387 | 9.9279 | 10.6268 | 10.5194 | 12.0142 | 11.7502 | 11.9662 | 11.6997 |  |  | 2015-03-31
AZ_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.66727 | 0.65462 | 0.72753 | 0.69889 | 0.82591 | 0.79869 | 0.82489 | 0.79701 |  |  | 2015-03-31
AZ_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.306 | 4.4181 | 7.8742 | 3.789 | 7.3019 | 3.5803 | 7.3949 | 3.6282 |  |  | 2015-03-31
AZ_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.4181 | 0 | 3.789 | 0 | 3.5803 | 0 | 3.6282 |  |  | 2015-03-31
AZ_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 27.9181 | 26.5089 | 23.6226 | 22.7341 | 21.9057 | 21.4816 | 22.1847 | 21.7693 |  |  | 2015-03-31
AZ_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 14.4402 | 13.8164 | 15.9745 | 16.0203 | 16.5896 | 16.1756 | 17.747 | 17.2429 |  |  | 2015-03-31
AZ_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 37.2785 | 35.262 | 31.5427 | 30.6158 | 29.6654 | 28.9291 | 30.0432 | 29.3165 |  |  | 2015-03-31
AZ_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8223 | 3.8094 | 4.0397 | 4.012 | 4.1414 | 4.1069 | 4.1175 | 4.0915 |  |  | 2015-03-31
AZ_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | NO | NO | YES | YES |  |  | 2015-03-31
AZ_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO | NO | NO |  |  | 2015-03-31
AZ_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO | YES | YES |  |  | 2015-03-31
AZ_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO | NO | NO |  |  | 2015-03-31
AZ_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4174.5623 | 3883.0953 | 4020.7744 | 4054.2854 | 4036.3409 | 3932.8857 | 4148.5239 | 4036.2046 |  |  | 2015-03-31
AZ_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.2486 | 9.1638 | 8.3148 | 8.2539 | 8.1807 | 8.1648 | 8.1688 | 8.147 |  |  | 2015-03-31
AZ_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 35.4016 | 33.6883 | 30.9901 | 29.9116 | 34.8423 | 30.2018 | 35.2964 | 30.0094 |  |  | 2015-03-31
AZ_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.4601 | 6.7774 | 6.1746 | 5.8867 | 6.1985 | 5.8594 | 6.2852 | 5.9393 |  |  | 2015-03-31
AZ_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.5655 | 5.8033 | 5.2667 | 4.9049 | 5.0824 | 4.6475 | 5.1636 | 4.7198 |  |  | 2015-03-31
AZ_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4068.2496 | 4025.872 | 3750.4176 | 3708.04 | 3686.8512 | 3665.6624 | 3686.8512 | 3665.6624 |  |  | 2015-03-31
AZ_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14026.9856 | 12967.5456 | 13942.2304 | 13094.6784 | 15510.2016 | 13603.2096 | 15467.824 | 13518.4544 |  |  | 2015-03-31
AZ_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2945.2432 | 2627.4112 | 2669.7888 | 2521.4672 | 2796.9216 | 2627.4112 | 2839.2992 | 2669.7888 |  |  | 2015-03-31
AZ_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2521.4672 | 2161.2576 | 2203.6352 | 2034.1248 | 2288.3904 | 2097.6912 | 2330.768 | 2118.88 |  |  | 2015-03-31
AZ_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | n/a | VFD | n/a | VFD |  |  | 2015-03-31
AZ_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD |  |  | 2015-03-31
AZ_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  | 2015-03-31
AZ_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  | 2015-03-31
AZ_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2015-03-31
AZ_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2015-03-31
AZ_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.405 | 1.3519 | 2.3863 | 1.5176 | 2.7895 | 1.8326 | 3.1556 | 2.0553 |  |  | 2015-03-31
AZ_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.7541 | 2.721 | 2.5349 | 2.5163 | 2.494 | 2.4891 | 2.4903 | 2.4837 |  |  | 2015-03-31
AZ_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.9574 | 13.9244 | 14.8635 | 14.0496 | 16.5465 | 14.5905 | 16.5 | 14.4975 |  |  | 2015-03-31
AZ_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 2.0649 | 1.8364 | 1.8719 | 1.7691 | 1.9552 | 1.8483 | 1.9826 | 1.8735 |  |  | 2015-03-31
AZ_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.7727 | 1.5205 | 1.5487 | 1.4207 | 1.6032 | 1.466 | 1.6288 | 1.4888 |  |  | 2015-03-31
AZ_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 32.1401 | 25.4453 | 27.8732 | 24.426 | 23.3806 | 21.0631 | 23.6591 | 21.2488 |  |  | 2015-03-31
AZ_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 31.7135 | 25.4828 | 27.499 | 24.4434 | 23.1366 | 20.9287 | 23.4134 | 21.1066 |  |  | 2015-03-31
AZ_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 28.7096 | 23.3579 | 24.638 | 22.4062 | 20.626 | 19.0442 | 20.8836 | 19.143 |  |  | 2015-03-31
AZ_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 33.7815 | 29.5104 | 26.6164 | 24.7252 | 25.1843 | 21.4873 | 25.4466 | 21.5695 |  |  | 2015-03-31
AZ_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.9194 | 8.8068 | 8.1911 | 8.1927 | 7.6787 | 7.6334 | 7.7507 | 7.6891 |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 7.4582 | 6.171 | 6.182 | 5.6381 | 5.7182 | 5.0826 | 5.7996 | 5.1107 |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 8.8997 | 8.8997 | 8.9675 | 8.9675 |  |  | 2015-03-31
AZ_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 9640.904 | 7627.968 | 8369.576 | 7331.3248 | 8984.0512 | 7712.7232 | 9132.3728 | 7776.2896 |  |  | 2015-03-31
AZ_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 9513.7712 | 7649.1568 | 8242.4432 | 7331.3248 | 8835.7296 | 7649.1568 | 8984.0512 | 7712.7232 |  |  | 2015-03-31
AZ_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 8623.8416 | 7013.4928 | 7416.08 | 6716.8496 | 8009.3664 | 7077.0592 | 8157.688 | 7119.4368 |  |  | 2015-03-31
AZ_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 11441.952 | 9407.8272 | 10234.1904 | 9153.5616 | 11336.008 | 9683.2816 | 11463.1408 | 9704.4704 |  |  | 2015-03-31
AZ_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3029.9984 | 2966.432 | 3157.1312 | 3135.9424 | 3411.3968 | 3369.0192 | 3390.208 | 3347.8304 |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2246.0128 | 1843.4256 | 2055.3136 | 1822.2368 | 2351.9568 | 1991.7472 | 2351.9568 | 1991.7472 |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  | 2015-03-31
AZ_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | n/a | n/a | n/a |  |  | 2015-03-31
AZ_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD |  |  | 2015-03-31
AZ_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | n/a | VFD | n/a | VFD |  |  | 2015-03-31
AZ_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2015-03-31
AZ_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2015-03-31
AZ_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | Yes | No | Yes | No | Yes |  |  | 2015-03-31
AZ_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | Yes | No | Yes | No | Yes |  |  | 2015-03-31
AZ_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | Yes | No | Yes | No | Yes |  |  | 2015-03-31
AZ_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7635.7019 | 7852.8447 | 7329.8204 | 7852.8447 | 7705.3495 | 7852.8447 | 7772.9206 |  |  | 2015-03-31
AZ_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7646.9744 | 7852.8447 | 7335.0752 | 7852.8447 | 7656.1915 | 7852.8447 | 7720.9233 |  |  | 2015-03-31
AZ_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6777.6191 | 6777.6191 | 6723.736 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 |  |  | 2015-03-31
AZ_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  | 2015-03-31
AZ_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  | 2015-03-31
AZ_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | No | Yes | No | Yes | No |  |  | 2015-03-31
AZ_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | No | Yes | No | Yes | No |  |  | 2015-03-31
AZ_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | No | Yes | No | Yes | No |  |  | 2015-03-31
AZ_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  | 2015-03-31
AZ_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
AZ_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2943 | 1.1177 | 1.2316 | 1.143 | 1.309 | 1.173 | 1.4082 | 1.2442 |  |  | 2015-03-31
AZ_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 130.1285 | 112.3794 | 123.8286 | 114.9245 | 131.6132 | 117.9353 | 141.5805 | 125.0953 |  |  | 2015-03-31
AZ_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 14.1211 | 11.1796 | 12.2464 | 10.7318 | 13.151 | 11.2816 | 13.3699 | 11.3805 |  |  | 2015-03-31
AZ_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 13.9336 | 11.1961 | 12.082 | 10.7395 | 12.9387 | 11.2096 | 13.1584 | 11.3044 |  |  | 2015-03-31
AZ_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 12.6138 | 10.2625 | 10.8718 | 9.9195 | 11.7411 | 10.3496 | 11.9395 | 10.4351 |  |  | 2015-03-31
AZ_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 16.6581 | 13.7652 | 14.8941 | 13.4089 | 16.4917 | 14.1621 | 16.6635 | 14.2163 |  |  | 2015-03-31
AZ_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.0531 | 2.0813 | 2.1337 | 2.1261 | 2.3098 | 2.2832 | 2.2977 | 2.2656 |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.5682 | 1.2976 | 1.4464 | 1.2803 | 1.6469 | 1.3996 | 1.6468 | 1.3885 |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  | 2015-03-31
AZ_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8128 | 2.4291 | 2.6766 | 2.4842 | 2.8449 | 2.5492 | 3.0603 | 2.704 |  |  | 2015-03-31
AZ_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
AZ_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
AZ_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
AZ_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | NO | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
AZ_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | NO | NO | NO | NO | NO | NO | YES | YES |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
AZ_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
AZ_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 109.8948 | 96.0321 | 93.4527 | 87.8568 | 93.532 | 85.0501 | 96.1996 | 86.2071 |  |  | 2015-03-31
AZ_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5147 | 2.254 | 1.9946 | 1.9111 | 1.717 | 1.6251 | 1.7559 | 1.6487 |  |  | 2015-03-31
AZ_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.6013 | 5.9748 | 5.3674 | 5.2465 | 4.7105 | 4.5568 | 4.7981 | 4.6201 |  |  | 2015-03-31
AZ_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9894 | 2.745 | 2.7661 | 2.6628 | 2.4868 | 2.3678 | 2.5268 | 2.3992 |  |  | 2015-03-31
AZ_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.8222 | 4.7036 | 4.2538 | 4.2129 | 3.963 | 3.9262 | 4.0333 | 3.9927 |  |  | 2015-03-31
AZ_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 868.7408 | 762.7968 | 805.1744 | 762.7968 | 762.7968 | 720.4192 | 783.9856 | 720.4192 |  |  | 2015-03-31
AZ_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1991.7472 | 1801.048 | 1928.1808 | 1864.6144 | 1906.992 | 1822.2368 | 1906.992 | 1822.2368 |  |  | 2015-03-31
AZ_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 889.9296 | 826.3632 | 889.9296 | 847.552 | 911.1184 | 847.552 | 911.1184 | 847.552 |  |  | 2015-03-31
AZ_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1652.7264 | 1610.3488 | 1716.2928 | 1695.104 | 1779.8592 | 1758.6704 | 1779.8592 | 1758.6704 |  |  | 2015-03-31
AZ_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  | 2015-03-31
AZ_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  | 2015-03-31
AZ_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  | 2015-03-31
AZ_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  | 2015-03-31
AZ_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
AZ_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
AZ_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
AZ_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | No | No | No | No | No | No |  |  | 2015-03-31
AZ_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.3917 | 1.2563 | 1.3477 | 1.3024 | 1.3329 | 1.2811 | 1.335 | 1.2765 |  |  | 2015-03-31
AZ_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.1611 | 1.1293 | 1.2034 | 1.1898 | 1.2462 | 1.2327 | 1.2422 | 1.2271 |  |  | 2015-03-31
AZ_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.81574 | 0.74641 | 0.58163 | 0.55142 | 0.53271 | 0.52784 | 0.53272 | 0.51658 |  |  | 2015-03-31
AZ_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.81246 | 0.74346 | 0.57749 | 0.54816 | 0.52668 | 0.52208 | 0.52668 | 0.51098 |  |  | 2015-03-31
AZ_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 1.1035 | 0.92234 | 0.72886 | 0.68576 | 0.67113 | 0.67621 | 0.66757 | 0.65752 |  |  | 2015-03-31
AZ_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.3049 | 1.1159 | 0.94256 | 0.87986 | 0.92689 | 0.9236 | 0.93373 | 0.90644 |  |  | 2015-03-31
AZ_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.91094 | 0.74144 | 0.57048 | 0.53899 | 0.52183 | 0.51132 | 0.52465 | 0.50276 |  |  | 2015-03-31
AZ_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.92395 | 0.74302 | 0.61552 | 0.58261 | 0.52526 | 0.51705 | 0.53081 | 0.51424 |  |  | 2015-03-31
AZ_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.3484 | 1.1254 | 0.9505 | 0.88547 | 0.93335 | 0.92544 | 0.94331 | 0.91101 |  |  | 2015-03-31
AZ_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.9026 | 1.7457 | 1.5078 | 1.4422 | 1.4912 | 1.4676 | 1.5158 | 1.4666 |  |  | 2015-03-31
AZ_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.8974 | 1.741 | 1.5012 | 1.4371 | 1.4812 | 1.4582 | 1.5058 | 1.4573 |  |  | 2015-03-31
AZ_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.5847 | 2.2379 | 1.9219 | 1.8104 | 1.9161 | 1.9012 | 1.941 | 1.894 |  |  | 2015-03-31
AZ_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 3.0097 | 2.6086 | 2.3725 | 2.2204 | 2.4677 | 2.4339 | 2.5165 | 2.4303 |  |  | 2015-03-31
AZ_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 2.1277 | 1.77 | 1.5505 | 1.4348 | 1.485 | 1.4471 | 1.5197 | 1.4626 |  |  | 2015-03-31
AZ_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 2.132 | 1.886 | 1.5549 | 1.4813 | 1.4759 | 1.4438 | 1.5223 | 1.4682 |  |  | 2015-03-31
AZ_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.7805 | 2.392 | 2.0766 | 1.9484 | 2.0469 | 2.0112 | 2.1171 | 2.0374 |  |  | 2015-03-31
AZ_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 3.106 | 2.6529 | 2.4031 | 2.2437 | 2.4968 | 2.4505 | 2.5555 | 2.4572 |  |  | 2015-03-31
AZ_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.4687 | 2.3005 | 2.2851 | 2.2195 | 2.3435 | 2.372 | 2.3391 | 2.3408 |  |  | 2015-03-31
AZ_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.2791 | 1.1553 | 1.0263 | 0.95001 | 1.06 | 0.95709 | 1.0931 | 0.96494 |  |  | 2015-03-31
AZ_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.2731 | 1.1499 | 1.0191 | 0.94431 | 1.0592 | 0.94675 | 1.0918 | 0.95452 |  |  | 2015-03-31
AZ_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.6361 | 1.501 | 1.289 | 1.1766 | 1.3402 | 1.2004 | 1.3852 | 1.2132 |  |  | 2015-03-31
AZ_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.9388 | 1.6463 | 1.5406 | 1.4078 | 1.6598 | 1.5437 | 1.7011 | 1.5502 |  |  | 2015-03-31
AZ_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.4895 | 1.2978 | 1.127 | 1.0238 | 1.1993 | 1.0514 | 1.2401 | 1.0735 |  |  | 2015-03-31
AZ_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.4919 | 1.2995 | 1.13 | 1.0263 | 1.2032 | 1.0553 | 1.2434 | 1.0774 |  |  | 2015-03-31
AZ_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.858 | 1.6134 | 1.4237 | 1.2974 | 1.4974 | 1.3468 | 1.5496 | 1.3717 |  |  | 2015-03-31
AZ_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 2.0059 | 1.7103 | 1.5753 | 1.4345 | 1.6968 | 1.5638 | 1.7496 | 1.5805 |  |  | 2015-03-31
AZ_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
AZ_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  | 2015-03-31
AZ_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
AZ_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
AZ_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
AZ_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
AZ_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
AZ_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
AZ_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
AZ_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
AZ_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  | 2015-03-31
AZ_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
AZ_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 296.6432 | 254.2656 | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 233.0768 |  |  | 2015-03-31
AZ_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 275.4544 | 254.2656 | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 233.0768 |  |  | 2015-03-31
AZ_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 360.2096 | 317.832 | 317.832 | 296.6432 | 296.6432 | 296.6432 | 296.6432 |  |  | 2015-03-31
AZ_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 444.9648 | 423.776 | 402.5872 | 423.776 | 423.776 | 423.776 | 402.5872 |  |  | 2015-03-31
AZ_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 275.4544 | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 233.0768 | 233.0768 |  |  | 2015-03-31
AZ_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 275.4544 | 254.2656 | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 233.0768 |  |  | 2015-03-31
AZ_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 444.9648 | 423.776 | 402.5872 | 423.776 | 423.776 | 423.776 | 402.5872 |  |  | 2015-03-31
AZ_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 678.0416 | 678.0416 | 656.8528 | 678.0416 | 656.8528 | 678.0416 | 656.8528 |  |  | 2015-03-31
AZ_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 678.0416 | 678.0416 | 656.8528 | 656.8528 | 656.8528 | 678.0416 | 656.8528 |  |  | 2015-03-31
AZ_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 889.9296 | 868.7408 | 805.1744 | 868.7408 | 847.552 | 868.7408 | 847.552 |  |  | 2015-03-31
AZ_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1207.7616 | 1059.44 | 1059.44 | 995.8736 | 1101.8176 | 1101.8176 | 1123.0064 | 1101.8176 |  |  | 2015-03-31
AZ_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 678.0416 | 678.0416 | 635.664 | 678.0416 | 656.8528 | 678.0416 | 656.8528 |  |  | 2015-03-31
AZ_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 678.0416 | 678.0416 | 656.8528 | 656.8528 | 656.8528 | 678.0416 | 656.8528 |  |  | 2015-03-31
AZ_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 1101.8176 | 932.3072 | 932.3072 | 868.7408 | 911.1184 | 911.1184 | 953.496 | 911.1184 |  |  | 2015-03-31
AZ_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1228.9504 | 1059.44 | 1080.6288 | 1017.0624 | 1123.0064 | 1101.8176 | 1144.1952 | 1101.8176 |  |  | 2015-03-31
AZ_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 1101.8176 | 1038.2512 | 1038.2512 | 995.8736 | 1059.44 | 1059.44 | 1059.44 | 1059.44 |  |  | 2015-03-31
AZ_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 466.1536 | 423.776 | 487.3424 | 423.776 | 487.3424 | 444.9648 |  |  | 2015-03-31
AZ_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 466.1536 | 423.776 | 487.3424 | 423.776 | 487.3424 | 423.776 |  |  | 2015-03-31
AZ_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 572.0976 | 572.0976 | 529.72 | 593.2864 | 550.9088 | 614.4752 | 550.9088 |  |  | 2015-03-31
AZ_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 678.0416 | 699.2304 | 635.664 | 741.608 | 699.2304 | 762.7968 | 699.2304 |  |  | 2015-03-31
AZ_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 487.3424 | 508.5312 | 466.1536 | 529.72 | 466.1536 | 550.9088 | 487.3424 |  |  | 2015-03-31
AZ_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 487.3424 | 508.5312 | 466.1536 | 550.9088 | 466.1536 | 550.9088 | 487.3424 |  |  | 2015-03-31
AZ_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 614.4752 | 635.664 | 593.2864 | 678.0416 | 614.4752 | 699.2304 | 614.4752 |  |  | 2015-03-31
AZ_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 678.0416 | 699.2304 | 635.664 | 762.7968 | 699.2304 | 783.9856 | 720.4192 |  |  | 2015-03-31
AZ_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
AZ_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.22329 | 0.20366 | 0.18561 | 0.17597 | 0.17 | 0.16845 | 0.17 | 0.16485 |  |  | 2015-03-31
AZ_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.22227 | 0.20274 | 0.1843 | 0.17494 | 0.16807 | 0.16661 | 0.16807 | 0.16307 |  |  | 2015-03-31
AZ_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.31226 | 0.25726 | 0.2326 | 0.21884 | 0.21417 | 0.2158 | 0.21303 | 0.20983 |  |  | 2015-03-31
AZ_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.36906 | 0.31262 | 0.30079 | 0.28078 | 0.29579 | 0.29474 | 0.29798 | 0.28927 |  |  | 2015-03-31
AZ_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.23149 | 0.20008 | 0.18206 | 0.172 | 0.16653 | 0.16318 | 0.16743 | 0.16044 |  |  | 2015-03-31
AZ_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.23535 | 0.20262 | 0.18583 | 0.17464 | 0.16763 | 0.165 | 0.1694 | 0.1641 |  |  | 2015-03-31
AZ_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.3722 | 0.31223 | 0.30333 | 0.28258 | 0.29785 | 0.29533 | 0.30103 | 0.29072 |  |  | 2015-03-31
AZ_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.52713 | 0.48312 | 0.48116 | 0.46025 | 0.47589 | 0.46834 | 0.48375 | 0.46803 |  |  | 2015-03-31
AZ_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.52553 | 0.48164 | 0.47908 | 0.45862 | 0.47267 | 0.46535 | 0.48053 | 0.46507 |  |  | 2015-03-31
AZ_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.74417 | 0.62875 | 0.61332 | 0.57774 | 0.61147 | 0.60671 | 0.61943 | 0.60441 |  |  | 2015-03-31
AZ_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.86339 | 0.74373 | 0.75713 | 0.70858 | 0.7875 | 0.77672 | 0.80306 | 0.77557 |  |  | 2015-03-31
AZ_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.5545 | 0.48144 | 0.48231 | 0.45789 | 0.47389 | 0.46179 | 0.48498 | 0.46676 |  |  | 2015-03-31
AZ_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.55579 | 0.48062 | 0.48383 | 0.45876 | 0.47101 | 0.46075 | 0.48581 | 0.46853 |  |  | 2015-03-31
AZ_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.78715 | 0.66251 | 0.66269 | 0.62176 | 0.65323 | 0.64181 | 0.67561 | 0.65018 |  |  | 2015-03-31
AZ_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.87309 | 0.7483 | 0.76689 | 0.71603 | 0.79681 | 0.78202 | 0.8155 | 0.78415 |  |  | 2015-03-31
AZ_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.78782 | 0.73416 | 0.72923 | 0.7083 | 0.74787 | 0.75697 | 0.74647 | 0.747 |  |  | 2015-03-31
AZ_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.3636 | 0.32508 | 0.3275 | 0.30316 | 0.33827 | 0.30543 | 0.34881 | 0.30794 |  |  | 2015-03-31
AZ_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.36174 | 0.32339 | 0.32522 | 0.30135 | 0.338 | 0.30213 | 0.34842 | 0.30461 |  |  | 2015-03-31
AZ_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.47012 | 0.4074 | 0.41135 | 0.37549 | 0.42769 | 0.38308 | 0.44205 | 0.38715 |  |  | 2015-03-31
AZ_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.55493 | 0.47361 | 0.49163 | 0.44926 | 0.52966 | 0.49264 | 0.54286 | 0.49469 |  |  | 2015-03-31
AZ_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.40298 | 0.34597 | 0.35966 | 0.32671 | 0.38274 | 0.33551 | 0.39575 | 0.34256 |  |  | 2015-03-31
AZ_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.4037 | 0.34649 | 0.36059 | 0.3275 | 0.38397 | 0.33678 | 0.39681 | 0.34381 |  |  | 2015-03-31
AZ_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.51373 | 0.4409 | 0.45435 | 0.41403 | 0.47787 | 0.42978 | 0.4945 | 0.43774 |  |  | 2015-03-31
AZ_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.5698 | 0.48274 | 0.50271 | 0.45778 | 0.54148 | 0.49905 | 0.55835 | 0.50437 |  |  | 2015-03-31
CA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7337 | 1.686 | 1.3671 | 1.3092 | 1.2529 | 1.1948 | 1.6449 | 1.5227 | 1.2359 | 1.1652 | 2015-03-31
CA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.1191 | 1.9103 | 1.5755 | 1.4674 | 1.624 | 1.5014 | 1.8374 | 1.6766 | 1.6792 | 1.5849 | 2015-03-31
CA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.7304 | 1.4121 | 1.2582 | 1.1288 | 1.2054 | 1.0697 | 1.4355 | 1.3548 | 1.2348 | 1.2027 | 2015-03-31
CA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 2.0102 | 1.8491 | 1.3081 | 1.2406 | 1.167 | 1.1012 | 1.6887 | 1.5561 | 1.0306 | 0.98405 | 2015-03-31
CA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 2.0073 | 1.6618 | 1.4056 | 1.273 | 1.3708 | 1.2327 | 1.7441 | 1.6072 | 1.381 | 1.3193 | 2015-03-31
CA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 741.608 | 720.4192 | 614.4752 | 593.2864 | 572.0976 | 529.72 | 635.664 | 572.0976 | 550.9088 | 529.72 | 2015-03-31
CA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 953.496 | 847.552 | 699.2304 | 656.8528 | 741.608 | 678.0416 | 741.608 | 678.0416 | 762.7968 | 720.4192 | 2015-03-31
CA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 783.9856 | 635.664 | 572.0976 | 508.5312 | 550.9088 | 487.3424 | 635.664 | 614.4752 | 550.9088 | 550.9088 | 2015-03-31
CA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 911.1184 | 826.3632 | 593.2864 | 550.9088 | 529.72 | 487.3424 | 699.2304 | 614.4752 | 466.1536 | 444.9648 | 2015-03-31
CA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 911.1184 | 741.608 | 635.664 | 572.0976 | 614.4752 | 550.9088 | 783.9856 | 720.4192 | 614.4752 | 593.2864 | 2015-03-31
CA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 2015-03-31
CA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2015-03-31
CA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2015-03-31
CA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 2015-03-31
CA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 2015-03-31
CA_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2015-03-31
CA_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2015-03-31
CA_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2015-03-31
CA_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2015-03-31
CA_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2015-03-31
CA_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.52476 | 0.5077 | 0.43626 | 0.4178 | 0.39984 | 0.38129 | 0.45036 | 0.41073 | 0.39441 | 0.37184 | 2015-03-31
CA_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.67625 | 0.60582 | 0.50276 | 0.46828 | 0.51826 | 0.47915 | 0.53044 | 0.47451 | 0.53589 | 0.50579 | 2015-03-31
CA_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.55221 | 0.45065 | 0.40152 | 0.36023 | 0.38469 | 0.34137 | 0.45809 | 0.43235 | 0.39405 | 0.3838 | 2015-03-31
CA_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.63961 | 0.58379 | 0.41746 | 0.3959 | 0.37243 | 0.3514 | 0.48907 | 0.44258 | 0.32889 | 0.31403 | 2015-03-31
CA_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.64058 | 0.53032 | 0.44856 | 0.40624 | 0.43745 | 0.39338 | 0.55659 | 0.51291 | 0.44073 | 0.42104 | 2015-03-31
CA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11865.728 | 11463.1408 | 10573.2112 | 10191.8128 | 9683.2816 | 9301.8832 | 10340.1344 | 9746.848 | 9895.1696 | 9450.2048 | 2015-03-31
CA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 28287.048 | 26274.112 | 23625.512 | 22672.016 | 22968.6592 | 21930.408 | 24515.4416 | 24134.0432 | 22862.7152 | 22587.2608 | 2015-03-31
CA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 227440.5795 | 210256.4627 | 186821.6499 | 176672.2147 | 181037.1075 | 170167.2531 | 198750.9443 | 194873.3939 | 179087.7379 | 176184.8723 | 2015-03-31
CA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 26507.1888 | 23689.0784 | 19938.6608 | 18413.0672 | 19557.2624 | 18031.6688 | 24028.0992 | 22036.352 | 20129.36 | 18942.7872 | 2015-03-31
CA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2015-03-31
CA_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2015-03-31
CA_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2015-03-31
CA_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2015-03-31
CA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2015-03-31
CA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 2015-03-31
CA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 2015-03-31
CA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 2015-03-31
CA_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 2015-03-31
CA_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 2015-03-31
CA_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 2015-03-31
CA_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 2015-03-31
CA_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
CA_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
CA_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
CA_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
CA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 336.9574 | 319.2817 | 283.9537 | 271.8716 | 242.9346 | 229.7811 | 365.9863 | 360.1414 | 208.6287 | 204.1321 | 2015-03-31
CA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 336.9574 | 319.2817 | 283.9537 | 271.8716 | 242.9346 | 229.7811 | 365.9863 | 360.1414 | 208.6287 | 204.1321 | 2015-03-31
CA_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Screw | Screw | Centrifugal | Centrifugal | Screw | Screw | 2015-03-31
CA_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Screw | Screw | Centrifugal | Centrifugal | Screw | Screw | 2015-03-31
CA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 319.8198 | 303.0422 | 269.5135 | 258.0417 | 230.5862 | 218.0957 | 347.3811 | 341.8239 | 198.0234 | 193.7496 | 2015-03-31
CA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 319.8198 | 303.0422 | 269.5135 | 258.0417 | 230.5862 | 218.0957 | 347.3811 | 341.8239 | 198.0234 | 193.7496 | 2015-03-31
CA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.6091 | 3.4507 | 2.8799 | 2.8361 | 3.1366 | 3.0806 | 3.5723 | 3.5081 | 3.5299 | 3.4547 | 2015-03-31
CA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2015-03-31
CA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1586.7758 | 751.738 | 1337.1206 | 640.1121 | 1143.9638 | 541.0127 | 1723.4056 | 847.9416 | 982.4189 | 480.623 | 2015-03-31
CA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 751.738 | 0 | 640.1121 | 0 | 541.0127 | 0 | 847.9416 | 0 | 480.623 | 2015-03-31
CA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1586.7758 | 1503.4776 | 1337.1206 | 1280.2258 | 1143.9638 | 1082.0239 | 1723.4056 | 1695.8261 | 982.4189 | 961.2444 | 2015-03-31
CA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 725.7467 | 693.8939 | 579.0995 | 570.2994 | 630.7208 | 619.475 | 718.3477 | 705.4377 | 709.8123 | 694.7006 | 2015-03-31
CA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1851.3177 | 1747.4981 | 1582.2347 | 1506.4781 | 1368.8593 | 1288.4442 | 2010.772 | 1971.1462 | 1175.5567 | 1144.6232 | 2015-03-31
CA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | 2015-03-31
CA_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 12.7291 | 12.3107 | 11.3359 | 10.9336 | 10.3862 | 9.9843 | 11.0945 | 10.4585 | 10.6095 | 10.135 | 2015-03-31
CA_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 40.5102 | 35.733 | 33.9675 | 30.8412 | 33.0072 | 29.8207 | 35.2425 | 32.823 | 32.8619 | 30.7224 | 2015-03-31
CA_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 319.853 | 279.7726 | 262.7383 | 248.4546 | 254.5991 | 226.439 | 279.4891 | 274.0468 | 251.8381 | 247.7709 | 2015-03-31
CA_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 38.1056 | 32.2175 | 28.809 | 25.1848 | 28.2598 | 24.656 | 34.5446 | 29.9697 | 29.0904 | 25.9093 | 2015-03-31
CA_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 47.0169 | 46.9311 | 42.9923 | 42.9109 | 42.3795 | 42.297 | 42.8048 | 42.6148 | 42.7646 | 42.6416 | 2015-03-31
CA_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.84372 | 0.83656 | 0.76332 | 0.75718 | 0.76387 | 0.74816 | 0.81934 | 0.80178 | 0.82143 | 0.80272 | 2015-03-31
CA_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.371 | 10.2719 | 9.4516 | 9.2967 | 9.5446 | 9.1837 | 10.3686 | 10.0952 | 10.3628 | 10.0714 | 2015-03-31
CA_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.6974 | 0.68242 | 0.6355 | 0.60711 | 0.63969 | 0.60546 | 0.7151 | 0.68793 | 0.69966 | 0.67583 | 2015-03-31
CA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 8.5597 | 4.0554 | 7.2133 | 3.4532 | 6.1713 | 2.9186 | 9.2972 | 4.5743 | 5.2998 | 2.5928 | 2015-03-31
CA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.0554 | 0 | 3.4532 | 0 | 2.9186 | 0 | 4.5743 | 0 | 2.5928 | 2015-03-31
CA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 25.6792 | 24.3322 | 21.6399 | 20.7191 | 18.5138 | 17.5114 | 27.8915 | 27.4461 | 15.8994 | 15.5567 | 2015-03-31
CA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.6874 | 14.9989 | 12.5176 | 12.3273 | 13.6334 | 13.3903 | 15.5275 | 15.2484 | 15.343 | 15.0163 | 2015-03-31
CA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 34.289 | 32.3666 | 29.3053 | 27.9022 | 25.3533 | 23.8639 | 37.243 | 36.5086 | 21.7731 | 21.2001 | 2015-03-31
CA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8461 | 3.8322 | 3.8821 | 3.8557 | 3.6888 | 3.6536 | 4.0051 | 3.9678 | 3.7443 | 3.7121 | 2015-03-31
CA_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | 2015-03-31
CA_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | 2015-03-31
CA_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | NO | YES | NO | NO | YES | YES | YES | YES | 2015-03-31
CA_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO | NO | NO | NO | NO | 2015-03-31
CA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4291.9853 | 4013.075 | 3577.9549 | 3509.6086 | 3709.9401 | 3683.0669 | 4039.2521 | 3954.5171 | 3895.0128 | 3812.2235 | 2015-03-31
CA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.781 | 8.7031 | 7.7519 | 7.7559 | 6.1408 | 6.1399 | 8.4146 | 8.3277 | 6.3305 | 6.3665 | 2015-03-31
CA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 31.2981 | 29.1118 | 31.2716 | 30.6972 | 25.1308 | 27.9443 | 42.3521 | 33.0938 | 25.3983 | 25.0025 | 2015-03-31
CA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.5506 | 5.9724 | 5.069 | 4.7912 | 5.1244 | 4.7804 | 6.6858 | 6.376 | 5.3191 | 5.1765 | 2015-03-31
CA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.694 | 5.021 | 4.2704 | 3.9215 | 4.2017 | 3.7795 | 5.7948 | 5.4239 | 4.3431 | 4.1206 | 2015-03-31
CA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3962.3056 | 3919.928 | 3008.8096 | 2987.6208 | 2669.7888 | 2669.7888 | 3263.0752 | 3220.6976 | 2351.9568 | 2373.1456 | 2015-03-31
CA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14090.552 | 13094.6784 | 12119.9936 | 11399.5744 | 11314.8192 | 8793.352 | 13433.6992 | 11886.9168 | 11441.952 | 8496.7088 | 2015-03-31
CA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2881.6768 | 2585.0336 | 2288.3904 | 2140.0688 | 2309.5792 | 2161.2576 | 2521.4672 | 2394.3344 | 2394.3344 | 2330.768 | 2015-03-31
CA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2436.712 | 2097.6912 | 1864.6144 | 1695.104 | 1885.8032 | 1695.104 | 2118.88 | 1928.1808 | 1949.3696 | 1864.6144 | 2015-03-31
CA_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD | 2015-03-31
CA_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD | 2015-03-31
CA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 2015-03-31
CA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 2015-03-31
CA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2015-03-31
CA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 2015-03-31
CA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | gravity | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2015-03-31
CA_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | No | No | No | No | DifferentialDryBulb | DifferentialDryBulb | No | No | 2015-03-31
CA_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.9839 | 1.8113 | 1.3356 | 0.65388 | 1.6417 | 0.8935 | 2.0522 | 1.1979 | 2.0839 | 1.2219 | 2015-03-31
CA_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.677 | 2.6532 | 2.0307 | 2.0914 | 1.8763 | 1.8748 | 2.2046 | 2.1741 | 1.6432 | 1.6648 | 2015-03-31
CA_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 15.0225 | 14.0639 | 13.0152 | 12.2399 | 12.1407 | 9.515 | 14.4131 | 12.7679 | 12.2699 | 9.1952 | 2015-03-31
CA_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 2.0208 | 1.8055 | 1.5988 | 1.4975 | 1.6164 | 1.5079 | 1.7733 | 1.6773 | 1.6778 | 1.6329 | 2015-03-31
CA_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.7135 | 1.473 | 1.3084 | 1.1823 | 1.3253 | 1.1922 | 1.4797 | 1.3584 | 1.37 | 1.2998 | 2015-03-31
CA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 28.9175 | 24.5519 | 19.9742 | 17.8808 | 14.4179 | 13.0413 | 26.9693 | 23.0025 | 14.9153 | 13.7351 | 2015-03-31
CA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 28.6063 | 24.5153 | 19.7066 | 17.88 | 14.2737 | 13.0819 | 26.7133 | 23.0079 | 14.719 | 13.5602 | 2015-03-31
CA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 25.5029 | 22.2853 | 17.9299 | 16.4398 | 12.9712 | 12.0127 | 23.997 | 21.3061 | 13.3605 | 12.6848 | 2015-03-31
CA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 28.5996 | 24.7569 | 20.8908 | 19.4431 | 17.0203 | 15.3247 | 33.2952 | 28.4475 | 17.639 | 15.6677 | 2015-03-31
CA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.0413 | 7.9601 | 6.7878 | 6.8184 | 5.8642 | 5.8717 | 8.8203 | 8.7446 | 5.9895 | 5.9916 | 2015-03-31
CA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.3654 | 5.488 | 4.5474 | 4.1568 | 3.448 | 3.0317 | 6.7076 | 5.6266 | 3.5433 | 3.1354 | 2015-03-31
CA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.4518 | 10.4518 | 9.6124 | 9.6124 | 7.0043 | 7.0043 | 10.5074 | 10.5074 | 7.0043 | 7.0043 | 2015-03-31
CA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 9534.96 | 7585.5904 | 6526.1504 | 5848.1088 | 6483.7728 | 5869.2976 | 8094.1216 | 6907.5488 | 6716.8496 | 6187.1296 | 2015-03-31
CA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 9407.8272 | 7585.5904 | 6441.3952 | 5848.1088 | 6420.2064 | 5890.4864 | 8009.3664 | 6907.5488 | 6632.0944 | 6102.3744 | 2015-03-31
CA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 8517.8976 | 6949.9264 | 5869.2976 | 5381.9552 | 5848.1088 | 5403.144 | 7204.192 | 6399.0176 | 6017.6192 | 5699.7872 | 2015-03-31
CA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 11420.7632 | 9429.016 | 7924.6112 | 7161.8144 | 7670.3456 | 6907.5488 | 10001.1136 | 8539.0864 | 7945.8 | 7055.8704 | 2015-03-31
CA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3135.9424 | 3093.5648 | 2690.9776 | 2690.9776 | 2648.6 | 2648.6 | 2860.488 | 2818.1104 | 2690.9776 | 2690.9776 | 2015-03-31
CA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2224.824 | 1843.4256 | 1610.3488 | 1440.8384 | 1546.7824 | 1356.0832 | 2012.936 | 1695.104 | 1589.16 | 1419.6496 | 2015-03-31
CA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 2015-03-31
CA_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | n/a | n/a | n/a | VFD | n/a | n/a | 2015-03-31
CA_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD | 2015-03-31
CA_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | n/a | VFD | VFD | VFD | n/a | VFD | 2015-03-31
CA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2015-03-31
CA_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 2015-03-31
CA_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | Yes | No | Yes | No | Yes | No | Yes | 2015-03-31
CA_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | Yes | No | Yes | No | Yes | No | Yes | 2015-03-31
CA_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | Yes | No | Yes | No | Yes | No | Yes | 2015-03-31
CA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7589.4468 | 6531.7866 | 5847.2401 | 6490.4049 | 5870.6961 | 7852.8447 | 6902.6754 | 6714.307 | 6183.0402 | 2015-03-31
CA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7578.132 | 6444.2769 | 5846.9646 | 6425.4824 | 5888.982 | 7852.8447 | 6904.3069 | 6625.9497 | 6104.3026 | 2015-03-31
CA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6777.6191 | 5863.28 | 5376.0012 | 5839.1459 | 5407.6572 | 6777.6191 | 6393.5933 | 6014.4197 | 5710.1909 | 2015-03-31
CA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 2015-03-31
CA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 2015-03-31
CA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 2015-03-31
CA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 2015-03-31
CA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | gravity | gravity | gravity | motorized | motorized | motorized | motorized | 2015-03-31
CA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | No | No | No | DifferentialDryBulb | DifferentialDryBulb | No | No | 2015-03-31
CA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | 2015-03-31
CA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | 2015-03-31
CA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | 2015-03-31
CA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | No | Yes | No | Yes | No | Yes | No | 2015-03-31
CA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 2015-03-31
CA_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no | no | no | no | no | 2015-03-31
CA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.3064 | 1.1249 | 1.0429 | 1.024 | 1.0908 | 1.0694 | 1.2802 | 1.1934 | 1.1706 | 1.1285 | 2015-03-31
CA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 131.3538 | 113.096 | 104.8603 | 102.9593 | 109.6749 | 107.5178 | 128.7149 | 119.9871 | 117.6937 | 113.4668 | 2015-03-31
CA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 13.9741 | 11.1119 | 9.6363 | 8.6264 | 9.5753 | 8.661 | 11.8492 | 10.1064 | 9.9056 | 9.1218 | 2015-03-31
CA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 13.7629 | 11.0953 | 9.5073 | 8.626 | 9.4795 | 8.688 | 11.7368 | 10.1088 | 9.7753 | 9.0057 | 2015-03-31
CA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 12.4639 | 10.168 | 8.6501 | 7.9312 | 8.6145 | 7.9779 | 10.5433 | 9.4325 | 8.8731 | 8.4243 | 2015-03-31
CA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 16.6013 | 13.7934 | 11.6026 | 10.4816 | 11.218 | 10.1004 | 14.6285 | 12.4987 | 11.6257 | 10.3265 | 2015-03-31
CA_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.1247 | 2.0891 | 1.8785 | 1.8795 | 1.8498 | 1.8521 | 1.999 | 1.968 | 1.8893 | 1.89 | 2015-03-31
CA_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.5579 | 1.2933 | 1.1323 | 1.0158 | 1.0876 | 0.96747 | 1.4104 | 1.1831 | 1.1177 | 1.0006 | 2015-03-31
CA_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2015-03-31
CA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8393 | 2.4446 | 2.2666 | 2.2255 | 2.3707 | 2.3241 | 2.7822 | 2.5936 | 2.544 | 2.4526 | 2015-03-31
CA_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
CA_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
CA_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
CA_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
CA_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | NO | NO | YES | YES | NO | NO | YES | YES | YES | YES | 2015-03-31
CA_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
CA_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES | YES | YES | 2015-03-31
CA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.1867 | 91.0565 | 95.5769 | 94.5551 | 95.6508 | 94.7417 | 102.9973 | 97.7945 | 96.2724 | 93.8071 | 2015-03-31
CA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2953 | 2.0643 | 1.5427 | 1.4667 | 1.4946 | 1.4154 | 1.9624 | 1.8747 | 1.3636 | 1.271 | 2015-03-31
CA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.0283 | 5.5781 | 4.0491 | 3.9213 | 3.7892 | 3.6827 | 5.3413 | 5.1643 | 3.0952 | 2.9617 | 2015-03-31
CA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 3.0258 | 2.841 | 2.1098 | 2.066 | 1.9676 | 1.9258 | 2.5338 | 2.4155 | 1.6445 | 1.5691 | 2015-03-31
CA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5398 | 4.4361 | 3.4733 | 3.4371 | 3.3543 | 3.3162 | 4.2523 | 4.2182 | 3.202 | 3.1731 | 2015-03-31
CA_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 868.7408 | 783.9856 | 656.8528 | 614.4752 | 656.8528 | 614.4752 | 678.0416 | 635.664 | 614.4752 | 572.0976 | 2015-03-31
CA_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 2034.1248 | 1843.4256 | 1525.5936 | 1483.216 | 1504.4048 | 1440.8384 | 1610.3488 | 1546.7824 | 1398.4608 | 1334.8944 | 2015-03-31
CA_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 932.3072 | 847.552 | 741.608 | 720.4192 | 699.2304 | 699.2304 | 762.7968 | 720.4192 | 678.0416 | 635.664 | 2015-03-31
CA_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1716.2928 | 1673.9152 | 1462.0272 | 1440.8384 | 1440.8384 | 1419.6496 | 1504.4048 | 1483.216 | 1440.8384 | 1419.6496 | 2015-03-31
CA_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 2015-03-31
CA_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 2015-03-31
CA_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 2015-03-31
CA_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 2015-03-31
CA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized | 2015-03-31
CA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | No | No | No | No | DifferentialDryBulb | DifferentialDryBulb | No | No | 2015-03-31
CA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | No | No | No | No | No | No | No | No | No | 2015-03-31
CA_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.4288 | 1.2973 | 1.0741 | 1.0462 | 1.0502 | 1.0245 | 1.1231 | 1.0859 | 0.98776 | 0.94514 | 2015-03-31
CA_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.2048 | 1.1756 | 1.0399 | 1.0274 | 1.0268 | 1.0135 | 1.0523 | 1.054 | 1.0218 | 1.0126 | 2015-03-31
CA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.69255 | 0.63716 | 0.36282 | 0.34238 | 0.30284 | 0.29302 | 0.54785 | 0.54357 | 0.24939 | 0.24926 | 2015-03-31
CA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.68933 | 0.6342 | 0.3596 | 0.33983 | 0.29946 | 0.29038 | 0.54229 | 0.53828 | 0.2451 | 0.2452 | 2015-03-31
CA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.92861 | 0.78802 | 0.49024 | 0.44665 | 0.40595 | 0.3755 | 0.66464 | 0.65759 | 0.33384 | 0.34829 | 2015-03-31
CA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.1438 | 0.97001 | 0.59784 | 0.5474 | 0.55239 | 0.51471 | 0.92337 | 0.92002 | 0.48796 | 0.49531 | 2015-03-31
CA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.7712 | 0.62768 | 0.46985 | 0.43665 | 0.44417 | 0.41826 | 0.63066 | 0.62568 | 0.42626 | 0.4377 | 2015-03-31
CA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.78423 | 0.62777 | 0.48273 | 0.44894 | 0.45908 | 0.43292 | 0.6443 | 0.63937 | 0.44204 | 0.45405 | 2015-03-31
CA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.1804 | 0.97926 | 0.66761 | 0.60885 | 0.6445 | 0.59625 | 0.94273 | 0.93376 | 0.60583 | 0.6175 | 2015-03-31
CA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6523 | 1.5083 | 0.97603 | 0.92268 | 0.93828 | 0.88457 | 1.4354 | 1.4148 | 0.80981 | 0.79698 | 2015-03-31
CA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6472 | 1.5194 | 0.97036 | 0.91821 | 0.93219 | 0.87982 | 1.4262 | 1.406 | 0.80144 | 0.7891 | 2015-03-31
CA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2396 | 1.9292 | 1.3078 | 1.1927 | 1.2235 | 1.1035 | 1.7808 | 1.7339 | 1.0841 | 1.092 | 2015-03-31
CA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6749 | 2.303 | 1.5486 | 1.4177 | 1.546 | 1.4092 | 2.3611 | 2.3303 | 1.4259 | 1.4174 | 2015-03-31
CA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8342 | 1.5206 | 1.2225 | 1.1386 | 1.3042 | 1.201 | 1.6726 | 1.638 | 1.297 | 1.2989 | 2015-03-31
CA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8386 | 1.5162 | 1.2272 | 1.1425 | 1.3091 | 1.2052 | 1.6705 | 1.6437 | 1.3037 | 1.3054 | 2015-03-31
CA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3793 | 2.1545 | 1.5643 | 1.4285 | 1.6318 | 1.4796 | 2.1863 | 2.1447 | 1.5942 | 1.5945 | 2015-03-31
CA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.7444 | 2.3235 | 1.7258 | 1.5697 | 1.7888 | 1.6198 | 2.4225 | 2.3767 | 1.7669 | 1.7528 | 2015-03-31
CA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.4649 | 2.2806 | 2.0359 | 1.9367 | 1.9697 | 1.9319 | 2.0863 | 2.0318 | 1.898 | 1.9123 | 2015-03-31
CA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1113 | 1.0027 | 0.63003 | 0.56906 | 0.58211 | 0.53199 | 1.094 | 0.91772 | 0.51312 | 0.4606 | 2015-03-31
CA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1053 | 0.9973 | 0.63087 | 0.56988 | 0.58193 | 0.52629 | 1.0929 | 0.90782 | 0.51413 | 0.45157 | 2015-03-31
CA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4902 | 1.3095 | 0.80095 | 0.71438 | 0.73395 | 0.65173 | 1.352 | 1.2085 | 0.65353 | 0.62957 | 2015-03-31
CA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.7227 | 1.4642 | 0.98404 | 0.87966 | 0.95604 | 0.85444 | 1.5634 | 1.4506 | 0.89163 | 0.85281 | 2015-03-31
CA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2961 | 1.1296 | 0.84823 | 0.7578 | 0.8794 | 0.78594 | 1.2821 | 1.141 | 0.91386 | 0.84991 | 2015-03-31
CA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2986 | 1.1314 | 0.85184 | 0.76099 | 0.88283 | 0.789 | 1.2851 | 1.1449 | 0.91867 | 0.85472 | 2015-03-31
CA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6213 | 1.4082 | 1.0181 | 0.90605 | 1.0444 | 0.92813 | 1.5439 | 1.3987 | 1.0541 | 0.99499 | 2015-03-31
CA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7686 | 1.513 | 1.1102 | 0.98896 | 1.1328 | 1.0085 | 1.6678 | 1.5294 | 1.1351 | 1.0779 | 2015-03-31
CA_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | 2015-03-31
CA_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 2015-03-31
CA_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
CA_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
CA_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
CA_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
CA_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
CA_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
CA_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
CA_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 2015-03-31
CA_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 2015-03-31
CA_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 2015-03-31
CA_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 275.4544 | 169.5104 | 148.3216 | 127.1328 | 127.1328 | 211.888 | 211.888 | 105.944 | 105.944 | 2015-03-31
CA_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 275.4544 | 169.5104 | 148.3216 | 127.1328 | 127.1328 | 211.888 | 211.888 | 105.944 | 105.944 | 2015-03-31
CA_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 339.0208 | 211.888 | 190.6992 | 190.6992 | 169.5104 | 275.4544 | 254.2656 | 148.3216 | 148.3216 | 2015-03-31
CA_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 423.776 | 275.4544 | 254.2656 | 254.2656 | 233.0768 | 381.3984 | 381.3984 | 211.888 | 233.0768 | 2015-03-31
CA_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 275.4544 | 211.888 | 190.6992 | 190.6992 | 190.6992 | 211.888 | 211.888 | 190.6992 | 190.6992 | 2015-03-31
CA_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 275.4544 | 211.888 | 190.6992 | 211.888 | 190.6992 | 233.0768 | 233.0768 | 190.6992 | 211.888 | 2015-03-31
CA_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 423.776 | 296.6432 | 275.4544 | 296.6432 | 275.4544 | 381.3984 | 381.3984 | 275.4544 | 275.4544 | 2015-03-31
CA_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 678.0416 | 444.9648 | 423.776 | 423.776 | 402.5872 | 593.2864 | 572.0976 | 360.2096 | 360.2096 | 2015-03-31
CA_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 678.0416 | 444.9648 | 423.776 | 423.776 | 402.5872 | 593.2864 | 572.0976 | 360.2096 | 360.2096 | 2015-03-31
CA_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 868.7408 | 593.2864 | 529.72 | 550.9088 | 487.3424 | 741.608 | 720.4192 | 487.3424 | 487.3424 | 2015-03-31
CA_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1207.7616 | 1038.2512 | 699.2304 | 635.664 | 699.2304 | 635.664 | 995.8736 | 974.6848 | 635.664 | 635.664 | 2015-03-31
CA_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 656.8528 | 550.9088 | 508.5312 | 593.2864 | 550.9088 | 614.4752 | 614.4752 | 593.2864 | 593.2864 | 2015-03-31
CA_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 656.8528 | 550.9088 | 508.5312 | 593.2864 | 550.9088 | 614.4752 | 614.4752 | 593.2864 | 593.2864 | 2015-03-31
CA_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 911.1184 | 699.2304 | 635.664 | 741.608 | 656.8528 | 847.552 | 826.3632 | 720.4192 | 720.4192 | 2015-03-31
CA_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1207.7616 | 1038.2512 | 783.9856 | 699.2304 | 805.1744 | 720.4192 | 1017.0624 | 995.8736 | 805.1744 | 783.9856 | 2015-03-31
CA_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 1101.8176 | 1017.0624 | 911.1184 | 868.7408 | 889.9296 | 868.7408 | 932.3072 | 911.1184 | 847.552 | 868.7408 | 2015-03-31
CA_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 275.4544 | 254.2656 | 254.2656 | 233.0768 | 423.776 | 381.3984 | 233.0768 | 211.888 | 2015-03-31
CA_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 275.4544 | 254.2656 | 254.2656 | 233.0768 | 423.776 | 381.3984 | 233.0768 | 211.888 | 2015-03-31
CA_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 550.9088 | 360.2096 | 317.832 | 339.0208 | 296.6432 | 529.72 | 466.1536 | 296.6432 | 275.4544 | 2015-03-31
CA_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 656.8528 | 444.9648 | 402.5872 | 423.776 | 381.3984 | 678.0416 | 614.4752 | 402.5872 | 381.3984 | 2015-03-31
CA_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 466.1536 | 381.3984 | 339.0208 | 402.5872 | 360.2096 | 508.5312 | 444.9648 | 402.5872 | 381.3984 | 2015-03-31
CA_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 466.1536 | 381.3984 | 339.0208 | 402.5872 | 360.2096 | 508.5312 | 444.9648 | 423.776 | 381.3984 | 2015-03-31
CA_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 614.4752 | 466.1536 | 402.5872 | 466.1536 | 423.776 | 614.4752 | 550.9088 | 466.1536 | 444.9648 | 2015-03-31
CA_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 678.0416 | 508.5312 | 444.9648 | 508.5312 | 444.9648 | 699.2304 | 635.664 | 508.5312 | 487.3424 | 2015-03-31
CA_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | 2015-03-31
CA_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.21662 | 0.19787 | 0.1138 | 0.1068 | 0.096647 | 0.093509 | 0.15254 | 0.15113 | 0.07959 | 0.079549 | 2015-03-31
CA_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.21553 | 0.19686 | 0.1127 | 0.10594 | 0.095561 | 0.092665 | 0.15072 | 0.14939 | 0.078222 | 0.078249 | 2015-03-31
CA_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.29631 | 0.24781 | 0.15644 | 0.14254 | 0.12954 | 0.11983 | 0.18828 | 0.18596 | 0.10654 | 0.11114 | 2015-03-31
CA_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.36252 | 0.30661 | 0.19079 | 0.17468 | 0.17628 | 0.16426 | 0.26783 | 0.26673 | 0.15572 | 0.15807 | 2015-03-31
CA_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.22048 | 0.19225 | 0.14651 | 0.13509 | 0.14175 | 0.13347 | 0.15568 | 0.15414 | 0.13603 | 0.13968 | 2015-03-31
CA_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.22465 | 0.19468 | 0.15097 | 0.13957 | 0.14651 | 0.13815 | 0.15994 | 0.15843 | 0.14106 | 0.1449 | 2015-03-31
CA_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.36445 | 0.30461 | 0.21305 | 0.1943 | 0.20567 | 0.19028 | 0.27086 | 0.26794 | 0.19334 | 0.19706 | 2015-03-31
CA_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.5203 | 0.47707 | 0.31148 | 0.29445 | 0.29942 | 0.28229 | 0.41688 | 0.41003 | 0.25843 | 0.25434 | 2015-03-31
CA_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.51861 | 0.4755 | 0.30967 | 0.29303 | 0.29748 | 0.28077 | 0.41383 | 0.40712 | 0.25576 | 0.25182 | 2015-03-31
CA_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.71471 | 0.61302 | 0.41735 | 0.38061 | 0.39044 | 0.35214 | 0.52454 | 0.51707 | 0.34596 | 0.34846 | 2015-03-31
CA_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.85364 | 0.73493 | 0.49418 | 0.45241 | 0.49336 | 0.44973 | 0.70323 | 0.69312 | 0.45505 | 0.45233 | 2015-03-31
CA_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.53658 | 0.47126 | 0.39008 | 0.36124 | 0.4162 | 0.38325 | 0.43672 | 0.42826 | 0.41391 | 0.41451 | 2015-03-31
CA_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.53798 | 0.46979 | 0.39165 | 0.36259 | 0.41777 | 0.38462 | 0.43841 | 0.43004 | 0.41603 | 0.41658 | 2015-03-31
CA_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.75418 | 0.64116 | 0.49921 | 0.45588 | 0.52073 | 0.47217 | 0.60141 | 0.58832 | 0.50873 | 0.50885 | 2015-03-31
CA_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.86052 | 0.73602 | 0.55074 | 0.50093 | 0.57083 | 0.51692 | 0.71831 | 0.7033 | 0.56386 | 0.55935 | 2015-03-31
CA_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.7866 | 0.7278 | 0.64968 | 0.61804 | 0.62858 | 0.61652 | 0.66578 | 0.64841 | 0.60569 | 0.61026 | 2015-03-31
CA_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.35463 | 0.31816 | 0.20048 | 0.17955 | 0.18577 | 0.16977 | 0.30025 | 0.26865 | 0.16375 | 0.14699 | 2015-03-31
CA_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.35265 | 0.31635 | 0.20076 | 0.17983 | 0.1857 | 0.16795 | 0.29992 | 0.26539 | 0.16407 | 0.14411 | 2015-03-31
CA_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.45496 | 0.39693 | 0.2556 | 0.22797 | 0.23422 | 0.20798 | 0.37828 | 0.33327 | 0.20856 | 0.20091 | 2015-03-31
CA_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.54755 | 0.46725 | 0.31403 | 0.28072 | 0.3051 | 0.27267 | 0.47374 | 0.43977 | 0.28454 | 0.27215 | 2015-03-31
CA_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.38967 | 0.33626 | 0.27069 | 0.24183 | 0.28064 | 0.25081 | 0.3575 | 0.31325 | 0.29163 | 0.27122 | 2015-03-31
CA_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.39045 | 0.33682 | 0.27184 | 0.24285 | 0.28174 | 0.25179 | 0.35846 | 0.31446 | 0.29317 | 0.27276 | 2015-03-31
CA_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.49709 | 0.42864 | 0.32492 | 0.28914 | 0.3333 | 0.29619 | 0.44034 | 0.39462 | 0.33638 | 0.31753 | 2015-03-31
CA_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.55978 | 0.47596 | 0.3543 | 0.3156 | 0.3615 | 0.32183 | 0.4926 | 0.45085 | 0.36225 | 0.344 | 2015-03-31
AR_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9276 | 1.875 | 1.78 | 1.6741 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9928 | 1.9142 | 1.8702 | 1.7231 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4198 | 1.3136 | 1.4728 | 1.3841 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.9188 | 1.8593 | 1.7687 | 1.6354 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6517 | 1.5401 | 1.702 | 1.5758 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 593.2864 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 699.2304 | 741.608 | 656.8528 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 656.8528 | 614.4752 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 635.664 | 762.7968 | 699.2304 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.45443 | 0.43637 | 0.45809 | 0.41969 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.5192 | 0.49288 | 0.52669 | 0.47129 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.42726 | 0.3876 | 0.47001 | 0.44169 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.49694 | 0.47604 | 0.49287 | 0.44601 | [6 empty] | 2015-03-31
AR_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.48919 | 0.44859 | 0.54315 | 0.50143 | [6 empty] | 2015-03-31
AR_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10594.4 | 10234.1904 | 10763.9104 | 10149.4352 | [6 empty] | 2015-03-31
AR_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24579.008 | 23689.0784 | 25680.8256 | 25257.0496 | [6 empty] | 2015-03-31
AR_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 197924.5811 | 188537.9427 | 208434.2259 | 204069.3331 | [6 empty] | 2015-03-31
AR_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22036.352 | 20489.5696 | 24473.064 | 22481.3168 | [6 empty] | 2015-03-31
AR_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
AR_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
AR_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
AR_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
AR_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
AR_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
AR_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
AR_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
AR_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
AR_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
AR_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
AR_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
AR_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AR_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AR_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AR_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AR_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AR_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AR_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AR_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AR_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AR_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AR_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 426.0844 | 414.6391 | 399.5823 | 393.4911 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 426.0844 | 414.6391 | 399.5823 | 393.4911 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
AR_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 404.4224 | 393.5593 | 379.256 | 373.487 | [6 empty] | 2015-03-31
AR_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 404.4224 | 393.5593 | 379.256 | 373.487 | [6 empty] | 2015-03-31
AR_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.3613 | 4.4032 | 4.8784 | 4.7674 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 2006.3339 | 976.2547 | 1881.5919 | 926.4625 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 976.2547 | 0 | 926.4625 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 2006.3339 | 1952.4428 | 1881.5919 | 1852.9028 | [6 empty] | 2015-03-31
AR_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 876.9936 | 885.4228 | 980.9797 | 958.6624 | [6 empty] | 2015-03-31
AR_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2340.9342 | 2269.4493 | 2195.4283 | 2153.7419 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AR_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.3752 | 10.9767 | 11.5497 | 10.891 | [6 empty] | 2015-03-31
AR_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.3395 | 32.221 | 36.9243 | 34.346 | [6 empty] | 2015-03-31
AR_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 278.343 | 265.133 | 293.1191 | 286.977 | [6 empty] | 2015-03-31
AR_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 31.6825 | 28.0157 | 35.1932 | 30.5929 | [6 empty] | 2015-03-31
AR_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.1251 | 43.0442 | 44.6419 | 44.4454 | [6 empty] | 2015-03-31
AR_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.77204 | 0.76611 | 0.83454 | 0.81904 | [6 empty] | 2015-03-31
AR_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.5522 | 9.4596 | 10.5031 | 10.264 | [6 empty] | 2015-03-31
AR_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.6444 | 0.61987 | 0.72337 | 0.6984 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.8238 | 5.2666 | 10.1506 | 4.9979 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.2666 | 0 | 4.9979 | [6 empty] | 2015-03-31
AR_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.4715 | 31.5993 | 30.4518 | 29.9876 | [6 empty] | 2015-03-31
AR_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.9567 | 19.1389 | 21.2044 | 20.722 | [6 empty] | 2015-03-31
AR_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.3586 | 42.0333 | 40.6617 | 39.8894 | [6 empty] | 2015-03-31
AR_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8496 | 3.8255 | 3.9132 | 3.8805 | [6 empty] | 2015-03-31
AR_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
AR_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
AR_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
AR_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
AR_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4509.0155 | 4589.403 | 4728.5415 | 4582.2089 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.4991 | 9.4385 | 9.0547 | 8.9469 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 41.5018 | 39.7018 | 39.0519 | 37.5239 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.5452 | 6.2904 | 6.5025 | 6.235 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.7035 | 5.3773 | 5.6554 | 5.3228 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3474.9632 | 3432.5856 | 3474.9632 | 3411.3968 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12903.9792 | 11908.1056 | 13327.7552 | 12289.504 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2224.824 | 2563.8448 | 2436.712 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1928.1808 | 1779.8592 | 2118.88 | 1949.3696 | [6 empty] | 2015-03-31
AR_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
AR_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AR_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.7914 | 1.8474 | 3.5629 | 2.3746 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.349 | 2.3208 | 2.3491 | 2.3084 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.845 | 12.7855 | 14.31 | 13.1948 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6398 | 1.5519 | 1.7964 | 1.7024 | [6 empty] | 2015-03-31
AR_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.3507 | 1.24 | 1.4886 | 1.3689 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 24.0998 | 21.1341 | 26.6534 | 22.8169 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 23.7738 | 21.154 | 26.2647 | 22.6912 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 21.4208 | 19.386 | 23.838 | 21.1173 | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.6963 | 26.5526 | 33.292 | 28.3572 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.9969 | 5.3166 | 6.8563 | 5.7983 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7225.3808 | 6335.4512 | 7988.1776 | 6843.9824 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7140.6256 | 6356.64 | 7882.2336 | 6801.6048 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6420.2064 | 5826.92 | 7161.8144 | 6335.4512 | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8920.4848 | 7966.9888 | 9979.9248 | 8517.8976 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1801.048 | 1589.16 | 2055.3136 | 1737.4816 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
AR_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | VFD | [6 empty] | 2015-03-31
AR_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
AR_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
AR_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
AR_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
AR_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
AR_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
AR_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
AR_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7231.9493 | 6341.9774 | 7852.8447 | 6846.97 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7134.1418 | 6347.9738 | 7852.8447 | 6809.2328 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6428.0251 | 5817.4274 | 6777.6191 | 6336.9344 | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AR_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AR_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AR_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | No | [6 empty] | 2015-03-31
AR_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AR_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AR_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.3564 | 1.2948 | 1.5401 | 1.4019 | [6 empty] | 2015-03-31
AR_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 136.38 | 130.1876 | 154.8469 | 140.9555 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.5885 | 9.3563 | 11.7104 | 10.0248 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.4453 | 9.3652 | 11.5396 | 9.9696 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.4833 | 8.5824 | 10.4734 | 9.3489 | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.0473 | 11.6661 | 14.6271 | 12.459 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.261 | 1.1179 | 1.4417 | 1.2192 | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
AR_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.9479 | 2.8141 | 3.3471 | 3.0468 | [6 empty] | 2015-03-31
AR_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AR_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AR_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AR_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AR_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AR_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 99.9141 | 97.6868 | 102.3581 | 95.6524 | [6 empty] | 2015-03-31
AR_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2263 | 2.1457 | 2.0767 | 1.9888 | [6 empty] | 2015-03-31
AR_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.5369 | 5.3474 | 5.5253 | 5.3513 | [6 empty] | 2015-03-31
AR_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6047 | 2.4797 | 2.6306 | 2.4788 | [6 empty] | 2015-03-31
AR_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.6288 | 4.5922 | 4.4365 | 4.4043 | [6 empty] | 2015-03-31
AR_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
AR_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1652.7264 | 1610.3488 | 1652.7264 | 1610.3488 | [6 empty] | 2015-03-31
AR_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 741.608 | [6 empty] | 2015-03-31
AR_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1504.4048 | 1546.7824 | 1546.7824 | [6 empty] | 2015-03-31
AR_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
AR_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
AR_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
AR_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
AR_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AR_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AR_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
AR_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AR_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | No | No | [6 empty] | 2015-03-31
AR_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1642 | 1.1244 | 1.1618 | 1.1252 | [6 empty] | 2015-03-31
AR_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0586 | 1.0471 | 1.0895 | 1.0788 | [6 empty] | 2015-03-31
AR_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.7069 | 0.68335 | 0.63258 | 0.62744 | [6 empty] | 2015-03-31
AR_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.70334 | 0.6805 | 0.62738 | 0.62249 | [6 empty] | 2015-03-31
AR_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84507 | 0.80346 | 0.7653 | 0.76603 | [6 empty] | 2015-03-31
AR_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0249 | 0.97638 | 0.98421 | 0.98012 | [6 empty] | 2015-03-31
AR_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.70823 | 0.66827 | 0.67366 | 0.6688 | [6 empty] | 2015-03-31
AR_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.72732 | 0.68696 | 0.68702 | 0.68097 | [6 empty] | 2015-03-31
AR_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0358 | 0.9845 | 1.0038 | 0.99543 | [6 empty] | 2015-03-31
AR_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7492 | 1.6938 | 1.647 | 1.6244 | [6 empty] | 2015-03-31
AR_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7435 | 1.6892 | 1.6383 | 1.6162 | [6 empty] | 2015-03-31
AR_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1273 | 2.0455 | 2.0544 | 2.0215 | [6 empty] | 2015-03-31
AR_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.5141 | 2.3892 | 2.5224 | 2.4906 | [6 empty] | 2015-03-31
AR_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8154 | 1.7484 | 1.7791 | 1.7493 | [6 empty] | 2015-03-31
AR_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8197 | 1.7521 | 1.7807 | 1.7546 | [6 empty] | 2015-03-31
AR_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2647 | 2.2102 | 2.3036 | 2.2641 | [6 empty] | 2015-03-31
AR_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5336 | 2.402 | 2.5724 | 2.5288 | [6 empty] | 2015-03-31
AR_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2273 | 2.1781 | 2.0745 | 2.1377 | [6 empty] | 2015-03-31
AR_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.12 | 1.0563 | 1.1473 | 1.0131 | [6 empty] | 2015-03-31
AR_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1135 | 1.051 | 1.1497 | 1.0083 | [6 empty] | 2015-03-31
AR_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3995 | 1.299 | 1.4094 | 1.2544 | [6 empty] | 2015-03-31
AR_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5802 | 1.4619 | 1.634 | 1.5293 | [6 empty] | 2015-03-31
AR_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.248 | 1.1562 | 1.3117 | 1.1799 | [6 empty] | 2015-03-31
AR_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2505 | 1.1585 | 1.3152 | 1.1835 | [6 empty] | 2015-03-31
AR_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5111 | 1.4 | 1.5814 | 1.4451 | [6 empty] | 2015-03-31
AR_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6222 | 1.4959 | 1.6985 | 1.5775 | [6 empty] | 2015-03-31
AR_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AR_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
AR_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AR_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AR_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AR_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AR_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AR_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AR_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AR_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AR_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
AR_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AR_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
AR_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
AR_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | 275.4544 | 275.4544 | [6 empty] | 2015-03-31
AR_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | 381.3984 | 360.2096 | [6 empty] | 2015-03-31
AR_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
AR_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
AR_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | 381.3984 | 381.3984 | [6 empty] | 2015-03-31
AR_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 614.4752 | 593.2864 | [6 empty] | 2015-03-31
AR_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 593.2864 | 593.2864 | [6 empty] | 2015-03-31
AR_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 699.2304 | 783.9856 | 783.9856 | [6 empty] | 2015-03-31
AR_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 847.552 | 995.8736 | 974.6848 | [6 empty] | 2015-03-31
AR_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 614.4752 | 614.4752 | [6 empty] | 2015-03-31
AR_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
AR_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | 847.552 | 847.552 | [6 empty] | 2015-03-31
AR_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 847.552 | 1017.0624 | 995.8736 | [6 empty] | 2015-03-31
AR_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 932.3072 | 953.496 | [6 empty] | 2015-03-31
AR_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 423.776 | 381.3984 | [6 empty] | 2015-03-31
AR_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 423.776 | 381.3984 | [6 empty] | 2015-03-31
AR_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 529.72 | 487.3424 | [6 empty] | 2015-03-31
AR_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 656.8528 | 614.4752 | [6 empty] | 2015-03-31
AR_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 402.5872 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
AR_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 402.5872 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
AR_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 487.3424 | 614.4752 | 550.9088 | [6 empty] | 2015-03-31
AR_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
AR_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AR_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15624 | 0.14879 | 0.15245 | 0.15073 | [6 empty] | 2015-03-31
AR_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15512 | 0.1479 | 0.15073 | 0.14908 | [6 empty] | 2015-03-31
AR_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.19729 | 0.18389 | 0.19465 | 0.19493 | [6 empty] | 2015-03-31
AR_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.25123 | 0.23562 | 0.2631 | 0.26171 | [6 empty] | 2015-03-31
AR_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15066 | 0.14311 | 0.15323 | 0.15168 | [6 empty] | 2015-03-31
AR_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15473 | 0.14614 | 0.15761 | 0.15615 | [6 empty] | 2015-03-31
AR_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.25013 | 0.23378 | 0.26664 | 0.26383 | [6 empty] | 2015-03-31
AR_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.41455 | 0.3968 | 0.42902 | 0.42136 | [6 empty] | 2015-03-31
AR_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.41274 | 0.39536 | 0.42611 | 0.4186 | [6 empty] | 2015-03-31
AR_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.52702 | 0.49199 | 0.55651 | 0.54909 | [6 empty] | 2015-03-31
AR_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.64278 | 0.60243 | 0.70558 | 0.69478 | [6 empty] | 2015-03-31
AR_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.4088 | 0.38806 | 0.44163 | 0.43312 | [6 empty] | 2015-03-31
AR_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.41012 | 0.3892 | 0.44344 | 0.43488 | [6 empty] | 2015-03-31
AR_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.55745 | 0.5221 | 0.60693 | 0.59387 | [6 empty] | 2015-03-31
AR_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.64391 | 0.60164 | 0.72008 | 0.7053 | [6 empty] | 2015-03-31
AR_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65656 | 0.63944 | 0.65682 | 0.67612 | [6 empty] | 2015-03-31
AR_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.28042 | 0.25982 | 0.30412 | 0.27317 | [6 empty] | 2015-03-31
AR_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27832 | 0.25815 | 0.30389 | 0.27007 | [6 empty] | 2015-03-31
AR_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.3468 | 0.3153 | 0.38249 | 0.34653 | [6 empty] | 2015-03-31
AR_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.41604 | 0.37959 | 0.47188 | 0.43784 | [6 empty] | 2015-03-31
AR_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.30731 | 0.27845 | 0.35762 | 0.31385 | [6 empty] | 2015-03-31
AR_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.30805 | 0.27911 | 0.35874 | 0.31506 | [6 empty] | 2015-03-31
AR_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.38288 | 0.34783 | 0.44054 | 0.39525 | [6 empty] | 2015-03-31
AR_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.42504 | 0.38608 | 0.48872 | 0.44789 | [6 empty] | 2015-03-31
NC_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7841 | 1.7362 | 1.8059 | 1.6959 | 1.5445 | 1.4538 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.824 | 1.7509 | 1.8794 | 1.7235 | 1.5877 | 1.4907 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3213 | 1.2187 | 1.382 | 1.3124 | 1.3351 | 1.2919 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.759 | 1.7014 | 1.795 | 1.6661 | 1.4559 | 1.3621 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5165 | 1.4088 | 1.5996 | 1.4964 | 1.5447 | 1.4604 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 572.0976 | 635.664 | 593.2864 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 678.0416 | 720.4192 | 635.664 | 699.2304 | 635.664 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 593.2864 | 529.72 | 614.4752 | 572.0976 | 593.2864 | 572.0976 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 678.0416 | 614.4752 | 635.664 | 572.0976 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 699.2304 | 635.664 | 699.2304 | 656.8528 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.4563 | 0.43752 | 0.44329 | 0.40585 | 0.44879 | 0.41357 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.50929 | 0.47927 | 0.51026 | 0.45288 | 0.49218 | 0.45408 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.41511 | 0.37577 | 0.42891 | 0.40433 | 0.42604 | 0.41227 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.48758 | 0.46544 | 0.48302 | 0.43538 | 0.44588 | 0.40803 |  |  |  |  | 2015-03-31
NC_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.47427 | 0.43363 | 0.49175 | 0.45317 | 0.49296 | 0.46605 |  |  |  |  | 2015-03-31
NC_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10742.7216 | 10382.512 | 10424.8896 | 9831.6032 | 10573.2112 | 10213.0016 |  |  |  |  | 2015-03-31
NC_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24473.064 | 23561.9456 | 24621.3856 | 24239.9872 | 25172.2944 | 24875.6512 |  |  |  |  | 2015-03-31
NC_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 195191.2259 | 185741.0211 | 198772.1331 | 195000.5267 | 201187.6563 | 197861.0147 |  |  |  |  | 2015-03-31
NC_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 21782.0864 | 20192.9264 | 23561.9456 | 21697.3312 | 23731.456 | 21951.5968 |  |  |  |  | 2015-03-31
NC_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NC_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NC_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NC_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NC_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
NC_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
NC_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
NC_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
NC_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
NC_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
NC_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
NC_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
NC_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | No | No | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NC_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NC_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NC_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NC_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NC_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NC_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 387.8936 | 376.8631 | 408.2885 | 402.8961 | 341.0138 | 336.3892 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 387.8936 | 376.8631 | 408.2885 | 402.8961 | 341.0138 | 336.3892 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
NC_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 368.1679 | 357.7018 | 387.5257 | 382.4051 | 323.6702 | 319.2773 |  |  |  |  | 2015-03-31
NC_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 368.1679 | 357.7018 | 387.5257 | 382.4051 | 323.6702 | 319.2773 |  |  |  |  | 2015-03-31
NC_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.1121 | 4.1383 | 4.1835 | 4.0789 | 4.9012 | 4.7914 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1826.5912 | 887.3122 | 1922.6442 | 948.6054 | 1605.7962 | 792.0169 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 887.3122 | 0 | 948.6054 | 0 | 792.0169 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1826.5912 | 1774.6022 | 1922.6442 | 1897.2837 | 1605.7962 | 1584.0353 |  |  |  |  | 2015-03-31
NC_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 826.8923 | 832.1483 | 841.2416 | 820.2035 | 985.5715 | 963.4857 |  |  |  |  | 2015-03-31
NC_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2131.2344 | 2062.6026 | 2243.1377 | 2205.097 | 1873.6667 | 1841.1735 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NC_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.5394 | 11.1343 | 11.1817 | 10.5451 | 11.3476 | 10.9528 |  |  |  |  | 2015-03-31
NC_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.1746 | 32.0601 | 35.3974 | 32.9646 | 36.1815 | 35.7592 |  |  |  |  | 2015-03-31
NC_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 274.4836 | 261.2149 | 279.5411 | 274.2266 | 282.93 | 278.2412 |  |  |  |  | 2015-03-31
NC_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 31.3091 | 27.6282 | 33.8603 | 29.5024 | 34.1132 | 31.5713 |  |  |  |  | 2015-03-31
NC_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.8633 | 43.7806 | 43.2886 | 43.0985 | 45.5924 | 45.514 |  |  |  |  | 2015-03-31
NC_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.78302 | 0.77688 | 0.78428 | 0.7728 | 0.84 | 0.82665 |  |  |  |  | 2015-03-31
NC_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.6706 | 9.5737 | 9.874 | 9.6955 | 10.5349 | 10.3165 |  |  |  |  | 2015-03-31
NC_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.64808 | 0.62539 | 0.67625 | 0.6556 | 0.72241 | 0.70007 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.8537 | 4.7867 | 10.3718 | 5.1174 | 8.6628 | 4.2727 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.7867 | 0 | 5.1174 | 0 | 4.2727 |  |  |  |  | 2015-03-31
NC_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 29.561 | 28.7204 | 31.1153 | 30.7044 | 25.9884 | 25.6359 |  |  |  |  | 2015-03-31
NC_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.8737 | 17.9874 | 18.1839 | 17.7292 | 21.3037 | 20.8263 |  |  |  |  | 2015-03-31
NC_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.4723 | 38.2038 | 41.5477 | 40.8428 | 34.7017 | 34.1008 |  |  |  |  | 2015-03-31
NC_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8402 | 3.8171 | 3.8593 | 3.8313 | 3.8765 | 3.8539 |  |  |  |  | 2015-03-31
NC_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | YES | YES | YES |  |  |  |  | 2015-03-31
NC_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | YES | YES |  |  |  |  | 2015-03-31
NC_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NC_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | YES | YES |  |  |  |  | 2015-03-31
NC_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4299.4894 | 4362.5479 | 4300.7463 | 4193.8838 | 4579.9823 | 4432.5721 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.9184 | 8.8746 | 9.1805 | 9.072 | 8.0426 | 7.9636 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 38.29 | 36.9022 | 39.6644 | 38.0354 | 33.8595 | 33.015 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.0713 | 5.8054 | 6.478 | 6.2115 | 5.7094 | 5.4994 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.2464 | 4.9114 | 5.6401 | 5.3 | 4.8897 | 4.5991 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3305.4528 | 3326.6416 | 3263.0752 | 3114.7536 | 3114.7536 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12628.5248 | 11696.2176 | 12628.5248 | 11611.4624 | 12670.9024 | 11844.5392 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2182.4464 | 2436.712 | 2309.5792 | 2500.2784 | 2394.3344 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1906.992 | 1737.4816 | 2012.936 | 1843.4256 | 2055.3136 | 1906.992 |  |  |  |  | 2015-03-31
NC_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | VFD | VFD | n/a | VFD |  |  |  |  | 2015-03-31
NC_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NC_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.6046 | 1.6973 | 2.7035 | 1.7732 | 3.8275 | 2.5778 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2605 | 2.241 | 2.2479 | 2.2113 | 2.1083 | 2.1088 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.5533 | 12.5484 | 13.5599 | 12.4515 | 13.5915 | 12.7032 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6275 | 1.532 | 1.7145 | 1.6194 | 1.7593 | 1.6775 |  |  |  |  | 2015-03-31
NC_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.3323 | 1.2138 | 1.4165 | 1.2969 | 1.4379 | 1.329 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 23.5211 | 20.4898 | 25.5632 | 21.6479 | 25.6369 | 21.9936 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 23.1321 | 20.5545 | 25.0782 | 21.2119 | 25.1821 | 21.6081 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 21.0022 | 18.9519 | 22.8232 | 19.9705 | 22.9686 | 20.2261 |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.135 | 25.8681 | 31.9891 | 27.0734 | 28.963 | 26.3007 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 11.1636 | 11.1636 | 11.1636 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.932 | 5.1592 | 6.5026 | 5.515 | 6.4818 | 5.5574 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7055.8704 | 6144.752 | 7670.3456 | 6504.9616 | 7691.5344 | 6589.7168 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6949.9264 | 6165.9408 | 7522.024 | 6356.64 | 7564.4016 | 6483.7728 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6293.0736 | 5678.5984 | 6843.9824 | 5996.4304 | 6886.36 | 6059.9968 |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8750.9744 | 7755.1008 | 9598.5264 | 8115.3104 | 9598.5264 | 8200.0656 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1779.8592 | 1546.7824 | 1949.3696 | 1652.7264 | 1949.3696 | 1673.9152 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
NC_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
NC_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
NC_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
NC_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NC_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7058.3071 | 6148.6507 | 7671.0872 | 6496.1683 | 7693.2295 | 6599.9086 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6941.5568 | 6168.0597 | 7525.5625 | 6365.3486 | 7556.7313 | 6484.2178 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6302.3967 | 5687.1587 | 6777.6191 | 5992.8283 | 6777.6191 | 6069.5318 |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NC_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NC_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NC_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | No | No | No |  |  |  |  | 2015-03-31
NC_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NC_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NC_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2852 | 1.2294 | 1.3671 | 1.2672 | 1.5161 | 1.3798 |  |  |  |  | 2015-03-31
NC_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 129.2207 | 123.6102 | 137.4531 | 127.4127 | 152.4359 | 138.7307 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.3342 | 9.0711 | 11.2314 | 9.5838 | 11.2638 | 9.7369 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.1633 | 9.0997 | 11.0183 | 9.3908 | 11.064 | 9.5662 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.2979 | 8.3903 | 10.0276 | 8.8412 | 10.0915 | 8.9544 |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.8007 | 11.3654 | 14.0547 | 11.8949 | 14.0518 | 12.0036 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 2.2687 | 2.2687 | 2.2687 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2473 | 1.0848 | 1.3673 | 1.1596 | 1.3724 | 1.1686 |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
NC_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.7932 | 2.6719 | 2.9711 | 2.7541 | 3.295 | 2.9988 |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NC_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NC_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NC_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NC_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 97.1752 | 95.1821 | 100.3031 | 95.7407 | 99.0549 | 92.7291 |  |  |  |  | 2015-03-31
NC_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0506 | 1.9672 | 2.0757 | 1.9354 | 1.7953 | 1.6789 |  |  |  |  | 2015-03-31
NC_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.4851 | 5.2695 | 5.3551 | 5.171 | 5.0571 | 4.8824 |  |  |  |  | 2015-03-31
NC_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.599 | 2.4727 | 2.5583 | 2.3813 | 2.5919 | 2.432 |  |  |  |  | 2015-03-31
NC_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.3726 | 4.3342 | 4.427 | 4.3901 | 3.9972 | 3.9623 |  |  |  |  | 2015-03-31
NC_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 593.2864 | 678.0416 | 614.4752 |  |  |  |  | 2015-03-31
NC_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1652.7264 | 1589.16 | 1610.3488 | 1546.7824 | 1610.3488 | 1546.7824 |  |  |  |  | 2015-03-31
NC_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 762.7968 | 720.4192 | 783.9856 | 720.4192 |  |  |  |  | 2015-03-31
NC_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1504.4048 | 1483.216 | 1567.9712 | 1546.7824 |  |  |  |  | 2015-03-31
NC_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
NC_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
NC_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
NC_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
NC_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NC_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NC_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NC_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1534 | 1.108 | 1.126 | 1.0873 | 1.1313 | 1.0831 |  |  |  |  | 2015-03-31
NC_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.068 | 1.0557 | 1.0545 | 1.055 | 1.0991 | 1.0868 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.62542 | 0.6018 | 0.63983 | 0.63412 | 0.47932 | 0.47237 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.62216 | 0.5992 | 0.6319 | 0.63007 | 0.47492 | 0.46827 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.75493 | 0.71374 | 0.7752 | 0.77847 | 0.58385 | 0.58526 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.91613 | 0.86803 | 0.95363 | 0.94898 | 0.77042 | 0.75991 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.62677 | 0.60145 | 0.67549 | 0.67071 | 0.55058 | 0.54508 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.66376 | 0.63484 | 0.68856 | 0.68392 | 0.56292 | 0.55887 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.9291 | 0.87852 | 0.98045 | 0.97261 | 0.80966 | 0.7985 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5672 | 1.5108 | 1.6642 | 1.6407 | 1.3217 | 1.2939 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.562 | 1.5067 | 1.6572 | 1.6342 | 1.3143 | 1.287 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.9144 | 1.8162 | 2.0671 | 2.0528 | 1.6434 | 1.6159 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2613 | 2.1375 | 2.4485 | 2.417 | 2.0458 | 2.0006 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6472 | 1.5231 | 1.7787 | 1.7491 | 1.5153 | 1.4892 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.6512 | 1.5806 | 1.7831 | 1.754 | 1.5205 | 1.4912 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.0534 | 1.9405 | 2.2906 | 2.2581 | 1.9394 | 1.8946 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.2867 | 2.1558 | 2.5097 | 2.4692 | 2.1505 | 2.0949 |  |  |  |  | 2015-03-31
NC_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0782 | 2.0305 | 2.1265 | 2.1318 | 2.0798 | 2.086 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0069 | 0.94495 | 1.1573 | 1.0246 | 0.92164 | 0.81219 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0009 | 0.94015 | 1.1562 | 1.017 | 0.92378 | 0.80427 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2408 | 1.1444 | 1.4203 | 1.2691 | 1.133 | 0.9975 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4132 | 1.3022 | 1.6086 | 1.4906 | 1.3332 | 1.2347 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.131 | 1.042 | 1.2971 | 1.1699 | 1.1157 | 1.0032 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1336 | 1.0443 | 1.2996 | 1.1732 | 1.1191 | 1.0067 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3628 | 1.2544 | 1.5661 | 1.4382 | 1.3353 | 1.2151 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.4639 | 1.3425 | 1.6763 | 1.5526 | 1.4324 | 1.3159 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NC_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | 190.6992 | 169.5104 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 190.6992 | 169.5104 | 169.5104 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 254.2656 | 254.2656 | 233.0768 | 233.0768 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | 339.0208 | 339.0208 | 317.832 | 317.832 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 211.888 | 190.6992 | 190.6992 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 211.888 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | 339.0208 | 339.0208 | 339.0208 | 317.832 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 572.0976 | 572.0976 | 550.9088 | 529.72 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | 572.0976 | 572.0976 | 529.72 | 529.72 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 741.608 | 741.608 | 678.0416 | 678.0416 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 805.1744 | 911.1184 | 911.1184 | 889.9296 | 868.7408 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 593.2864 | 572.0976 | 593.2864 | 593.2864 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 593.2864 | 593.2864 | 593.2864 | 593.2864 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 805.1744 | 805.1744 | 805.1744 | 783.9856 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 805.1744 | 932.3072 | 911.1184 | 932.3072 | 911.1184 |  |  |  |  | 2015-03-31
NC_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | 911.1184 | 911.1184 | 932.3072 | 932.3072 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 423.776 | 360.2096 | 381.3984 | 339.0208 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 423.776 | 360.2096 | 381.3984 | 339.0208 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 423.776 | 529.72 | 466.1536 | 466.1536 | 423.776 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 614.4752 | 572.0976 | 593.2864 | 550.9088 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 487.3424 | 423.776 | 466.1536 | 423.776 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 487.3424 | 423.776 | 466.1536 | 423.776 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 593.2864 | 529.72 | 572.0976 | 508.5312 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 656.8528 | 593.2864 | 635.664 | 572.0976 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14875 | 0.14095 | 0.1442 | 0.14235 | 0.12903 | 0.12658 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14769 | 0.14011 | 0.14282 | 0.14105 | 0.12748 | 0.12514 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.1869 | 0.17314 | 0.18495 | 0.18608 | 0.1612 | 0.16162 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23877 | 0.22272 | 0.24047 | 0.23896 | 0.22551 | 0.22175 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.14613 | 0.13787 | 0.14521 | 0.14372 | 0.14018 | 0.13872 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.1499 | 0.14065 | 0.14939 | 0.14794 | 0.14499 | 0.14362 |  |  |  |  | 2015-03-31
NC_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.2402 | 0.22339 | 0.24518 | 0.24262 | 0.23729 | 0.23227 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.39885 | 0.38002 | 0.40905 | 0.40131 | 0.38489 | 0.37491 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.39712 | 0.37865 | 0.40676 | 0.39918 | 0.38223 | 0.37244 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.50251 | 0.46635 | 0.52891 | 0.52423 | 0.48667 | 0.47991 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.61399 | 0.57251 | 0.65036 | 0.63996 | 0.62675 | 0.61046 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.39824 | 0.37722 | 0.4205 | 0.41216 | 0.42233 | 0.41317 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.39954 | 0.37672 | 0.42191 | 0.41375 | 0.42417 | 0.41505 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.53794 | 0.50046 | 0.57618 | 0.56571 | 0.56562 | 0.55125 |  |  |  |  | 2015-03-31
NC_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.6205 | 0.57675 | 0.66603 | 0.65266 | 0.66252 | 0.64247 |  |  |  |  | 2015-03-31
NC_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64635 | 0.62923 | 0.64569 | 0.64758 | 0.66371 | 0.66568 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.26811 | 0.24734 | 0.2946 | 0.26246 | 0.26887 | 0.23976 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.26611 | 0.24576 | 0.29425 | 0.25997 | 0.26875 | 0.23695 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.32712 | 0.29561 | 0.3705 | 0.33389 | 0.33652 | 0.30019 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.39552 | 0.35953 | 0.44051 | 0.40571 | 0.41963 | 0.38532 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.29728 | 0.26808 | 0.33909 | 0.29775 | 0.33585 | 0.29595 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.29815 | 0.26886 | 0.33991 | 0.29878 | 0.33704 | 0.29714 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.36715 | 0.33155 | 0.4188 | 0.37714 | 0.40815 | 0.36637 |  |  |  |  | 2015-03-31
NC_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.40719 | 0.36806 | 0.45998 | 0.42067 | 0.44994 | 0.40943 |  |  |  |  | 2015-03-31
OK_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8328 | 1.7856 | 1.5876 | 1.4524 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9399 | 1.8618 | 1.8131 | 1.6179 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4201 | 1.3045 | 1.6608 | 1.5601 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8583 | 1.8002 | 1.7281 | 1.5548 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.661 | 1.5413 | 1.8924 | 1.7406 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 656.8528 | 635.664 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 826.3632 | 720.4192 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 572.0976 | 741.608 | 699.2304 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 783.9856 | 699.2304 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 741.608 | 678.0416 | 847.552 | 783.9856 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.4718 | 0.45305 | 0.50664 | 0.46229 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.54275 | 0.51463 | 0.5786 | 0.51632 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.45319 | 0.40937 | 0.53 | 0.49788 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.51621 | 0.49524 | 0.55147 | 0.49618 | [6 empty] | 2015-03-31
OK_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.52737 | 0.48251 | 0.60392 | 0.55545 | [6 empty] | 2015-03-31
OK_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11018.176 | 10615.5888 | 11717.4064 | 11039.3648 | [6 empty] | 2015-03-31
OK_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25468.9376 | 24494.2528 | 27566.6288 | 27100.4752 | [6 empty] | 2015-03-31
OK_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 204535.4867 | 194343.6739 | 221783.1699 | 217291.1443 | [6 empty] | 2015-03-31
OK_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22905.0928 | 21294.744 | 26591.944 | 24409.4976 | [6 empty] | 2015-03-31
OK_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
OK_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | Yes | [6 empty] | 2015-03-31
OK_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | Yes | [6 empty] | 2015-03-31
OK_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | Yes | [6 empty] | 2015-03-31
OK_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
OK_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
OK_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
OK_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
OK_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
OK_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
OK_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
OK_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
OK_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OK_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OK_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OK_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | No | [6 empty] | 2015-03-31
OK_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | No | [6 empty] | 2015-03-31
OK_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | No | [6 empty] | 2015-03-31
OK_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OK_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OK_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OK_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 390.4675 | 378.159 | 331.5652 | 325.6491 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 390.4675 | 378.159 | 331.5652 | 325.6491 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
OK_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 370.6158 | 358.9323 | 314.6992 | 309.089 | [6 empty] | 2015-03-31
OK_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 370.6158 | 358.9323 | 314.6992 | 309.089 | [6 empty] | 2015-03-31
OK_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.6432 | 4.6814 | 4.5234 | 4.3974 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1838.6375 | 890.3634 | 1561.3186 | 766.7309 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 890.3634 | 0 | 766.7309 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1838.6375 | 1780.7838 | 1561.3186 | 1533.4601 | [6 empty] | 2015-03-31
OK_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 933.676 | 941.3539 | 909.5898 | 884.2531 | [6 empty] | 2015-03-31
OK_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2145.3412 | 2069.7352 | 1821.6776 | 1782.3688 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OK_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.8172 | 11.4031 | 12.5706 | 11.8528 | [6 empty] | 2015-03-31
OK_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.6133 | 33.3142 | 39.4567 | 36.8591 | [6 empty] | 2015-03-31
OK_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 287.6444 | 273.2989 | 311.8881 | 289.1569 | [6 empty] | 2015-03-31
OK_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.9402 | 29.1212 | 38.2454 | 33.1942 | [6 empty] | 2015-03-31
OK_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 44.8055 | 44.7202 | 48.3652 | 48.1501 | [6 empty] | 2015-03-31
OK_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.80224 | 0.79599 | 0.91346 | 0.89572 | [6 empty] | 2015-03-31
OK_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.9265 | 9.8301 | 11.5148 | 11.2324 | [6 empty] | 2015-03-31
OK_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.67896 | 0.64829 | 0.79221 | 0.76418 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.9191 | 4.8032 | 8.4228 | 4.1362 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.8032 | 0 | 4.1362 | [6 empty] | 2015-03-31
OK_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 29.7572 | 28.8192 | 25.2683 | 24.8174 | [6 empty] | 2015-03-31
OK_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.1819 | 20.3479 | 19.6613 | 19.1136 | [6 empty] | 2015-03-31
OK_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.7342 | 38.3352 | 33.7402 | 33.012 | [6 empty] | 2015-03-31
OK_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8691 | 3.8395 | 4.1163 | 4.0798 | [6 empty] | 2015-03-31
OK_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
OK_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
OK_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | YES | NO | NO | [6 empty] | 2015-03-31
OK_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
OK_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4733.6917 | 4824.1782 | 4519.3832 | 4394.6963 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.9708 | 8.9223 | 8.0665 | 8.0798 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 37.9579 | 36.9243 | 39.5178 | 32.0693 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3982 | 6.146 | 6.2511 | 5.9603 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5404 | 5.2166 | 5.3544 | 4.9834 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3580.9072 | 3538.5296 | 3623.2848 | 3602.096 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13200.6224 | 12395.448 | 14895.7264 | 13052.3008 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2436.712 | 2309.5792 | 2712.1664 | 2563.8448 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2012.936 | 1843.4256 | 2246.0128 | 2055.3136 | [6 empty] | 2015-03-31
OK_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
OK_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | No | No | [6 empty] | 2015-03-31
OK_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.135 | 2.0494 | 3.3947 | 2.242 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.4213 | 2.3981 | 2.4544 | 2.4446 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.1553 | 13.3058 | 15.8859 | 13.9997 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7125 | 1.6235 | 1.8981 | 1.791 | [6 empty] | 2015-03-31
OK_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4111 | 1.2985 | 1.569 | 1.4338 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.3142 | 22.3063 | 29.0258 | 24.8772 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.1301 | 22.4673 | 28.6615 | 24.8225 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.6267 | 20.5738 | 25.9091 | 22.9941 | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.0623 | 28.0621 | 29.75 | 26.9942 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 8.5685 | 8.5176 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.3728 | 5.6226 | 7.0159 | 6.3185 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7606.7792 | 6695.6608 | 8708.5968 | 7458.4576 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7543.2128 | 6738.0384 | 8602.6528 | 7458.4576 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6780.416 | 6165.9408 | 7776.2896 | 6907.5488 | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9323.072 | 8411.9536 | 10954.6096 | 9365.4496 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3263.0752 | 3220.6976 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1906.992 | 1695.104 | 2309.5792 | 1949.3696 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
OK_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
OK_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
OK_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
OK_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
OK_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | Yes | Yes | [6 empty] | 2015-03-31
OK_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | Yes | [6 empty] | 2015-03-31
OK_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | Yes | [6 empty] | 2015-03-31
OK_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | Yes | [6 empty] | 2015-03-31
OK_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7596.3755 | 6693.7538 | 7852.8447 | 7465.238 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7541.1363 | 6742.0643 | 7852.8447 | 7448.8379 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6173.8442 | 6777.6191 | 6777.6191 | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 825.0071 | 825.0071 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | No | [6 empty] | 2015-03-31
OK_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | No | [6 empty] | 2015-03-31
OK_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | No | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | No | No | [6 empty] | 2015-03-31
OK_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
OK_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | No | No | [6 empty] | 2015-03-31
OK_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OK_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4097 | 1.3366 | 1.4823 | 1.3274 | [6 empty] | 2015-03-31
OK_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 141.7317 | 134.3808 | 149.0385 | 133.4632 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.122 | 9.8753 | 12.7528 | 10.9301 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.0412 | 9.8712 | 12.5927 | 10.906 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.9413 | 9.1083 | 11.3834 | 10.1027 | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.6475 | 12.3294 | 15.9337 | 13.6987 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2086 | 2.1827 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.34 | 1.1823 | 1.6126 | 1.3705 | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
OK_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.0636 | 2.9047 | 3.2216 | 2.8849 | [6 empty] | 2015-03-31
OK_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OK_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OK_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OK_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | NO | NO | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OK_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OK_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 99.1803 | 96.2115 | 99.2825 | 90.4291 | [6 empty] | 2015-03-31
OK_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2285 | 2.1695 | 1.9332 | 1.8489 | [6 empty] | 2015-03-31
OK_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.8712 | 5.6625 | 5.3472 | 5.2131 | [6 empty] | 2015-03-31
OK_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.7384 | 2.6707 | 2.7682 | 2.647 | [6 empty] | 2015-03-31
OK_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5927 | 4.5468 | 4.2083 | 4.172 | [6 empty] | 2015-03-31
OK_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 741.608 | 699.2304 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
OK_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1758.6704 | 1695.104 | 1864.6144 | 1801.048 | [6 empty] | 2015-03-31
OK_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 826.3632 | 805.1744 | 889.9296 | 826.3632 | [6 empty] | 2015-03-31
OK_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1567.9712 | 1567.9712 | 1695.104 | 1673.9152 | [6 empty] | 2015-03-31
OK_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
OK_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
OK_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
OK_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
OK_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OK_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OK_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OK_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OK_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | No | No | [6 empty] | 2015-03-31
OK_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.2345 | 1.1907 | 1.3099 | 1.268 | [6 empty] | 2015-03-31
OK_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.1061 | 1.0946 | 1.1909 | 1.1785 | [6 empty] | 2015-03-31
OK_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.68555 | 0.66192 | 0.5479 | 0.54191 | [6 empty] | 2015-03-31
OK_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.6814 | 0.65859 | 0.54185 | 0.53624 | [6 empty] | 2015-03-31
OK_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.83069 | 0.78883 | 0.71226 | 0.71323 | [6 empty] | 2015-03-31
OK_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.042 | 0.98971 | 0.95293 | 0.94621 | [6 empty] | 2015-03-31
OK_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.67373 | 0.64529 | 0.54865 | 0.53788 | [6 empty] | 2015-03-31
OK_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.72258 | 0.64834 | 0.54248 | 0.53215 | [6 empty] | 2015-03-31
OK_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0492 | 0.99578 | 0.96238 | 0.95053 | [6 empty] | 2015-03-31
OK_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7091 | 1.6533 | 1.511 | 1.4845 | [6 empty] | 2015-03-31
OK_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7023 | 1.6479 | 1.5011 | 1.4754 | [6 empty] | 2015-03-31
OK_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1159 | 2.0103 | 2.0052 | 1.9812 | [6 empty] | 2015-03-31
OK_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.5619 | 2.4276 | 2.5113 | 2.4687 | [6 empty] | 2015-03-31
OK_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7979 | 1.655 | 1.5071 | 1.4653 | [6 empty] | 2015-03-31
OK_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8019 | 1.7345 | 1.4993 | 1.5363 | [6 empty] | 2015-03-31
OK_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3266 | 2.2141 | 2.1121 | 2.0765 | [6 empty] | 2015-03-31
OK_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5768 | 2.4385 | 2.5478 | 2.4924 | [6 empty] | 2015-03-31
OK_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.172 | 2.1205 | 2.2734 | 2.2779 | [6 empty] | 2015-03-31
OK_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1122 | 1.0472 | 1.0775 | 0.96885 | [6 empty] | 2015-03-31
OK_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1107 | 1.0413 | 1.0764 | 0.95908 | [6 empty] | 2015-03-31
OK_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.407 | 1.3053 | 1.3811 | 1.2524 | [6 empty] | 2015-03-31
OK_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6109 | 1.4949 | 1.6892 | 1.5678 | [6 empty] | 2015-03-31
OK_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2498 | 1.1573 | 1.2079 | 1.0687 | [6 empty] | 2015-03-31
OK_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2522 | 1.1594 | 1.2119 | 1.0724 | [6 empty] | 2015-03-31
OK_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5284 | 1.4153 | 1.5289 | 1.376 | [6 empty] | 2015-03-31
OK_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6411 | 1.5116 | 1.7212 | 1.5851 | [6 empty] | 2015-03-31
OK_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OK_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
OK_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OK_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OK_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OK_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OK_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OK_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OK_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OK_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OK_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
OK_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OK_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
OK_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 254.2656 | 233.0768 | [6 empty] | 2015-03-31
OK_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 275.4544 | 317.832 | 317.832 | [6 empty] | 2015-03-31
OK_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 423.776 | 423.776 | [6 empty] | 2015-03-31
OK_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
OK_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
OK_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 423.776 | 423.776 | [6 empty] | 2015-03-31
OK_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 678.0416 | 678.0416 | [6 empty] | 2015-03-31
OK_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
OK_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 741.608 | 911.1184 | 889.9296 | [6 empty] | 2015-03-31
OK_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 932.3072 | 1123.0064 | 1101.8176 | [6 empty] | 2015-03-31
OK_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
OK_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
OK_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 783.9856 | 953.496 | 932.3072 | [6 empty] | 2015-03-31
OK_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 932.3072 | 1144.1952 | 1123.0064 | [6 empty] | 2015-03-31
OK_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | 1017.0624 | 1017.0624 | [6 empty] | 2015-03-31
OK_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 402.5872 | 487.3424 | 444.9648 | [6 empty] | 2015-03-31
OK_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 402.5872 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
OK_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
OK_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 593.2864 | 762.7968 | 699.2304 | [6 empty] | 2015-03-31
OK_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 423.776 | 550.9088 | 466.1536 | [6 empty] | 2015-03-31
OK_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 423.776 | 550.9088 | 487.3424 | [6 empty] | 2015-03-31
OK_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
OK_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 783.9856 | 720.4192 | [6 empty] | 2015-03-31
OK_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OK_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.17056 | 0.16275 | 0.17484 | 0.17294 | [6 empty] | 2015-03-31
OK_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.1692 | 0.16166 | 0.17291 | 0.17113 | [6 empty] | 2015-03-31
OK_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.21054 | 0.19956 | 0.2273 | 0.22761 | [6 empty] | 2015-03-31
OK_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.2796 | 0.26224 | 0.3041 | 0.30196 | [6 empty] | 2015-03-31
OK_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16232 | 0.15467 | 0.17109 | 0.16721 | [6 empty] | 2015-03-31
OK_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16493 | 0.1571 | 0.17255 | 0.16881 | [6 empty] | 2015-03-31
OK_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.27832 | 0.26065 | 0.30712 | 0.30334 | [6 empty] | 2015-03-31
OK_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.44864 | 0.43005 | 0.48219 | 0.47376 | [6 empty] | 2015-03-31
OK_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.4464 | 0.42826 | 0.47904 | 0.47082 | [6 empty] | 2015-03-31
OK_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.56293 | 0.53036 | 0.63991 | 0.63224 | [6 empty] | 2015-03-31
OK_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.70908 | 0.66434 | 0.80141 | 0.78781 | [6 empty] | 2015-03-31
OK_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.43669 | 0.41722 | 0.48096 | 0.46763 | [6 empty] | 2015-03-31
OK_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.43796 | 0.41659 | 0.47845 | 0.4665 | [6 empty] | 2015-03-31
OK_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.59612 | 0.56014 | 0.67404 | 0.66265 | [6 empty] | 2015-03-31
OK_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.70999 | 0.66411 | 0.81306 | 0.79537 | [6 empty] | 2015-03-31
OK_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67988 | 0.66147 | 0.72551 | 0.72691 | [6 empty] | 2015-03-31
OK_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.30154 | 0.27995 | 0.34384 | 0.30919 | [6 empty] | 2015-03-31
OK_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29914 | 0.27799 | 0.34349 | 0.30606 | [6 empty] | 2015-03-31
OK_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.37051 | 0.33794 | 0.44073 | 0.39966 | [6 empty] | 2015-03-31
OK_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.45725 | 0.41859 | 0.53908 | 0.50032 | [6 empty] | 2015-03-31
OK_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.32781 | 0.29808 | 0.38548 | 0.33796 | [6 empty] | 2015-03-31
OK_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.32859 | 0.29875 | 0.38674 | 0.33925 | [6 empty] | 2015-03-31
OK_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.40952 | 0.37317 | 0.48789 | 0.43913 | [6 empty] | 2015-03-31
OK_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46111 | 0.42046 | 0.54928 | 0.50583 | [6 empty] | 2015-03-31
SC_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.823 | 1.7706 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8873 | 1.8151 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3418 | 1.2396 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8274 | 1.7705 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5537 | 1.4505 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 678.0416 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.45109 | 0.4328 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.51112 | 0.48297 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.41094 | 0.37272 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.49229 | 0.47085 | [8 empty] | 2015-03-31
SC_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.4722 | 0.43288 | [8 empty] | 2015-03-31
SC_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10573.2112 | 10191.8128 | [8 empty] | 2015-03-31
SC_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24134.0432 | 23265.3024 | [8 empty] | 2015-03-31
SC_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 193029.9683 | 183939.9731 | [8 empty] | 2015-03-31
SC_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 21697.3312 | 20150.5488 | [8 empty] | 2015-03-31
SC_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | [8 empty] | 2015-03-31
SC_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
SC_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
SC_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
SC_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
SC_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
SC_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
SC_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
SC_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
SC_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
SC_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
SC_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
SC_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | [8 empty] | 2015-03-31
SC_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
SC_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
SC_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
SC_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
SC_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
SC_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
SC_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
SC_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
SC_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
SC_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 395.6577 | 384.7247 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 395.6577 | 384.7247 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
SC_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 375.5379 | 365.1644 | [8 empty] | 2015-03-31
SC_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 375.5379 | 365.1644 | [8 empty] | 2015-03-31
SC_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.0474 | 4.0773 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1863.2055 | 905.8222 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 905.8222 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1863.2055 | 1811.6919 | [8 empty] | 2015-03-31
SC_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 813.8824 | 819.8928 | [8 empty] | 2015-03-31
SC_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2173.8718 | 2105.7154 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
SC_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.3355 | 10.9394 | [8 empty] | 2015-03-31
SC_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 34.7068 | 31.6593 | [8 empty] | 2015-03-31
SC_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 271.4632 | 258.6798 | [8 empty] | 2015-03-31
SC_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 31.1821 | 27.5564 | [8 empty] | 2015-03-31
SC_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.0542 | 42.9734 | [8 empty] | 2015-03-31
SC_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.76941 | 0.76344 | [8 empty] | 2015-03-31
SC_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.5095 | 9.4157 | [8 empty] | 2015-03-31
SC_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.63754 | 0.6159 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.0509 | 4.8866 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.8866 | [8 empty] | 2015-03-31
SC_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 30.1527 | 29.3195 | [8 empty] | 2015-03-31
SC_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.5925 | 17.7225 | [8 empty] | 2015-03-31
SC_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 40.2623 | 39.0007 | [8 empty] | 2015-03-31
SC_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8247 | 3.801 | [8 empty] | 2015-03-31
SC_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | [8 empty] | 2015-03-31
SC_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
SC_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
SC_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
SC_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4247.9414 | 4316.5389 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.9562 | 8.9099 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 38.4092 | 37.0396 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2034 | 5.943 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.3769 | 5.0461 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3326.6416 | 3305.4528 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12480.2032 | 11590.2736 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2288.3904 | 2161.2576 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1885.8032 | 1716.2928 | [8 empty] | 2015-03-31
SC_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
SC_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
SC_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.5107 | 1.6229 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2558 | 2.2353 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.3994 | 12.4411 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6054 | 1.5147 | [8 empty] | 2015-03-31
SC_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.3158 | 1.2027 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 23.4849 | 20.5597 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 23.1106 | 20.6305 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 20.9458 | 18.9864 | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.1325 | 25.9382 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.9087 | 5.1413 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7055.8704 | 6165.9408 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 6928.7376 | 6187.1296 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6293.0736 | 5699.7872 | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8750.9744 | 7776.2896 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1779.8592 | 1546.7824 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
SC_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | [8 empty] | 2015-03-31
SC_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
SC_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
SC_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | [8 empty] | 2015-03-31
SC_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
SC_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
SC_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
SC_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
SC_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7047.4373 | 6169.6488 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 6935.0943 | 6190.88 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6285.5092 | 5697.52 | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
SC_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
SC_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
SC_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | [8 empty] | 2015-03-31
SC_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
SC_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
SC_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2888 | 1.2352 | [8 empty] | 2015-03-31
SC_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 129.5778 | 124.1933 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.3183 | 9.1021 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.1538 | 9.1334 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.273 | 8.4055 | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.7996 | 11.3962 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2424 | 1.0811 | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
SC_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8009 | 2.6845 | [8 empty] | 2015-03-31
SC_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
SC_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
SC_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
SC_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
SC_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
SC_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 98.4961 | 96.5065 | [8 empty] | 2015-03-31
SC_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1195 | 2.0406 | [8 empty] | 2015-03-31
SC_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.491 | 5.2791 | [8 empty] | 2015-03-31
SC_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5891 | 2.4651 | [8 empty] | 2015-03-31
SC_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.4658 | 4.4293 | [8 empty] | 2015-03-31
SC_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 2015-03-31
SC_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1652.7264 | 1589.16 | [8 empty] | 2015-03-31
SC_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | [8 empty] | 2015-03-31
SC_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | [8 empty] | 2015-03-31
SC_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
SC_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
SC_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
SC_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
SC_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
SC_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
SC_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
SC_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
SC_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
SC_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1546 | 1.1101 | [8 empty] | 2015-03-31
SC_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0535 | 1.054 | [8 empty] | 2015-03-31
SC_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.65409 | 0.63066 | [8 empty] | 2015-03-31
SC_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.65087 | 0.62809 | [8 empty] | 2015-03-31
SC_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.79137 | 0.75402 | [8 empty] | 2015-03-31
SC_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.96024 | 0.91252 | [8 empty] | 2015-03-31
SC_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.65317 | 0.62478 | [8 empty] | 2015-03-31
SC_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.65039 | 0.62347 | [8 empty] | 2015-03-31
SC_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.96842 | 0.91875 | [8 empty] | 2015-03-31
SC_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.641 | 1.5853 | [8 empty] | 2015-03-31
SC_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6358 | 1.5812 | [8 empty] | 2015-03-31
SC_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0153 | 1.9187 | [8 empty] | 2015-03-31
SC_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3647 | 2.2424 | [8 empty] | 2015-03-31
SC_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6439 | 1.5846 | [8 empty] | 2015-03-31
SC_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.639 | 1.5808 | [8 empty] | 2015-03-31
SC_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.1314 | 2.0219 | [8 empty] | 2015-03-31
SC_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.3867 | 2.2503 | [8 empty] | 2015-03-31
SC_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1119 | 2.0652 | [8 empty] | 2015-03-31
SC_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0599 | 0.99623 | [8 empty] | 2015-03-31
SC_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.054 | 0.99147 | [8 empty] | 2015-03-31
SC_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3227 | 1.2246 | [8 empty] | 2015-03-31
SC_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4871 | 1.3774 | [8 empty] | 2015-03-31
SC_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.1755 | 1.0863 | [8 empty] | 2015-03-31
SC_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1778 | 1.0883 | [8 empty] | 2015-03-31
SC_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.4274 | 1.3191 | [8 empty] | 2015-03-31
SC_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.5287 | 1.4109 | [8 empty] | 2015-03-31
SC_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
SC_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
SC_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
SC_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
SC_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
SC_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
SC_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
SC_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
SC_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
SC_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
SC_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
SC_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
SC_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
SC_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
SC_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | [8 empty] | 2015-03-31
SC_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | [8 empty] | 2015-03-31
SC_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | [8 empty] | 2015-03-31
SC_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
SC_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | [8 empty] | 2015-03-31
SC_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 2015-03-31
SC_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 2015-03-31
SC_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 678.0416 | [8 empty] | 2015-03-31
SC_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 826.3632 | [8 empty] | 2015-03-31
SC_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2015-03-31
SC_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2015-03-31
SC_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 720.4192 | [8 empty] | 2015-03-31
SC_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 826.3632 | [8 empty] | 2015-03-31
SC_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | [8 empty] | 2015-03-31
SC_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | [8 empty] | 2015-03-31
SC_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | [8 empty] | 2015-03-31
SC_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
SC_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2015-03-31
SC_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | [8 empty] | 2015-03-31
SC_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | [8 empty] | 2015-03-31
SC_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | [8 empty] | 2015-03-31
SC_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | [8 empty] | 2015-03-31
SC_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
SC_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15264 | 0.14511 | [8 empty] | 2015-03-31
SC_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15162 | 0.14429 | [8 empty] | 2015-03-31
SC_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.19143 | 0.17909 | [8 empty] | 2015-03-31
SC_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.24421 | 0.22871 | [8 empty] | 2015-03-31
SC_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.14868 | 0.14089 | [8 empty] | 2015-03-31
SC_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15044 | 0.14309 | [8 empty] | 2015-03-31
SC_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24377 | 0.22772 | [8 empty] | 2015-03-31
SC_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40606 | 0.38798 | [8 empty] | 2015-03-31
SC_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40439 | 0.38667 | [8 empty] | 2015-03-31
SC_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.51255 | 0.48052 | [8 empty] | 2015-03-31
SC_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.62539 | 0.58549 | [8 empty] | 2015-03-31
SC_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.40148 | 0.38235 | [8 empty] | 2015-03-31
SC_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.39992 | 0.38115 | [8 empty] | 2015-03-31
SC_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.54154 | 0.50625 | [8 empty] | 2015-03-31
SC_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.62736 | 0.58575 | [8 empty] | 2015-03-31
SC_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.6403 | 0.62391 | [8 empty] | 2015-03-31
SC_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.27554 | 0.25475 | [8 empty] | 2015-03-31
SC_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27362 | 0.25323 | [8 empty] | 2015-03-31
SC_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.33874 | 0.3077 | [8 empty] | 2015-03-31
SC_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.40504 | 0.36928 | [8 empty] | 2015-03-31
SC_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.2987 | 0.27036 | [8 empty] | 2015-03-31
SC_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.2994 | 0.27098 | [8 empty] | 2015-03-31
SC_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.372 | 0.33759 | [8 empty] | 2015-03-31
SC_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.41381 | 0.37569 | [8 empty] | 2015-03-31
TN_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.9156 | 1.8665 | 1.7886 | 1.6789 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9564 | 1.8821 | 1.8546 | 1.6986 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4201 | 1.314 | 1.3916 | 1.318 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8858 | 1.8292 | 1.7706 | 1.6413 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6372 | 1.5258 | 1.6374 | 1.5311 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 678.0416 | 720.4192 | 635.664 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 635.664 | 593.2864 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.45241 | 0.4343 | 0.44699 | 0.40923 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.51093 | 0.48458 | 0.51053 | 0.454 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.4274 | 0.38753 | 0.44409 | 0.41915 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.48895 | 0.46784 | 0.48333 | 0.43546 | [6 empty] | 2015-03-31
TN_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.48502 | 0.44419 | 0.51084 | 0.47107 | [6 empty] | 2015-03-31
TN_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10594.4 | 10234.1904 | 10509.6448 | 9895.1696 | [6 empty] | 2015-03-31
TN_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24663.7632 | 23752.6448 | 25172.2944 | 24790.896 | [6 empty] | 2015-03-31
TN_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 198729.7555 | 189194.7955 | 205001.6403 | 201102.9011 | [6 empty] | 2015-03-31
TN_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 21888.0304 | 20320.0592 | 23858.5888 | 21972.7856 | [6 empty] | 2015-03-31
TN_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
TN_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
TN_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
TN_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
TN_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
TN_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
TN_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
TN_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
TN_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
TN_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
TN_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
TN_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
TN_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | No | No | [6 empty] | 2015-03-31
TN_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
TN_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
TN_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
TN_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
TN_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
TN_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
TN_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
TN_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
TN_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
TN_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 430.4225 | 419.2852 | 404.9396 | 399.282 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 430.4225 | 419.2852 | 404.9396 | 399.282 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
TN_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 408.5374 | 397.9654 | 384.3501 | 378.9781 | [6 empty] | 2015-03-31
TN_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 408.5374 | 397.9654 | 384.3501 | 378.9781 | [6 empty] | 2015-03-31
TN_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.3777 | 4.4201 | 4.4821 | 4.3753 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 2026.7808 | 987.193 | 1906.7939 | 940.0969 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 987.193 | 0 | 940.0969 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 2026.7808 | 1974.3163 | 1906.7939 | 1880.1653 | [6 empty] | 2015-03-31
TN_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 880.3032 | 888.8116 | 901.2827 | 879.8118 | [6 empty] | 2015-03-31
TN_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2364.8682 | 2294.8098 | 2224.7514 | 2185.4426 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
TN_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.3807 | 10.9807 | 11.2714 | 10.6291 | [6 empty] | 2015-03-31
TN_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.4441 | 32.3069 | 36.1949 | 33.7116 | [6 empty] | 2015-03-31
TN_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 279.466 | 266.076 | 288.2875 | 282.7994 | [6 empty] | 2015-03-31
TN_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 31.4539 | 27.7992 | 34.2945 | 29.8788 | [6 empty] | 2015-03-31
TN_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.1399 | 43.0589 | 43.548 | 43.3566 | [6 empty] | 2015-03-31
TN_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.77231 | 0.76638 | 0.79835 | 0.78532 | [6 empty] | 2015-03-31
TN_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.555 | 9.4624 | 10.0059 | 9.88 | [6 empty] | 2015-03-31
TN_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.64384 | 0.62013 | 0.68978 | 0.66779 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.9341 | 5.3256 | 10.2867 | 5.0715 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.3256 | 0 | 5.0715 | [6 empty] | 2015-03-31
TN_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.8021 | 31.9534 | 30.8601 | 30.4289 | [6 empty] | 2015-03-31
TN_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.0283 | 19.2122 | 19.4818 | 19.0176 | [6 empty] | 2015-03-31
TN_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.8 | 42.5042 | 41.2069 | 40.4765 | [6 empty] | 2015-03-31
TN_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8533 | 3.8305 | 3.8697 | 3.8399 | [6 empty] | 2015-03-31
TN_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | YES | [6 empty] | 2015-03-31
TN_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
TN_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
TN_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
TN_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4530.0397 | 4610.1428 | 4503.3955 | 4376.1648 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.6452 | 9.5738 | 9.2215 | 9.0754 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 42.5256 | 39.7472 | 39.773 | 37.834 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4727 | 5.5827 | 6.3869 | 6.1263 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6483 | 5.3213 | 5.5517 | 5.2178 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3474.9632 | 3432.5856 | 3453.7744 | 3369.0192 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13031.112 | 11929.2944 | 13221.8112 | 11992.8608 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2140.0688 | 2479.0896 | 2330.768 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 1906.992 | 1758.6704 | 2034.1248 | 1864.6144 | [6 empty] | 2015-03-31
TN_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
TN_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
TN_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.8021 | 1.8559 | 3.0409 | 2.0423 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3586 | 2.3257 | 2.3383 | 2.2817 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.9845 | 12.8002 | 14.1942 | 12.86 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.6324 | 1.5018 | 1.7315 | 1.6378 | [6 empty] | 2015-03-31
TN_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.3429 | 1.2306 | 1.4321 | 1.3136 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 23.739 | 20.8127 | 25.7516 | 21.8244 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 23.4154 | 20.8391 | 25.313 | 21.517 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 21.1457 | 19.1158 | 23.0064 | 20.1616 | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.343 | 26.1888 | 32.2656 | 27.2804 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.9532 | 5.2659 | 6.5676 | 5.5599 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7119.4368 | 6250.696 | 7733.912 | 6547.3392 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7034.6816 | 6250.696 | 7585.5904 | 6462.584 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6335.4512 | 5742.1648 | 6907.5488 | 6059.9968 | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8814.5408 | 7861.0448 | 9683.2816 | 8178.8768 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1779.8592 | 1589.16 | 1970.5584 | 1673.9152 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
TN_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | VFD | [6 empty] | 2015-03-31
TN_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
TN_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
TN_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
TN_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
TN_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
TN_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
TN_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
TN_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7123.6958 | 6245.5683 | 7727.6401 | 6549.1614 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7026.5875 | 6253.4717 | 7596.0153 | 6456.9054 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6345.4947 | 5736.3379 | 6777.6191 | 6050.1652 | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
TN_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
TN_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
TN_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | No | [6 empty] | 2015-03-31
TN_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
TN_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
TN_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.3509 | 1.2908 | 1.4366 | 1.3205 | [6 empty] | 2015-03-31
TN_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 135.8211 | 129.7831 | 144.438 | 132.7674 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.4299 | 9.2141 | 11.3142 | 9.662 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.2878 | 9.2257 | 11.1215 | 9.5259 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.3615 | 8.4628 | 10.1081 | 8.9258 | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.8921 | 11.5063 | 14.1762 | 11.9859 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2518 | 1.1073 | 1.381 | 1.1691 | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
TN_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.9359 | 2.8053 | 3.1221 | 2.8698 | [6 empty] | 2015-03-31
TN_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
TN_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
TN_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
TN_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
TN_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
TN_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 99.6932 | 97.6092 | 101.2999 | 95.9388 | [6 empty] | 2015-03-31
TN_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1936 | 2.1135 | 2.0348 | 1.9056 | [6 empty] | 2015-03-31
TN_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.4843 | 5.2962 | 5.3554 | 5.1699 | [6 empty] | 2015-03-31
TN_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5879 | 2.4628 | 2.5656 | 2.4166 | [6 empty] | 2015-03-31
TN_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5776 | 4.5413 | 4.3854 | 4.3512 | [6 empty] | 2015-03-31
TN_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 614.4752 | [6 empty] | 2015-03-31
TN_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1652.7264 | 1589.16 | 1610.3488 | 1546.7824 | [6 empty] | 2015-03-31
TN_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
TN_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | 1504.4048 | 1504.4048 | [6 empty] | 2015-03-31
TN_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
TN_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
TN_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
TN_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
TN_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
TN_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
TN_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialEnthalpy | [6 empty] | 2015-03-31
TN_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
TN_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | No | No | [6 empty] | 2015-03-31
TN_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1532 | 1.1137 | 1.1261 | 1.0871 | [6 empty] | 2015-03-31
TN_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0547 | 1.0554 | 1.0592 | 1.0483 | [6 empty] | 2015-03-31
TN_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.69981 | 0.6762 | 0.62476 | 0.61901 | [6 empty] | 2015-03-31
TN_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.69628 | 0.67337 | 0.62022 | 0.61472 | [6 empty] | 2015-03-31
TN_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.83744 | 0.7954 | 0.74735 | 0.75181 | [6 empty] | 2015-03-31
TN_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0059 | 0.95773 | 0.93567 | 0.93076 | [6 empty] | 2015-03-31
TN_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.69894 | 0.65785 | 0.65724 | 0.65144 | [6 empty] | 2015-03-31
TN_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.71826 | 0.67717 | 0.66947 | 0.66532 | [6 empty] | 2015-03-31
TN_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0216 | 0.96972 | 0.96837 | 0.96133 | [6 empty] | 2015-03-31
TN_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7345 | 1.6788 | 1.6327 | 1.6093 | [6 empty] | 2015-03-31
TN_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7289 | 1.6743 | 1.6253 | 1.6023 | [6 empty] | 2015-03-31
TN_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1063 | 1.9963 | 1.9975 | 1.9856 | [6 empty] | 2015-03-31
TN_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4729 | 2.3482 | 2.4149 | 2.3826 | [6 empty] | 2015-03-31
TN_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7905 | 1.7229 | 1.7324 | 1.7073 | [6 empty] | 2015-03-31
TN_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.795 | 1.7267 | 1.7372 | 1.712 | [6 empty] | 2015-03-31
TN_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2378 | 2.1249 | 2.2365 | 2.205 | [6 empty] | 2015-03-31
TN_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5014 | 2.3683 | 2.4778 | 2.4456 | [6 empty] | 2015-03-31
TN_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2405 | 2.1906 | 2.0884 | 2.0892 | [6 empty] | 2015-03-31
TN_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0981 | 1.0366 | 1.1374 | 0.99346 | [6 empty] | 2015-03-31
TN_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0915 | 1.0313 | 1.1376 | 0.98524 | [6 empty] | 2015-03-31
TN_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3631 | 1.2639 | 1.3893 | 1.2305 | [6 empty] | 2015-03-31
TN_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5461 | 1.4339 | 1.5947 | 1.4825 | [6 empty] | 2015-03-31
TN_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2252 | 1.1346 | 1.2766 | 1.1482 | [6 empty] | 2015-03-31
TN_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2259 | 1.1351 | 1.2794 | 1.1494 | [6 empty] | 2015-03-31
TN_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.4776 | 1.3676 | 1.5375 | 1.4062 | [6 empty] | 2015-03-31
TN_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.5867 | 1.4665 | 1.6645 | 1.5343 | [6 empty] | 2015-03-31
TN_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
TN_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
TN_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
TN_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
TN_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
TN_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
TN_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
TN_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
TN_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
TN_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
TN_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
TN_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
TN_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
TN_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
TN_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | 254.2656 | 275.4544 | [6 empty] | 2015-03-31
TN_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | 339.0208 | 339.0208 | [6 empty] | 2015-03-31
TN_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 211.888 | [6 empty] | 2015-03-31
TN_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
TN_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | 339.0208 | 339.0208 | [6 empty] | 2015-03-31
TN_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 572.0976 | [6 empty] | 2015-03-31
TN_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 572.0976 | [6 empty] | 2015-03-31
TN_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 678.0416 | 741.608 | 741.608 | [6 empty] | 2015-03-31
TN_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 826.3632 | 932.3072 | 911.1184 | [6 empty] | 2015-03-31
TN_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 593.2864 | 593.2864 | [6 empty] | 2015-03-31
TN_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 593.2864 | 593.2864 | [6 empty] | 2015-03-31
TN_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 826.3632 | 805.1744 | [6 empty] | 2015-03-31
TN_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 826.3632 | 932.3072 | 932.3072 | [6 empty] | 2015-03-31
TN_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 911.1184 | 911.1184 | [6 empty] | 2015-03-31
TN_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | 423.776 | 360.2096 | [6 empty] | 2015-03-31
TN_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | 423.776 | 360.2096 | [6 empty] | 2015-03-31
TN_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 423.776 | 529.72 | 466.1536 | [6 empty] | 2015-03-31
TN_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
TN_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
TN_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
TN_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 487.3424 | 593.2864 | 529.72 | [6 empty] | 2015-03-31
TN_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
TN_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
TN_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15258 | 0.1451 | 0.14369 | 0.14181 | [6 empty] | 2015-03-31
TN_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15148 | 0.14421 | 0.14223 | 0.14043 | [6 empty] | 2015-03-31
TN_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.19477 | 0.18113 | 0.18663 | 0.18819 | [6 empty] | 2015-03-31
TN_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.24459 | 0.22901 | 0.24087 | 0.23925 | [6 empty] | 2015-03-31
TN_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.14869 | 0.13995 | 0.14562 | 0.1442 | [6 empty] | 2015-03-31
TN_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.1528 | 0.14405 | 0.15001 | 0.14869 | [6 empty] | 2015-03-31
TN_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24432 | 0.22773 | 0.24543 | 0.24314 | [6 empty] | 2015-03-31
TN_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40717 | 0.38925 | 0.40916 | 0.40141 | [6 empty] | 2015-03-31
TN_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40536 | 0.38781 | 0.40669 | 0.3991 | [6 empty] | 2015-03-31
TN_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.52077 | 0.48489 | 0.53299 | 0.52905 | [6 empty] | 2015-03-31
TN_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.62875 | 0.58824 | 0.65451 | 0.64378 | [6 empty] | 2015-03-31
TN_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.40429 | 0.3831 | 0.42158 | 0.41349 | [6 empty] | 2015-03-31
TN_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.40569 | 0.3843 | 0.42313 | 0.41502 | [6 empty] | 2015-03-31
TN_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.55107 | 0.51464 | 0.57864 | 0.56837 | [6 empty] | 2015-03-31
TN_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.63137 | 0.58843 | 0.66823 | 0.65526 | [6 empty] | 2015-03-31
TN_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65863 | 0.64118 | 0.64643 | 0.64668 | [6 empty] | 2015-03-31
TN_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.27287 | 0.25288 | 0.29525 | 0.25989 | [6 empty] | 2015-03-31
TN_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27074 | 0.25116 | 0.29532 | 0.25717 | [6 empty] | 2015-03-31
TN_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.33762 | 0.30625 | 0.37146 | 0.33463 | [6 empty] | 2015-03-31
TN_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.40589 | 0.36951 | 0.44515 | 0.40931 | [6 empty] | 2015-03-31
TN_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.30236 | 0.27354 | 0.34148 | 0.29949 | [6 empty] | 2015-03-31
TN_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.30322 | 0.27433 | 0.34243 | 0.30056 | [6 empty] | 2015-03-31
TN_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.37561 | 0.3405 | 0.42095 | 0.37869 | [6 empty] | 2015-03-31
TN_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.41545 | 0.37665 | 0.46429 | 0.42382 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8327 | 1.7747 | 1.576 | 1.4473 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.1205 | 2.0252 | 1.7948 | 1.6412 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5046 | 1.3729 | 1.5358 | 1.4834 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 2.0085 | 1.9419 | 1.6347 | 1.4969 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7646 | 1.628 | 1.865 | 1.7523 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 699.2304 | 656.8528 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 889.9296 | 847.552 | 805.1744 | 741.608 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 699.2304 | 678.0416 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 847.552 | 805.1744 | 741.608 | 678.0416 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 783.9856 | 741.608 | 847.552 | 783.9856 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.51063 | 0.49083 | 0.50295 | 0.46187 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.6332 | 0.60032 | 0.57278 | 0.52375 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.48014 | 0.43813 | 0.49009 | 0.47338 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.59869 | 0.57561 | 0.52166 | 0.47769 | [6 empty] | 2015-03-31
NV_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.56314 | 0.51954 | 0.59517 | 0.55922 | [6 empty] | 2015-03-31
NV_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11505.5184 | 11102.9312 | 11505.5184 | 11102.9312 | [6 empty] | 2015-03-31
NV_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 27439.496 | 26486 | 28053.9712 | 27630.1952 | [6 empty] | 2015-03-31
NV_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 224537.7139 | 214324.7123 | 225406.4547 | 221401.7715 | [6 empty] | 2015-03-31
NV_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 25638.448 | 23858.5888 | 27248.7968 | 25066.3504 | [6 empty] | 2015-03-31
NV_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NV_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NV_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NV_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NV_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
NV_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
NV_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
NV_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
NV_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
NV_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
NV_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
NV_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
NV_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NV_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NV_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NV_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
NV_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
NV_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
NV_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NV_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NV_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NV_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 357.5338 | 346.0285 | 289.6015 | 284.4243 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 357.5338 | 346.0285 | 289.6015 | 284.4243 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
NV_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 339.3496 | 328.4336 | 274.8722 | 269.9633 | [6 empty] | 2015-03-31
NV_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 339.3496 | 328.4336 | 274.8722 | 269.9633 | [6 empty] | 2015-03-31
NV_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.4711 | 3.4707 | 4.0757 | 3.9825 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1683.6213 | 814.7129 | 1363.7143 | 669.6682 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 814.7129 | 0 | 669.6682 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1683.6213 | 1629.4132 | 1363.7143 | 1339.3365 | [6 empty] | 2015-03-31
NV_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 697.9896 | 697.9167 | 819.5679 | 800.8312 | [6 empty] | 2015-03-31
NV_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1964.3305 | 1893.9551 | 1613.7214 | 1576.0357 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NV_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 12.3384 | 11.9118 | 12.3464 | 11.9106 | [6 empty] | 2015-03-31
NV_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 39.2835 | 36.0189 | 40.1622 | 37.5884 | [6 empty] | 2015-03-31
NV_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 315.7755 | 285.1977 | 316.989 | 311.3454 | [6 empty] | 2015-03-31
NV_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 36.8557 | 32.4658 | 39.006 | 34.1011 | [6 empty] | 2015-03-31
NV_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 46.3282 | 46.2422 | 49.7345 | 49.6484 | [6 empty] | 2015-03-31
NV_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.83379 | 0.82754 | 0.94871 | 0.92997 | [6 empty] | 2015-03-31
NV_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.2732 | 10.1785 | 11.9821 | 11.684 | [6 empty] | 2015-03-31
NV_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.70042 | 0.67553 | 0.82307 | 0.79395 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.0824 | 4.3951 | 7.3568 | 3.6126 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.3951 | 0 | 3.6126 | [6 empty] | 2015-03-31
NV_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 27.2474 | 26.3705 | 22.0703 | 21.6757 | [6 empty] | 2015-03-31
NV_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.0874 | 15.0859 | 17.7154 | 17.3104 | [6 empty] | 2015-03-31
NV_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 36.3828 | 35.078 | 29.8882 | 29.1905 | [6 empty] | 2015-03-31
NV_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.0225 | 3.9937 | 4.113 | 4.0851 | [6 empty] | 2015-03-31
NV_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
NV_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
NV_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
NV_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
NV_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 3991.3791 | 3993.3362 | 4151.5319 | 4035.5237 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.3884 | 9.2674 | 7.7336 | 7.7007 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 37.0909 | 35.0385 | 35.0668 | 29.4166 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 7.1948 | 6.8635 | 6.3411 | 6.0191 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.2407 | 5.8296 | 5.2239 | 4.8073 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 4089.4384 | 4025.872 | 3474.9632 | 3474.9632 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14683.8384 | 13370.1328 | 15022.8592 | 13243 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2796.9216 | 2627.4112 | 2860.488 | 2712.1664 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2351.9568 | 2161.2576 | 2351.9568 | 2161.2576 | [6 empty] | 2015-03-31
NV_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
NV_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | [6 empty] | 2015-03-31
NV_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.0413 | 1.2436 | 3.1112 | 2.0921 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.7711 | 2.7231 | 2.3577 | 2.3477 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 15.6561 | 14.3533 | 16.0189 | 14.2111 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.9546 | 1.8465 | 2.0002 | 1.8986 | [6 empty] | 2015-03-31
NV_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.6438 | 1.5107 | 1.6478 | 1.5164 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 28.6159 | 25.1772 | 24.4717 | 22.0316 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 28.1875 | 25.1951 | 24.2577 | 21.9172 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 25.5636 | 23.1965 | 21.6362 | 20.0486 | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.597 | 30.2409 | 24.6862 | 21.7242 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 9.1635 | 9.1598 | 7.5936 | 7.5385 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.8346 | 5.94 | 5.7133 | 4.977 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 9.2649 | 9.2649 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8581.464 | 7564.4016 | 8984.0512 | 7691.5344 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 8454.3312 | 7564.4016 | 8856.9184 | 7649.1568 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7670.3456 | 6971.1152 | 8051.744 | 7119.4368 | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 10446.0784 | 9344.2608 | 11102.9312 | 9534.96 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3029.9984 | 3008.8096 | 3284.264 | 3241.8864 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2055.3136 | 1779.8592 | 2246.0128 | 1885.8032 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
NV_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | [6 empty] | 2015-03-31
NV_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
NV_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
NV_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NV_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NV_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | Yes | No | Yes | [6 empty] | 2015-03-31
NV_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | Yes | No | Yes | [6 empty] | 2015-03-31
NV_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | Yes | No | Yes | [6 empty] | 2015-03-31
NV_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7555.2692 | 7852.8447 | 7681.9995 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7560.63 | 7852.8447 | 7642.1009 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 825.0071 | 825.0071 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | No | Yes | No | [6 empty] | 2015-03-31
NV_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | No | Yes | No | [6 empty] | 2015-03-31
NV_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | No | Yes | No | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
NV_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
NV_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
NV_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NV_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2414 | 1.1504 | 1.4066 | 1.2517 | [6 empty] | 2015-03-31
NV_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 124.8137 | 115.6663 | 141.4194 | 125.8448 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 12.5727 | 11.0619 | 13.1491 | 11.2474 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 12.3844 | 11.0697 | 12.9666 | 11.189 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 11.2316 | 10.1916 | 11.7898 | 10.4378 | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 15.2072 | 13.6667 | 16.1656 | 13.9516 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.0525 | 2.0444 | 2.229 | 2.199 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4371 | 1.249 | 1.575 | 1.3178 | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
NV_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.6979 | 2.5002 | 3.0569 | 2.7202 | [6 empty] | 2015-03-31
NV_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NV_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NV_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NV_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NV_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NV_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 98.6943 | 92.3391 | 96.841 | 87.3144 | [6 empty] | 2015-03-31
NV_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2556 | 2.1369 | 1.756 | 1.6463 | [6 empty] | 2015-03-31
NV_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.0355 | 5.8572 | 4.7149 | 4.5625 | [6 empty] | 2015-03-31
NV_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9399 | 2.8012 | 2.484 | 2.3577 | [6 empty] | 2015-03-31
NV_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.6501 | 4.6045 | 3.9815 | 3.9401 | [6 empty] | 2015-03-31
NV_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
NV_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1885.8032 | 1822.2368 | 1843.4256 | 1779.8592 | [6 empty] | 2015-03-31
NV_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 889.9296 | 847.552 | 868.7408 | 826.3632 | [6 empty] | 2015-03-31
NV_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1673.9152 | 1652.7264 | 1737.4816 | 1716.2928 | [6 empty] | 2015-03-31
NV_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
NV_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
NV_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
NV_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
NV_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NV_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NV_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NV_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NV_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | No | No | [6 empty] | 2015-03-31
NV_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.327 | 1.277 | 1.2948 | 1.2449 | [6 empty] | 2015-03-31
NV_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.1724 | 1.1585 | 1.2193 | 1.2045 | [6 empty] | 2015-03-31
NV_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.67966 | 0.64627 | 0.49576 | 0.48224 | [6 empty] | 2015-03-31
NV_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.66987 | 0.64347 | 0.48958 | 0.4765 | [6 empty] | 2015-03-31
NV_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84444 | 0.80925 | 0.61372 | 0.59492 | [6 empty] | 2015-03-31
NV_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0411 | 0.98539 | 0.88692 | 0.8632 | [6 empty] | 2015-03-31
NV_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.74395 | 0.70885 | 0.52903 | 0.51426 | [6 empty] | 2015-03-31
NV_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.75771 | 0.72248 | 0.5455 | 0.53102 | [6 empty] | 2015-03-31
NV_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0836 | 1.0235 | 0.91042 | 0.88035 | [6 empty] | 2015-03-31
NV_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7059 | 1.648 | 1.4266 | 1.3844 | [6 empty] | 2015-03-31
NV_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7001 | 1.6433 | 1.4162 | 1.3747 | [6 empty] | 2015-03-31
NV_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1448 | 2.0588 | 1.7932 | 1.7319 | [6 empty] | 2015-03-31
NV_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.5775 | 2.4437 | 2.408 | 2.3302 | [6 empty] | 2015-03-31
NV_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8766 | 1.7991 | 1.5505 | 1.5009 | [6 empty] | 2015-03-31
NV_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8803 | 1.8024 | 1.5565 | 1.5074 | [6 empty] | 2015-03-31
NV_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.4712 | 2.349 | 2.1181 | 2.0449 | [6 empty] | 2015-03-31
NV_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.6723 | 2.527 | 2.4939 | 2.3994 | [6 empty] | 2015-03-31
NV_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.4137 | 2.3438 | 2.3523 | 2.337 | [6 empty] | 2015-03-31
NV_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.2176 | 1.0664 | 1.0144 | 0.89758 | [6 empty] | 2015-03-31
NV_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.2165 | 1.0608 | 1.0127 | 0.8864 | [6 empty] | 2015-03-31
NV_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.5216 | 1.4063 | 1.2862 | 1.1288 | [6 empty] | 2015-03-31
NV_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.7077 | 1.5647 | 1.609 | 1.4728 | [6 empty] | 2015-03-31
NV_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.35 | 1.2394 | 1.2354 | 1.0799 | [6 empty] | 2015-03-31
NV_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.352 | 1.2413 | 1.2386 | 1.0841 | [6 empty] | 2015-03-31
NV_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6568 | 1.5261 | 1.5248 | 1.3601 | [6 empty] | 2015-03-31
NV_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7985 | 1.6531 | 1.7033 | 1.5406 | [6 empty] | 2015-03-31
NV_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NV_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
NV_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NV_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NV_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NV_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NV_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NV_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NV_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NV_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NV_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
NV_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NV_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | 233.0768 | 211.888 | [6 empty] | 2015-03-31
NV_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | 211.888 | 211.888 | [6 empty] | 2015-03-31
NV_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 275.4544 | 275.4544 | [6 empty] | 2015-03-31
NV_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 402.5872 | 402.5872 | 381.3984 | [6 empty] | 2015-03-31
NV_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
NV_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 254.2656 | 233.0768 | [6 empty] | 2015-03-31
NV_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 402.5872 | 402.5872 | 402.5872 | [6 empty] | 2015-03-31
NV_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
NV_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
NV_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 868.7408 | 805.1744 | 783.9856 | [6 empty] | 2015-03-31
NV_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1080.6288 | 1017.0624 | 1080.6288 | 1059.44 | [6 empty] | 2015-03-31
NV_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 699.2304 | 678.0416 | [6 empty] | 2015-03-31
NV_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 699.2304 | 678.0416 | [6 empty] | 2015-03-31
NV_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 953.496 | 953.496 | 911.1184 | [6 empty] | 2015-03-31
NV_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1101.8176 | 1038.2512 | 1123.0064 | 1080.6288 | [6 empty] | 2015-03-31
NV_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 1080.6288 | 1059.44 | 1059.44 | 1059.44 | [6 empty] | 2015-03-31
NV_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 466.1536 | 402.5872 | [6 empty] | 2015-03-31
NV_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 466.1536 | 402.5872 | [6 empty] | 2015-03-31
NV_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
NV_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
NV_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 487.3424 | 550.9088 | 487.3424 | [6 empty] | 2015-03-31
NV_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 487.3424 | 550.9088 | 487.3424 | [6 empty] | 2015-03-31
NV_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
NV_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 678.0416 | 762.7968 | 699.2304 | [6 empty] | 2015-03-31
NV_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NV_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.19166 | 0.18285 | 0.15821 | 0.1539 | [6 empty] | 2015-03-31
NV_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.19052 | 0.18195 | 0.15624 | 0.15206 | [6 empty] | 2015-03-31
NV_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.24596 | 0.23453 | 0.19586 | 0.18985 | [6 empty] | 2015-03-31
NV_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.30337 | 0.2855 | 0.28304 | 0.27547 | [6 empty] | 2015-03-31
NV_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.19807 | 0.18715 | 0.16882 | 0.16411 | [6 empty] | 2015-03-31
NV_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.20235 | 0.19139 | 0.17408 | 0.16946 | [6 empty] | 2015-03-31
NV_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.30988 | 0.29087 | 0.29053 | 0.28094 | [6 empty] | 2015-03-31
NV_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.49684 | 0.47803 | 0.45528 | 0.44179 | [6 empty] | 2015-03-31
NV_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.49494 | 0.47653 | 0.45194 | 0.43869 | [6 empty] | 2015-03-31
NV_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.64214 | 0.61416 | 0.57227 | 0.55268 | [6 empty] | 2015-03-31
NV_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.76775 | 0.7248 | 0.76845 | 0.74362 | [6 empty] | 2015-03-31
NV_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.51615 | 0.49205 | 0.49481 | 0.47897 | [6 empty] | 2015-03-31
NV_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.51731 | 0.49305 | 0.49671 | 0.48105 | [6 empty] | 2015-03-31
NV_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.70691 | 0.66865 | 0.67592 | 0.65259 | [6 empty] | 2015-03-31
NV_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.78436 | 0.7383 | 0.79587 | 0.7657 | [6 empty] | 2015-03-31
NV_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.77027 | 0.74797 | 0.75066 | 0.74578 | [6 empty] | 2015-03-31
NV_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.34297 | 0.31617 | 0.32372 | 0.28644 | [6 empty] | 2015-03-31
NV_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.34262 | 0.31439 | 0.32319 | 0.28288 | [6 empty] | 2015-03-31
NV_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.4391 | 0.40327 | 0.41046 | 0.36023 | [6 empty] | 2015-03-31
NV_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.50849 | 0.46583 | 0.51345 | 0.47 | [6 empty] | 2015-03-31
NV_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.38554 | 0.35115 | 0.39423 | 0.34462 | [6 empty] | 2015-03-31
NV_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.38617 | 0.35172 | 0.39528 | 0.34597 | [6 empty] | 2015-03-31
NV_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.48467 | 0.44382 | 0.4866 | 0.43404 | [6 empty] | 2015-03-31
NV_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.52968 | 0.48422 | 0.54357 | 0.49163 | [6 empty] | 2015-03-31
NM_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6339 | 1.5811 | 1.6923 | 1.5452 | 1.623 | 1.4875 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8007 | 1.7051 | 1.9037 | 1.7035 | 1.8165 | 1.646 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5234 | 1.3702 | 1.6796 | 1.587 | 1.5935 | 1.5296 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7332 | 1.6612 | 1.8153 | 1.6327 | 1.725 | 1.5662 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7788 | 1.6231 | 1.9728 | 1.8173 | 1.8789 | 1.7604 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 762.7968 | 699.2304 | 720.4192 | 678.0416 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 847.552 | 762.7968 | 826.3632 | 741.608 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 762.7968 | 720.4192 | 720.4192 | 678.0416 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 783.9856 | 741.608 | 826.3632 | 741.608 | 783.9856 | 699.2304 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 805.1744 | 720.4192 | 889.9296 | 826.3632 | 847.552 | 783.9856 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.5114 | 0.49114 | 0.54007 | 0.49312 | 0.51793 | 0.47468 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.57464 | 0.54412 | 0.60751 | 0.54362 | 0.5797 | 0.52528 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.48616 | 0.43727 | 0.53601 | 0.50646 | 0.50854 | 0.48813 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.55312 | 0.53012 | 0.57931 | 0.52105 | 0.55048 | 0.49981 |  |  |  |  | 2015-03-31
NM_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.56767 | 0.51798 | 0.62957 | 0.57994 | 0.59958 | 0.56178 |  |  |  |  | 2015-03-31
NM_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11886.9168 | 11484.3296 | 12522.5808 | 11823.3504 | 11717.4064 | 11293.6304 |  |  |  |  | 2015-03-31
NM_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 27015.72 | 25935.0912 | 29558.376 | 29113.4112 | 28647.2576 | 28265.8592 |  |  |  |  | 2015-03-31
NM_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 215235.8307 | 204069.3331 | 238734.21 | 234390.506 | 231063.8643 | 226698.9715 |  |  |  |  | 2015-03-31
NM_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 24239.9872 | 22502.5056 | 28265.8592 | 26019.8464 | 27948.0272 | 25638.448 |  |  |  |  | 2015-03-31
NM_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NM_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NM_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NM_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NM_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
NM_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
NM_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
NM_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
NM_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
NM_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
NM_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
NM_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
NM_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NM_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NM_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NM_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 335.0203 | 322.5629 | 288.7425 | 283.1531 | 291.1032 | 285.6514 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 335.0203 | 322.5629 | 288.7425 | 283.1531 | 291.1032 | 285.6514 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
NM_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 317.9806 | 306.1649 | 274.0651 | 268.7593 | 276.3013 | 271.1277 |  |  |  |  | 2015-03-31
NM_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 317.9806 | 306.1649 | 274.0651 | 268.7593 | 276.3013 | 271.1277 |  |  |  |  | 2015-03-31
NM_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.3036 | 4.348 | 3.7931 | 3.6917 | 4.083 | 3.967 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1577.589 | 759.4635 | 1359.6708 | 666.6741 | 1370.7867 | 672.5577 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 759.4635 | 0 | 666.6741 | 0 | 672.5577 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1577.589 | 1518.9285 | 1359.6708 | 1333.3498 | 1370.7867 | 1345.1139 |  |  |  |  | 2015-03-31
NM_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 865.3912 | 874.3133 | 762.7366 | 742.3451 | 821.0277 | 797.7056 |  |  |  |  | 2015-03-31
NM_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1840.698 | 1765.409 | 1608.9663 | 1568.9918 | 1622.1221 | 1582.8339 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NM_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 12.7587 | 12.315 | 13.4438 | 12.6793 | 12.5726 | 12.1296 |  |  |  |  | 2015-03-31
NM_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 38.6737 | 35.2856 | 42.3151 | 39.4402 | 41.0217 | 38.4596 |  |  |  |  | 2015-03-31
NM_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 302.6855 | 271.556 | 335.7283 | 311.8986 | 324.9407 | 318.7986 |  |  |  |  | 2015-03-31
NM_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.8595 | 30.6171 | 40.4698 | 35.3954 | 40.0029 | 34.8836 |  |  |  |  | 2015-03-31
NM_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 48.0241 | 47.9318 | 51.7245 | 51.4957 | 50.651 | 50.563 |  |  |  |  | 2015-03-31
NM_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.8633 | 0.85501 | 0.96255 | 0.9462 | 0.95037 | 0.9342 |  |  |  |  | 2015-03-31
NM_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.7068 | 10.4609 | 12.0885 | 11.8355 | 11.9662 | 11.6997 |  |  |  |  | 2015-03-31
NM_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.73139 | 0.69729 | 0.83275 | 0.80548 | 0.82489 | 0.79701 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 8.5105 | 4.097 | 7.3349 | 3.5965 | 7.3949 | 3.6282 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.097 | 0 | 3.5965 | 0 | 3.6282 |  |  |  |  | 2015-03-31
NM_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 25.5316 | 24.5822 | 22.0048 | 21.5789 | 22.1847 | 21.7693 |  |  |  |  | 2015-03-31
NM_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.7059 | 18.8988 | 16.487 | 16.0462 | 17.747 | 17.2429 |  |  |  |  | 2015-03-31
NM_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 34.0919 | 32.6992 | 29.7996 | 29.0601 | 30.0432 | 29.3165 |  |  |  |  | 2015-03-31
NM_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.0644 | 4.0289 | 4.1472 | 4.1135 | 4.1175 | 4.0915 |  |  |  |  | 2015-03-31
NM_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | YES | YES |  |  |  |  | 2015-03-31
NM_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO |  |  |  |  | 2015-03-31
NM_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | NO | NO | YES | YES |  |  |  |  | 2015-03-31
NM_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | NO | NO |  |  |  |  | 2015-03-31
NM_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4466.5431 | 4538.8506 | 4058.1979 | 3952.4904 | 4148.5239 | 4036.2046 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.2906 | 8.2631 | 8.6474 | 8.545 | 8.1688 | 8.147 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 33.5719 | 32.6767 | 33.8241 | 31.0767 | 35.2964 | 30.0094 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.0938 | 5.8365 | 6.3912 | 6.0393 | 6.2852 | 5.9393 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.1929 | 4.8616 | 5.2668 | 4.8176 | 5.1636 | 4.7198 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3686.8512 | 3665.6624 | 3898.7392 | 3856.3616 | 3686.8512 | 3665.6624 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13730.3424 | 12946.3568 | 15234.7472 | 13984.608 | 15467.824 | 13518.4544 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2542.656 | 2415.5232 | 2881.6768 | 2712.1664 | 2839.2992 | 2669.7888 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2076.5024 | 1906.992 | 2373.1456 | 2161.2576 | 2330.768 | 2118.88 |  |  |  |  | 2015-03-31
NM_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
NM_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.0322 | 2.0352 | 2.7693 | 1.8161 | 3.1556 | 2.0553 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.4944 | 2.4804 | 2.6363 | 2.605 | 2.4903 | 2.4837 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.739 | 13.8888 | 16.2349 | 14.9163 | 16.5 | 14.4975 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7793 | 1.6866 | 2.016 | 1.905 | 1.9826 | 1.8735 |  |  |  |  | 2015-03-31
NM_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4558 | 1.3378 | 1.6613 | 1.5196 | 1.6288 | 1.4888 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.8531 | 23.5568 | 22.1934 | 19.905 | 23.6591 | 21.2488 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 26.7439 | 23.7643 | 21.9372 | 19.7374 | 23.4134 | 21.1066 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 24.0328 | 21.7322 | 19.6074 | 18.0044 | 20.8836 | 19.143 |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.3754 | 27.627 | 25.7151 | 21.9349 | 25.4466 | 21.5695 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.5756 | 8.5769 | 7.6316 | 7.5465 | 7.7507 | 7.6891 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.7517 | 6.0678 | 5.5773 | 4.9187 | 5.7996 | 5.1107 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 8.4083 | 8.4083 | 8.9675 | 8.9675 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8051.744 | 7077.0592 | 9195.9392 | 7839.856 | 9132.3728 | 7776.2896 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 8030.5552 | 7140.6256 | 9047.6176 | 7776.2896 | 8984.0512 | 7712.7232 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7204.192 | 6526.1504 | 8221.2544 | 7246.5696 | 8157.688 | 7119.4368 |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9937.5472 | 8984.0512 | 11569.0848 | 9873.9808 | 11463.1408 | 9704.4704 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3135.9424 | 3114.7536 | 3432.5856 | 3390.208 | 3390.208 | 3347.8304 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2055.3136 | 1822.2368 | 2373.1456 | 2012.936 | 2351.9568 | 1991.7472 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
NM_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | n/a | n/a |  |  |  |  | 2015-03-31
NM_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
NM_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
NM_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NM_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NM_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NM_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NM_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7069.0287 | 7852.8447 | 7832.2916 | 7852.8447 | 7772.9206 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7131.2813 | 7852.8447 | 7766.3309 | 7852.8447 | 7720.9233 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6521.4677 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 825.0071 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NM_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NM_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NM_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.3421 | 1.2541 | 1.3141 | 1.1716 | 1.4082 | 1.2442 |  |  |  |  | 2015-03-31
NM_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 134.9338 | 126.0949 | 132.1251 | 117.7947 | 141.5805 | 125.0953 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.7982 | 10.3499 | 13.47 | 11.4674 | 13.3699 | 11.3805 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.7502 | 10.4411 | 13.2423 | 11.3709 | 13.1584 | 11.3044 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.559 | 9.6211 | 12.0297 | 10.6074 | 11.9395 | 10.4351 |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.5605 | 13.1624 | 16.8393 | 14.4571 | 16.6635 | 14.2163 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.118 | 2.1108 | 2.3266 | 2.2957 | 2.2977 | 2.2656 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4444 | 1.2759 | 1.6659 | 1.4124 | 1.6468 | 1.3885 |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
NM_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.9167 | 2.7256 | 2.856 | 2.5462 | 3.0603 | 2.704 |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NM_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NM_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | NO | NO | NO | NO | YES | YES |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NM_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NM_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 94.5371 | 89.9864 | 93.9217 | 84.9336 | 96.1996 | 86.2071 |  |  |  |  | 2015-03-31
NM_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0048 | 1.954 | 1.7438 | 1.6381 | 1.7559 | 1.6487 |  |  |  |  | 2015-03-31
NM_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.568 | 5.4173 | 4.6737 | 4.5306 | 4.7981 | 4.6201 |  |  |  |  | 2015-03-31
NM_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.8573 | 2.8043 | 2.4782 | 2.3579 | 2.5268 | 2.3992 |  |  |  |  | 2015-03-31
NM_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.2798 | 4.2462 | 4.0029 | 3.9598 | 4.0333 | 3.9927 |  |  |  |  | 2015-03-31
NM_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 783.9856 | 762.7968 | 783.9856 | 741.608 | 783.9856 | 720.4192 |  |  |  |  | 2015-03-31
NM_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1885.8032 | 1822.2368 | 1928.1808 | 1843.4256 | 1906.992 | 1822.2368 |  |  |  |  | 2015-03-31
NM_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 911.1184 | 868.7408 | 911.1184 | 847.552 |  |  |  |  | 2015-03-31
NM_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1695.104 | 1673.9152 | 1801.048 | 1779.8592 | 1779.8592 | 1758.6704 |  |  |  |  | 2015-03-31
NM_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
NM_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
NM_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
NM_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
NM_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NM_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NM_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NM_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.3272 | 1.281 | 1.3461 | 1.2978 | 1.335 | 1.2765 |  |  |  |  | 2015-03-31
NM_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.1849 | 1.1731 | 1.2627 | 1.2491 | 1.2422 | 1.2271 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.58159 | 0.55508 | 0.54348 | 0.53774 | 0.53272 | 0.51658 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.57737 | 0.55172 | 0.53746 | 0.53207 | 0.52668 | 0.51098 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.72192 | 0.66732 | 0.68564 | 0.69131 | 0.66757 | 0.65752 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.9436 | 0.87928 | 0.93258 | 0.92738 | 0.93373 | 0.90644 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.56967 | 0.53811 | 0.53197 | 0.52311 | 0.52465 | 0.50276 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.56546 | 0.54078 | 0.54462 | 0.53928 | 0.53081 | 0.51424 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.93449 | 0.87395 | 0.94016 | 0.93088 | 0.94331 | 0.91101 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4848 | 1.42 | 1.5221 | 1.4963 | 1.5158 | 1.4666 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4771 | 1.4138 | 1.5121 | 1.487 | 1.5058 | 1.4573 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8643 | 1.743 | 1.9536 | 1.9395 | 1.941 | 1.894 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3616 | 2.2039 | 2.4943 | 2.4558 | 2.5165 | 2.4303 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.4656 | 1.4076 | 1.5201 | 1.4903 | 1.5197 | 1.4626 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.4602 | 1.4033 | 1.5258 | 1.4967 | 1.5223 | 1.4682 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9635 | 1.9152 | 2.1118 | 2.0735 | 2.1171 | 2.0374 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.3529 | 2.1949 | 2.5275 | 2.4767 | 2.5555 | 2.4572 |  |  |  |  | 2015-03-31
NM_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2462 | 2.18 | 2.4187 | 2.4266 | 2.3391 | 2.3408 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.99703 | 0.92394 | 1.0852 | 0.97277 | 1.0931 | 0.96494 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.98957 | 0.91727 | 1.0852 | 0.9619 | 1.0918 | 0.95452 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2534 | 1.1524 | 1.3736 | 1.2238 | 1.3852 | 1.2132 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5242 | 1.391 | 1.6811 | 1.5571 | 1.7011 | 1.5502 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0979 | 1.0086 | 1.238 | 1.0854 | 1.2401 | 1.0735 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1006 | 1.0108 | 1.2412 | 1.0895 | 1.2434 | 1.0774 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3563 | 1.2454 | 1.5398 | 1.3858 | 1.5496 | 1.3717 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.5278 | 1.3918 | 1.7341 | 1.5918 | 1.7496 | 1.5805 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NM_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 254.2656 | 233.0768 | 233.0768 | 233.0768 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 233.0768 | 233.0768 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 296.6432 | 317.832 | 317.832 | 296.6432 | 296.6432 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 402.5872 | 423.776 | 423.776 | 423.776 | 402.5872 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 233.0768 | 233.0768 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 233.0768 | 254.2656 | 233.0768 | 233.0768 | 233.0768 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 423.776 | 423.776 | 423.776 | 402.5872 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 678.0416 | 678.0416 | 656.8528 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 678.0416 | 678.0416 | 678.0416 | 656.8528 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 783.9856 | 889.9296 | 868.7408 | 868.7408 | 847.552 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 995.8736 | 1123.0064 | 1101.8176 | 1123.0064 | 1101.8176 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 678.0416 | 678.0416 | 678.0416 | 656.8528 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 678.0416 | 678.0416 | 678.0416 | 656.8528 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 953.496 | 932.3072 | 953.496 | 911.1184 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 995.8736 | 1144.1952 | 1123.0064 | 1144.1952 | 1101.8176 |  |  |  |  | 2015-03-31
NM_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 974.6848 | 1080.6288 | 1101.8176 | 1059.44 | 1059.44 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 423.776 | 487.3424 | 444.9648 | 487.3424 | 444.9648 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 402.5872 | 487.3424 | 423.776 | 487.3424 | 423.776 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 614.4752 | 550.9088 | 614.4752 | 550.9088 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 635.664 | 762.7968 | 699.2304 | 762.7968 | 699.2304 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 550.9088 | 487.3424 | 550.9088 | 487.3424 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 550.9088 | 487.3424 | 550.9088 | 487.3424 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 699.2304 | 614.4752 | 699.2304 | 614.4752 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 635.664 | 783.9856 | 720.4192 | 783.9856 | 720.4192 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.18267 | 0.17315 | 0.17343 | 0.17161 | 0.17 | 0.16485 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.18116 | 0.17195 | 0.17152 | 0.1698 | 0.16807 | 0.16307 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.22484 | 0.21094 | 0.2188 | 0.22061 | 0.21303 | 0.20983 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.30113 | 0.2806 | 0.29761 | 0.29595 | 0.29798 | 0.28927 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.17297 | 0.16367 | 0.16976 | 0.16693 | 0.16743 | 0.16044 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.17512 | 0.16631 | 0.1738 | 0.17209 | 0.1694 | 0.1641 |  |  |  |  | 2015-03-31
NM_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.29822 | 0.2776 | 0.30003 | 0.29706 | 0.30103 | 0.29072 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.47384 | 0.45314 | 0.48573 | 0.47752 | 0.48375 | 0.46803 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.47138 | 0.45119 | 0.48254 | 0.47453 | 0.48053 | 0.46507 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.59415 | 0.55622 | 0.62345 | 0.61894 | 0.61943 | 0.60441 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.75365 | 0.7033 | 0.79598 | 0.78369 | 0.80306 | 0.77557 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.45744 | 0.43685 | 0.4851 | 0.47558 | 0.48498 | 0.46676 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.45552 | 0.43534 | 0.48693 | 0.47763 | 0.48581 | 0.46853 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.61714 | 0.57854 | 0.67392 | 0.66171 | 0.67561 | 0.65018 |  |  |  |  | 2015-03-31
NM_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.75085 | 0.70043 | 0.80657 | 0.79039 | 0.8155 | 0.78415 |  |  |  |  | 2015-03-31
NM_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.7168 | 0.69568 | 0.77188 | 0.77437 | 0.74647 | 0.747 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.31817 | 0.29485 | 0.34632 | 0.31043 | 0.34881 | 0.30794 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.3158 | 0.29272 | 0.34632 | 0.30696 | 0.34842 | 0.30461 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.39166 | 0.35682 | 0.43835 | 0.39053 | 0.44205 | 0.38715 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.4864 | 0.44391 | 0.53648 | 0.49692 | 0.54286 | 0.49469 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.33803 | 0.30728 | 0.39509 | 0.34639 | 0.39575 | 0.34256 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.33893 | 0.30806 | 0.3961 | 0.3477 | 0.39681 | 0.34381 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.42553 | 0.38737 | 0.49139 | 0.44223 | 0.4945 | 0.43774 |  |  |  |  | 2015-03-31
NM_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.48757 | 0.44416 | 0.5534 | 0.50797 | 0.55835 | 0.50437 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7038 | 1.6481 | 1.5983 | 1.4637 | 1.5893 | 1.4707 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0072 | 1.9182 | 1.973 | 1.8119 | 1.8286 | 1.7084 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5748 | 1.4319 | 1.6099 | 1.5407 | 1.5555 | 1.5295 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8774 | 1.808 | 1.6992 | 1.5413 | 1.608 | 1.5041 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.812 | 1.6649 | 1.8543 | 1.7363 | 1.8511 | 1.7831 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 741.608 | 699.2304 | 720.4192 | 656.8528 | 720.4192 | 656.8528 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 911.1184 | 868.7408 | 889.9296 | 805.1744 | 826.3632 | 762.7968 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 699.2304 | 635.664 | 720.4192 | 699.2304 | 699.2304 | 678.0416 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 847.552 | 805.1744 | 762.7968 | 699.2304 | 720.4192 | 678.0416 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 805.1744 | 741.608 | 826.3632 | 783.9856 | 826.3632 | 805.1744 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | gravity | gravity | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.52053 | 0.50042 | 0.51006 | 0.4671 | 0.50717 | 0.46936 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.63897 | 0.60909 | 0.62964 | 0.57822 | 0.58356 | 0.54519 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.50255 | 0.45694 | 0.51377 | 0.49167 | 0.49638 | 0.48811 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.59914 | 0.57571 | 0.54224 | 0.49187 | 0.51316 | 0.47998 |  |  |  |  | 2015-03-31
UT_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.57824 | 0.53131 | 0.59177 | 0.5541 | 0.59072 | 0.56902 |  |  |  |  | 2015-03-31
UT_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11802.1616 | 11399.5744 | 11463.1408 | 11060.5536 | 11759.784 | 11314.8192 |  |  |  |  | 2015-03-31
UT_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 27460.6848 | 26464.8112 | 28392.992 | 27948.0272 | 28774.3904 | 28392.992 |  |  |  |  | 2015-03-31
UT_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 221931.4915 | 211612.5459 | 229877.2915 | 225448.8323 | 231042.6755 | 227207.5027 |  |  |  |  | 2015-03-31
UT_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 25723.2032 | 23922.1552 | 27863.272 | 25638.448 | 27948.0272 | 25765.5808 |  |  |  |  | 2015-03-31
UT_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
UT_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | 2015-03-31
UT_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | 2015-03-31
UT_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | 2015-03-31
UT_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
UT_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
UT_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
UT_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
UT_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
UT_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
UT_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
UT_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
UT_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
UT_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
UT_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
UT_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes |  |  |  |  | 2015-03-31
UT_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes |  |  |  |  | 2015-03-31
UT_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes |  |  |  |  | 2015-03-31
UT_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
UT_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
UT_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
UT_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 329.1514 | 317.7835 | 308.8965 | 303.2464 | 289.1726 | 284.1077 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 329.1514 | 317.7835 | 308.8965 | 303.2464 | 289.1726 | 284.1077 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
UT_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 312.4102 | 301.6264 | 293.1847 | 287.8259 | 274.4621 | 269.659 |  |  |  |  | 2015-03-31
UT_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 312.4102 | 301.6264 | 293.1847 | 287.8259 | 274.4621 | 269.659 |  |  |  |  | 2015-03-31
UT_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.5729 | 3.5685 | 4.2488 | 4.1607 | 4.4718 | 4.3419 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1549.9524 | 748.2113 | 1454.5731 | 713.9841 | 1361.6949 | 668.9217 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 748.2113 | 0 | 713.9841 | 0 | 668.9217 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1549.9524 | 1496.4227 | 1454.5731 | 1427.9683 | 1361.6949 | 1337.8449 |  |  |  |  | 2015-03-31
UT_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 718.4698 | 717.5695 | 854.3816 | 836.6514 | 899.2205 | 873.0865 |  |  |  |  | 2015-03-31
UT_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1808.3634 | 1739.256 | 1697.0941 | 1659.6873 | 1611.3439 | 1574.281 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
UT_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 12.6709 | 12.2335 | 12.306 | 11.8711 | 12.623 | 12.1475 |  |  |  |  | 2015-03-31
UT_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 39.3005 | 35.9893 | 40.6395 | 38.0101 | 41.2076 | 40.6343 |  |  |  |  | 2015-03-31
UT_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 312.111 | 281.5907 | 323.2787 | 317.0497 | 324.9063 | 319.5101 |  |  |  |  | 2015-03-31
UT_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 36.9793 | 32.5431 | 39.8946 | 34.887 | 39.997 | 37.0415 |  |  |  |  | 2015-03-31
UT_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 47.7317 | 47.6412 | 49.4242 | 49.3377 | 51.3508 | 51.2493 |  |  |  |  | 2015-03-31
UT_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.85639 | 0.84978 | 0.93291 | 0.91623 | 0.97956 | 0.96064 |  |  |  |  | 2015-03-31
UT_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.5344 | 10.4327 | 11.7636 | 11.492 | 12.3712 | 12.072 |  |  |  |  | 2015-03-31
UT_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.72136 | 0.69313 | 0.8096 | 0.78182 | 0.84888 | 0.81939 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 8.3614 | 4.0363 | 7.8469 | 3.8517 | 7.3459 | 3.6086 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.0363 | 0 | 3.8517 | 0 | 3.6086 |  |  |  |  | 2015-03-31
UT_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 25.0844 | 24.218 | 23.5407 | 23.1102 | 22.0376 | 21.6516 |  |  |  |  | 2015-03-31
UT_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 15.5301 | 15.5107 | 18.468 | 18.0847 | 19.4372 | 18.8723 |  |  |  |  | 2015-03-31
UT_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 33.4946 | 32.2147 | 31.4335 | 30.741 | 29.844 | 29.158 |  |  |  |  | 2015-03-31
UT_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.0359 | 4.0084 | 4.1095 | 4.0827 | 4.1541 | 4.1251 |  |  |  |  | 2015-03-31
UT_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | YES | YES |  |  |  |  | 2015-03-31
UT_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | YES | YES |  |  |  |  | 2015-03-31
UT_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 471.8063 | 469.2702 | 513.793 | 495.0889 | 518.7729 | 497.3357 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.7543 | 8.6775 | 8.2471 | 8.179 | 7.8175 | 7.8584 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 33.0705 | 31.7966 | 36.9625 | 30.083 | 31.3345 | 29.7277 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.9216 | 6.601 | 6.7411 | 6.413 | 6.5352 | 6.2256 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.9771 | 5.5781 | 5.6487 | 5.2334 | 5.3737 | 4.9677 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3941.1168 | 3898.7392 | 3708.04 | 3686.8512 | 3517.3408 | 3538.5296 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14217.6848 | 13306.5664 | 15128.8032 | 13454.888 | 14111.7408 | 13391.3216 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2818.1104 | 2669.7888 | 3029.9984 | 2881.6768 | 2945.2432 | 2796.9216 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2373.1456 | 2182.4464 | 2542.656 | 2351.9568 | 2415.5232 | 2246.0128 |  |  |  |  | 2015-03-31
UT_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
UT_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | No | No |  |  |  |  | 2015-03-31
UT_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.2522 | 1.4112 | 3.2627 | 2.1391 | 3.7666 | 2.5258 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.6688 | 2.6454 | 2.5142 | 2.4935 | 2.3832 | 2.3957 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 15.1678 | 14.2865 | 16.1268 | 14.44 | 15.04 | 14.3614 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.977 | 1.8688 | 2.0551 | 2.0229 | 2.0614 | 1.9638 |  |  |  |  | 2015-03-31
UT_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.659 | 1.5255 | 1.7818 | 1.649 | 1.6951 | 1.567 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 29.1839 | 25.5236 | 28.3021 | 25.7158 | 24.463 | 22.264 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 28.8107 | 25.6339 | 28.0451 | 25.4843 | 24.2383 | 22.1023 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 25.9393 | 23.5175 | 24.9755 | 23.0628 | 21.6356 | 20.0811 |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.6416 | 27.589 | 26.9698 | 24.1306 | 25.1861 | 21.5106 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.745 | 8.7389 | 8.1093 | 8.0483 | 9.8749 | 9.7509 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.8565 | 6.2146 | 6.3165 | 5.6554 | 5.6732 | 5.0309 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.3502 | 10.3502 | 9.1515 | 9.1515 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8750.9744 | 7649.1568 | 9323.072 | 8009.3664 | 9195.9392 | 7861.0448 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 8645.0304 | 7691.5344 | 9174.7504 | 7882.2336 | 9047.6176 | 7797.4784 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7776.2896 | 7055.8704 | 8369.576 | 7331.3248 | 8242.4432 | 7310.136 |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 10615.5888 | 9471.3936 | 11420.7632 | 9725.6592 | 11336.008 | 9683.2816 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3135.9424 | 3114.7536 | 3326.6416 | 3284.264 | 3411.3968 | 3369.0192 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2097.6912 | 1864.6144 | 2309.5792 | 1949.3696 | 2288.3904 | 1949.3696 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
UT_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | n/a |  |  |  |  | 2015-03-31
UT_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | VFD | VFD |  |  |  |  | 2015-03-31
UT_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | n/a | VFD |  |  |  |  | 2015-03-31
UT_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
UT_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2015-03-31
UT_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | Yes | No | Yes | No | No |  |  |  |  | 2015-03-31
UT_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | Yes | No | Yes | No | No |  |  |  |  | 2015-03-31
UT_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | Yes | No | Yes | No | No |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7659.2003 | 7852.8447 | 7852.8447 | 7852.8447 | 7852.8447 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7692.2972 | 7852.8447 | 7852.8447 | 7852.8447 | 7799.8304 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 1434.9903 | 1434.9903 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
UT_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | No | Yes | No | Yes | Yes |  |  |  |  | 2015-03-31
UT_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | No | Yes | No | Yes | Yes |  |  |  |  | 2015-03-31
UT_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | No | Yes | No | Yes | Yes |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2015-03-31
UT_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2015-03-31
UT_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2015-03-31
UT_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
UT_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.2612 | 1.1618 | 1.4803 | 1.3086 | 1.5118 | 1.3324 |  |  |  |  | 2015-03-31
UT_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 126.8088 | 116.814 | 148.8353 | 131.5727 | 152.0036 | 133.9611 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 12.8222 | 11.214 | 13.6583 | 11.7236 | 13.4513 | 11.5076 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 12.6583 | 11.2625 | 13.4426 | 11.5484 | 13.251 | 11.4199 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 11.3967 | 10.3327 | 12.2506 | 10.7479 | 12.0766 | 10.6901 |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 15.428 | 13.878 | 16.6231 | 14.2489 | 16.4929 | 14.1775 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.1218 | 2.1127 | 2.2486 | 2.2177 | 2.3041 | 2.2752 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.477 | 1.3067 | 1.6177 | 1.3694 | 1.607 | 1.3634 |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
UT_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.741 | 2.525 | 3.2172 | 2.844 | 3.2857 | 2.8956 |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
UT_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 97.0276 | 90.2825 | 99.6728 | 89.2598 | 96.8716 | 86.3789 |  |  |  |  | 2015-03-31
UT_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2026 | 2.1121 | 1.9146 | 1.7793 | 1.7192 | 1.5995 |  |  |  |  | 2015-03-31
UT_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.8093 | 5.6804 | 5.0238 | 4.8697 | 4.632 | 4.4885 |  |  |  |  | 2015-03-31
UT_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.9693 | 2.8617 | 2.6262 | 2.4972 | 2.4511 | 2.3322 |  |  |  |  | 2015-03-31
UT_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.514 | 4.469 | 4.1644 | 4.1203 | 3.9662 | 3.9224 |  |  |  |  | 2015-03-31
UT_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 847.552 | 805.1744 | 805.1744 | 741.608 | 762.7968 | 699.2304 |  |  |  |  | 2015-03-31
UT_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1970.5584 | 1885.8032 | 1885.8032 | 1801.048 | 1864.6144 | 1779.8592 |  |  |  |  | 2015-03-31
UT_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 911.1184 | 868.7408 | 889.9296 | 826.3632 | 889.9296 | 826.3632 |  |  |  |  | 2015-03-31
UT_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1716.2928 | 1695.104 | 1758.6704 | 1737.4816 | 1779.8592 | 1758.6704 |  |  |  |  | 2015-03-31
UT_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
UT_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
UT_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
UT_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
UT_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
UT_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
UT_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | No |  |  |  |  | 2015-03-31
UT_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
UT_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | No | No | No | No | No |  |  |  |  | 2015-03-31
UT_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.3749 | 1.3288 | 1.3149 | 1.2656 | 1.3003 | 1.2515 |  |  |  |  | 2015-03-31
UT_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.2089 | 1.1946 | 1.2339 | 1.218 | 1.2511 | 1.2373 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.62601 | 0.59908 | 0.53393 | 0.51763 | 0.48272 | 0.47254 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.6222 | 0.59606 | 0.52794 | 0.51207 | 0.4763 | 0.46659 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.80119 | 0.7536 | 0.68612 | 0.67358 | 0.59099 | 0.58823 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0054 | 0.94471 | 0.9302 | 0.90218 | 0.87416 | 0.84884 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.71245 | 0.67687 | 0.60289 | 0.58828 | 0.52662 | 0.51087 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.72496 | 0.6893 | 0.61814 | 0.60235 | 0.54346 | 0.52846 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0264 | 0.95996 | 0.98517 | 0.95166 | 0.91195 | 0.87581 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6001 | 1.5381 | 1.5139 | 1.464 | 1.4438 | 1.401 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5935 | 1.533 | 1.5039 | 1.4548 | 1.4328 | 1.3908 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0803 | 1.9691 | 1.9821 | 1.9291 | 1.8146 | 1.7758 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.5224 | 2.3761 | 2.5051 | 2.4172 | 2.4269 | 2.3368 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8072 | 1.7283 | 1.7271 | 1.6727 | 1.5951 | 1.5328 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8117 | 1.7321 | 1.7333 | 1.6791 | 1.6015 | 1.5396 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.4101 | 2.2833 | 2.3474 | 2.2656 | 2.1592 | 2.0647 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5806 | 2.4241 | 2.669 | 2.5658 | 2.5473 | 2.4291 |  |  |  |  | 2015-03-31
UT_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.3417 | 2.2777 | 2.3477 | 2.3483 | 2.3638 | 2.352 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1008 | 1.0221 | 1.0824 | 0.95135 | 1.0184 | 0.90272 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0937 | 1.0164 | 1.0815 | 0.94134 | 1.017 | 0.89113 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4516 | 1.3395 | 1.3783 | 1.2172 | 1.2816 | 1.1161 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6465 | 1.512 | 1.6839 | 1.5358 | 1.6263 | 1.4839 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2974 | 1.1899 | 1.3542 | 1.1917 | 1.2746 | 1.1081 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3002 | 1.1924 | 1.3584 | 1.1962 | 1.2795 | 1.1127 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6118 | 1.4827 | 1.6708 | 1.4964 | 1.5603 | 1.3781 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7014 | 1.5567 | 1.8102 | 1.6364 | 1.7305 | 1.5505 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
UT_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 233.0768 | 233.0768 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 233.0768 | 233.0768 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | 317.832 | 296.6432 | 275.4544 | 254.2656 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 423.776 | 423.776 | 402.5872 | 402.5872 | 381.3984 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 275.4544 | 254.2656 | 233.0768 | 233.0768 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 275.4544 | 275.4544 | 275.4544 | 254.2656 | 233.0768 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 423.776 | 444.9648 | 423.776 | 402.5872 | 402.5872 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 678.0416 | 656.8528 | 656.8528 | 635.664 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 678.0416 | 656.8528 | 635.664 | 635.664 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 889.9296 | 889.9296 | 868.7408 | 826.3632 | 805.1744 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1144.1952 | 1059.44 | 1123.0064 | 1080.6288 | 1101.8176 | 1059.44 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 720.4192 | 783.9856 | 762.7968 | 720.4192 | 699.2304 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 720.4192 | 783.9856 | 762.7968 | 720.4192 | 699.2304 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 974.6848 | 1059.44 | 1017.0624 | 974.6848 | 932.3072 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1165.384 | 1101.8176 | 1207.7616 | 1165.384 | 1144.1952 | 1101.8176 |  |  |  |  | 2015-03-31
UT_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 1017.0624 | 1059.44 | 1059.44 | 1059.44 | 1059.44 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 466.1536 | 487.3424 | 423.776 | 466.1536 | 402.5872 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 466.1536 | 487.3424 | 423.776 | 466.1536 | 402.5872 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 614.4752 | 550.9088 | 572.0976 | 508.5312 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 678.0416 | 762.7968 | 699.2304 | 741.608 | 678.0416 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 614.4752 | 529.72 | 572.0976 | 508.5312 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 614.4752 | 529.72 | 572.0976 | 508.5312 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 635.664 | 741.608 | 678.0416 | 699.2304 | 614.4752 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 805.1744 | 741.608 | 783.9856 | 699.2304 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.19911 | 0.18985 | 0.17039 | 0.16519 | 0.15404 | 0.1508 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.1978 | 0.1888 | 0.16847 | 0.16342 | 0.152 | 0.14891 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.25359 | 0.24049 | 0.21896 | 0.21495 | 0.1886 | 0.18772 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.32084 | 0.30148 | 0.29685 | 0.2879 | 0.27896 | 0.27089 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.20249 | 0.19103 | 0.1924 | 0.18722 | 0.16806 | 0.16303 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.20652 | 0.19504 | 0.19726 | 0.19222 | 0.17343 | 0.16865 |  |  |  |  | 2015-03-31
UT_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.32667 | 0.30634 | 0.31439 | 0.3037 | 0.29103 | 0.2795 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.51062 | 0.49084 | 0.48313 | 0.46721 | 0.46075 | 0.44708 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.50854 | 0.4892 | 0.47994 | 0.46425 | 0.45723 | 0.44384 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.66386 | 0.62838 | 0.63255 | 0.61562 | 0.57908 | 0.56669 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.80495 | 0.75827 | 0.79945 | 0.77137 | 0.77448 | 0.74573 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.53079 | 0.5053 | 0.55116 | 0.53379 | 0.50903 | 0.48916 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.53224 | 0.50653 | 0.55313 | 0.53583 | 0.51109 | 0.49132 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.73126 | 0.6902 | 0.74909 | 0.723 | 0.68904 | 0.65888 |  |  |  |  | 2015-03-31
UT_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.82352 | 0.7736 | 0.85174 | 0.81881 | 0.81291 | 0.77519 |  |  |  |  | 2015-03-31
UT_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.7473 | 0.72687 | 0.74922 | 0.7494 | 0.75432 | 0.75057 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.35131 | 0.32616 | 0.34543 | 0.30359 | 0.32498 | 0.28808 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.34903 | 0.32435 | 0.34514 | 0.3004 | 0.32454 | 0.28438 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.44774 | 0.41141 | 0.43986 | 0.38844 | 0.40898 | 0.35619 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.52543 | 0.48251 | 0.53736 | 0.49012 | 0.51899 | 0.47356 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.39409 | 0.3593 | 0.43216 | 0.3803 | 0.40676 | 0.35364 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.39497 | 0.36009 | 0.43349 | 0.38172 | 0.4083 | 0.35508 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.49964 | 0.45781 | 0.5332 | 0.47754 | 0.49792 | 0.43977 |  |  |  |  | 2015-03-31
UT_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.54297 | 0.49678 | 0.57767 | 0.52222 | 0.55223 | 0.4948 |  |  |  |  | 2015-03-31
DE_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7387 | 1.6334 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8724 | 1.7222 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3496 | 1.2884 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7115 | 1.5899 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5603 | 1.4613 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 550.9088 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 656.8528 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.4339 | 0.39788 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52028 | 0.46727 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.42478 | 0.40137 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.46484 | 0.41994 | [8 empty] | 2015-03-31
DE_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.48312 | 0.44613 | [8 empty] | 2015-03-31
DE_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10297.7568 | 9704.4704 | [8 empty] | 2015-03-31
DE_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24430.6864 | 24049.288 | [8 empty] | 2015-03-31
DE_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 197733.8819 | 194004.6531 | [8 empty] | 2015-03-31
DE_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23180.5472 | 21379.4992 | [8 empty] | 2015-03-31
DE_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
DE_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
DE_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
DE_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
DE_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
DE_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
DE_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
DE_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
DE_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
DE_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
DE_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
DE_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
DE_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | [8 empty] | 2015-03-31
DE_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
DE_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
DE_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
DE_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
DE_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
DE_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
DE_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
DE_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
DE_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
DE_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 396.7775 | 391.2687 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 396.7775 | 391.2687 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
DE_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 376.5964 | 371.3699 | [8 empty] | 2015-03-31
DE_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 376.5964 | 371.3699 | [8 empty] | 2015-03-31
DE_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.6388 | 4.5135 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1868.4361 | 921.2303 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 921.2303 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1868.4361 | 1842.4416 | [8 empty] | 2015-03-31
DE_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 932.7994 | 907.6006 | [8 empty] | 2015-03-31
DE_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2179.8949 | 2141.5372 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
DE_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0539 | 10.4241 | [8 empty] | 2015-03-31
DE_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.126 | 32.7177 | [8 empty] | 2015-03-31
DE_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 278.0811 | 272.8158 | [8 empty] | 2015-03-31
DE_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.3129 | 29.0942 | [8 empty] | 2015-03-31
DE_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.7569 | 42.569 | [8 empty] | 2015-03-31
DE_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.77825 | 0.76614 | [8 empty] | 2015-03-31
DE_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.8086 | 9.6201 | [8 empty] | 2015-03-31
DE_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.66938 | 0.64896 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.0794 | 4.9697 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.9697 | [8 empty] | 2015-03-31
DE_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 30.2381 | 29.8183 | [8 empty] | 2015-03-31
DE_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.163 | 19.6183 | [8 empty] | 2015-03-31
DE_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 40.3763 | 39.6641 | [8 empty] | 2015-03-31
DE_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8397 | 3.8109 | [8 empty] | 2015-03-31
DE_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | [8 empty] | 2015-03-31
DE_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
DE_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DE_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
DE_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4606.8449 | 4466.25 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.0872 | 8.9548 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 39.0086 | 37.258 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4316 | 6.1845 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.617 | 5.2896 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3284.264 | 3220.6976 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12628.5248 | 11547.896 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2500.2784 | 2373.1456 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2076.5024 | 1928.1808 | [8 empty] | 2015-03-31
DE_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
DE_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
DE_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.1151 | 2.0318 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2277 | 2.182 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.5464 | 12.3827 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7523 | 1.6634 | [8 empty] | 2015-03-31
DE_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4576 | 1.3438 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.2917 | 21.5319 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.8145 | 21.0833 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.6505 | 19.9147 | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.2744 | 26.5671 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.2924 | 5.3523 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7585.5904 | 6462.584 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7437.2688 | 6335.4512 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6801.6048 | 5975.2416 | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9386.6384 | 7966.9888 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1885.8032 | 1610.3488 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
DE_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | [8 empty] | 2015-03-31
DE_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
DE_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
DE_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
DE_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
DE_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
DE_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
DE_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
DE_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7589.6163 | 6461.3762 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7446.4224 | 6326.7426 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 5976.068 | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DE_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DE_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DE_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | [8 empty] | 2015-03-31
DE_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DE_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DE_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.459 | 1.3479 | [8 empty] | 2015-03-31
DE_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 146.6947 | 135.5239 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.1121 | 9.5325 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.9025 | 9.3338 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.9517 | 8.8165 | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.7407 | 11.6725 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3231 | 1.1254 | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
DE_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.1709 | 2.9294 | [8 empty] | 2015-03-31
DE_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DE_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DE_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DE_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DE_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DE_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.4268 | 97.6109 | [8 empty] | 2015-03-31
DE_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.04 | 1.9019 | [8 empty] | 2015-03-31
DE_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2589 | 5.0755 | [8 empty] | 2015-03-31
DE_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5172 | 2.3706 | [8 empty] | 2015-03-31
DE_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.3023 | 4.2647 | [8 empty] | 2015-03-31
DE_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2015-03-31
DE_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1567.9712 | 1525.5936 | [8 empty] | 2015-03-31
DE_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | [8 empty] | 2015-03-31
DE_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1483.216 | 1462.0272 | [8 empty] | 2015-03-31
DE_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
DE_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
DE_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
DE_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
DE_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DE_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
DE_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DE_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
DE_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
DE_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1058 | 1.0672 | [8 empty] | 2015-03-31
DE_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0554 | 1.0433 | [8 empty] | 2015-03-31
DE_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.6101 | 0.6048 | [8 empty] | 2015-03-31
DE_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.60578 | 0.60074 | [8 empty] | 2015-03-31
DE_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.7407 | 0.74461 | [8 empty] | 2015-03-31
DE_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.91294 | 0.90857 | [8 empty] | 2015-03-31
DE_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.68239 | 0.67873 | [8 empty] | 2015-03-31
DE_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.69568 | 0.69214 | [8 empty] | 2015-03-31
DE_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.95742 | 0.95534 | [8 empty] | 2015-03-31
DE_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6028 | 1.5803 | [8 empty] | 2015-03-31
DE_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5957 | 1.5737 | [8 empty] | 2015-03-31
DE_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.9914 | 1.9701 | [8 empty] | 2015-03-31
DE_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3653 | 2.3343 | [8 empty] | 2015-03-31
DE_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8015 | 1.7734 | [8 empty] | 2015-03-31
DE_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.806 | 1.7784 | [8 empty] | 2015-03-31
DE_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3037 | 2.2723 | [8 empty] | 2015-03-31
DE_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4765 | 2.4354 | [8 empty] | 2015-03-31
DE_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1167 | 2.1227 | [8 empty] | 2015-03-31
DE_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1003 | 0.97498 | [8 empty] | 2015-03-31
DE_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1004 | 0.96724 | [8 empty] | 2015-03-31
DE_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3543 | 1.2174 | [8 empty] | 2015-03-31
DE_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5432 | 1.4354 | [8 empty] | 2015-03-31
DE_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2914 | 1.1729 | [8 empty] | 2015-03-31
DE_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2949 | 1.1764 | [8 empty] | 2015-03-31
DE_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5555 | 1.4353 | [8 empty] | 2015-03-31
DE_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6525 | 1.5348 | [8 empty] | 2015-03-31
DE_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DE_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
DE_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DE_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DE_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DE_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DE_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DE_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DE_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DE_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DE_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
DE_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DE_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
DE_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
DE_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | [8 empty] | 2015-03-31
DE_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 317.832 | [8 empty] | 2015-03-31
DE_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
DE_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
DE_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | [8 empty] | 2015-03-31
DE_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 550.9088 | [8 empty] | 2015-03-31
DE_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 550.9088 | [8 empty] | 2015-03-31
DE_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 720.4192 | [8 empty] | 2015-03-31
DE_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | [8 empty] | 2015-03-31
DE_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | [8 empty] | 2015-03-31
DE_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | [8 empty] | 2015-03-31
DE_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 826.3632 | [8 empty] | 2015-03-31
DE_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | [8 empty] | 2015-03-31
DE_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | [8 empty] | 2015-03-31
DE_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | [8 empty] | 2015-03-31
DE_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 339.0208 | [8 empty] | 2015-03-31
DE_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | [8 empty] | 2015-03-31
DE_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2015-03-31
DE_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
DE_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
DE_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | [8 empty] | 2015-03-31
DE_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2015-03-31
DE_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DE_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.13858 | 0.13686 | [8 empty] | 2015-03-31
DE_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.1372 | 0.13558 | [8 empty] | 2015-03-31
DE_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.17872 | 0.18006 | [8 empty] | 2015-03-31
DE_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23131 | 0.2299 | [8 empty] | 2015-03-31
DE_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15313 | 0.15199 | [8 empty] | 2015-03-31
DE_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15745 | 0.15634 | [8 empty] | 2015-03-31
DE_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24133 | 0.23893 | [8 empty] | 2015-03-31
DE_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.39655 | 0.38918 | [8 empty] | 2015-03-31
DE_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.39425 | 0.38702 | [8 empty] | 2015-03-31
DE_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.51444 | 0.51022 | [8 empty] | 2015-03-31
DE_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.63049 | 0.62029 | [8 empty] | 2015-03-31
DE_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.44027 | 0.43217 | [8 empty] | 2015-03-31
DE_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.44176 | 0.43383 | [8 empty] | 2015-03-31
DE_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.59253 | 0.58238 | [8 empty] | 2015-03-31
DE_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.66116 | 0.64762 | [8 empty] | 2015-03-31
DE_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64614 | 0.6483 | [8 empty] | 2015-03-31
DE_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.28101 | 0.25017 | [8 empty] | 2015-03-31
DE_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.28108 | 0.24763 | [8 empty] | 2015-03-31
DE_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.35462 | 0.32181 | [8 empty] | 2015-03-31
DE_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.42344 | 0.38996 | [8 empty] | 2015-03-31
DE_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34395 | 0.3052 | [8 empty] | 2015-03-31
DE_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34509 | 0.30637 | [8 empty] | 2015-03-31
DE_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.4217 | 0.38243 | [8 empty] | 2015-03-31
DE_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.4549 | 0.41621 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7505 | 1.6474 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8976 | 1.742 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3695 | 1.3 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7423 | 1.6107 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5868 | 1.4874 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 656.8528 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 635.664 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.43606 | 0.39969 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52368 | 0.46945 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.43068 | 0.40618 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.47207 | 0.4248 | [8 empty] | 2015-03-31
DC_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.4914 | 0.45316 | [8 empty] | 2015-03-31
DC_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10340.1344 | 9746.848 | [8 empty] | 2015-03-31
DC_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24536.6304 | 24134.0432 | [8 empty] | 2015-03-31
DC_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 198645.0003 | 194703.8835 | [8 empty] | 2015-03-31
DC_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23456.0016 | 21612.576 | [8 empty] | 2015-03-31
DC_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
DC_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
DC_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
DC_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
DC_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
DC_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
DC_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
DC_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
DC_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
DC_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
DC_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
DC_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
DC_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | [8 empty] | 2015-03-31
DC_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
DC_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
DC_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
DC_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
DC_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
DC_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
DC_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
DC_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
DC_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
DC_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 396.8551 | 391.295 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 396.8551 | 391.295 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
DC_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 376.6758 | 371.3964 | [8 empty] | 2015-03-31
DC_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 376.6758 | 371.3964 | [8 empty] | 2015-03-31
DC_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.5336 | 4.4252 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1868.7531 | 921.2921 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 921.2921 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1868.7531 | 1842.6001 | [8 empty] | 2015-03-31
DC_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 911.6361 | 889.8371 | [8 empty] | 2015-03-31
DC_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2180.3705 | 2141.6957 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
DC_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0867 | 10.4546 | [8 empty] | 2015-03-31
DC_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.269 | 32.8318 | [8 empty] | 2015-03-31
DC_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 279.3447 | 273.8179 | [8 empty] | 2015-03-31
DC_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.734 | 29.3964 | [8 empty] | 2015-03-31
DC_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.8705 | 42.6821 | [8 empty] | 2015-03-31
DC_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.78148 | 0.7693 | [8 empty] | 2015-03-31
DC_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.8533 | 9.6634 | [8 empty] | 2015-03-31
DC_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.67361 | 0.65258 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.0813 | 4.97 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.97 | [8 empty] | 2015-03-31
DC_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 30.244 | 29.8203 | [8 empty] | 2015-03-31
DC_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.7055 | 19.2343 | [8 empty] | 2015-03-31
DC_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 40.3842 | 39.6668 | [8 empty] | 2015-03-31
DC_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8436 | 3.8147 | [8 empty] | 2015-03-31
DC_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | [8 empty] | 2015-03-31
DC_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
DC_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DC_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
DC_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4528.3746 | 4397.5864 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.0285 | 8.9015 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 38.7809 | 36.9916 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.524 | 6.2559 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6938 | 5.3614 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3305.4528 | 3241.8864 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12713.28 | 11590.2736 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2097.6912 | 1928.1808 | [8 empty] | 2015-03-31
DC_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
DC_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
DC_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.04 | 2.0423 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2376 | 2.1936 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.6396 | 12.4459 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7673 | 1.6748 | [8 empty] | 2015-03-31
DC_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4721 | 1.355 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.6976 | 21.8311 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.2229 | 21.3841 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.9997 | 20.1707 | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.7807 | 26.9508 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.3993 | 5.4349 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7712.7232 | 6547.3392 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7564.4016 | 6420.2064 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6907.5488 | 6059.9968 | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9534.96 | 8094.1216 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1928.1808 | 1631.5376 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
DC_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
DC_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
DC_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
DC_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
DC_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
DC_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
DC_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
DC_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
DC_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7711.4307 | 6551.1532 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7568.9784 | 6417.0281 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6052.8986 | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DC_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DC_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DC_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | [8 empty] | 2015-03-31
DC_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
DC_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
DC_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4513 | 1.3373 | [8 empty] | 2015-03-31
DC_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 145.9205 | 134.4569 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.2905 | 9.6649 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.0819 | 9.467 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.1051 | 8.9299 | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.9632 | 11.8411 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3456 | 1.1428 | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
DC_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.1542 | 2.9064 | [8 empty] | 2015-03-31
DC_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DC_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DC_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DC_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DC_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
DC_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.3622 | 97.23 | [8 empty] | 2015-03-31
DC_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0776 | 1.9378 | [8 empty] | 2015-03-31
DC_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3167 | 5.1267 | [8 empty] | 2015-03-31
DC_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.538 | 2.3891 | [8 empty] | 2015-03-31
DC_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.3658 | 4.328 | [8 empty] | 2015-03-31
DC_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2015-03-31
DC_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1589.16 | 1546.7824 | [8 empty] | 2015-03-31
DC_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | [8 empty] | 2015-03-31
DC_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | [8 empty] | 2015-03-31
DC_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
DC_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
DC_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
DC_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
DC_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
DC_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
DC_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
DC_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
DC_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
DC_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.118 | 1.078 | [8 empty] | 2015-03-31
DC_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0496 | 1.0498 | [8 empty] | 2015-03-31
DC_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.61732 | 0.6097 | [8 empty] | 2015-03-31
DC_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.61308 | 0.60572 | [8 empty] | 2015-03-31
DC_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.75732 | 0.75498 | [8 empty] | 2015-03-31
DC_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.93557 | 0.9286 | [8 empty] | 2015-03-31
DC_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.695 | 0.689 | [8 empty] | 2015-03-31
DC_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.70688 | 0.70259 | [8 empty] | 2015-03-31
DC_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.9813 | 0.97282 | [8 empty] | 2015-03-31
DC_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6244 | 1.596 | [8 empty] | 2015-03-31
DC_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6172 | 1.5893 | [8 empty] | 2015-03-31
DC_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0237 | 2.0052 | [8 empty] | 2015-03-31
DC_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4156 | 2.3777 | [8 empty] | 2015-03-31
DC_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8287 | 1.8016 | [8 empty] | 2015-03-31
DC_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8335 | 1.8063 | [8 empty] | 2015-03-31
DC_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3516 | 2.3129 | [8 empty] | 2015-03-31
DC_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5218 | 2.4864 | [8 empty] | 2015-03-31
DC_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1248 | 2.1301 | [8 empty] | 2015-03-31
DC_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1283 | 0.99286 | [8 empty] | 2015-03-31
DC_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1309 | 0.98506 | [8 empty] | 2015-03-31
DC_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3942 | 1.2387 | [8 empty] | 2015-03-31
DC_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5853 | 1.4687 | [8 empty] | 2015-03-31
DC_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3216 | 1.1968 | [8 empty] | 2015-03-31
DC_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3245 | 1.1981 | [8 empty] | 2015-03-31
DC_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5944 | 1.466 | [8 empty] | 2015-03-31
DC_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6949 | 1.5647 | [8 empty] | 2015-03-31
DC_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
DC_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
DC_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DC_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DC_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DC_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DC_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DC_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DC_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DC_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
DC_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
DC_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
DC_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
DC_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
DC_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | [8 empty] | 2015-03-31
DC_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | [8 empty] | 2015-03-31
DC_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
DC_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | [8 empty] | 2015-03-31
DC_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | [8 empty] | 2015-03-31
DC_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 2015-03-31
DC_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 2015-03-31
DC_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 741.608 | [8 empty] | 2015-03-31
DC_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | [8 empty] | 2015-03-31
DC_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
DC_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
DC_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | [8 empty] | 2015-03-31
DC_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | [8 empty] | 2015-03-31
DC_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | [8 empty] | 2015-03-31
DC_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | [8 empty] | 2015-03-31
DC_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | [8 empty] | 2015-03-31
DC_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | [8 empty] | 2015-03-31
DC_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 572.0976 | [8 empty] | 2015-03-31
DC_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | [8 empty] | 2015-03-31
DC_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | [8 empty] | 2015-03-31
DC_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | [8 empty] | 2015-03-31
DC_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
DC_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
DC_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14244 | 0.13999 | [8 empty] | 2015-03-31
DC_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14109 | 0.13872 | [8 empty] | 2015-03-31
DC_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18356 | 0.18404 | [8 empty] | 2015-03-31
DC_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23862 | 0.23636 | [8 empty] | 2015-03-31
DC_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15569 | 0.15423 | [8 empty] | 2015-03-31
DC_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15994 | 0.1586 | [8 empty] | 2015-03-31
DC_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24852 | 0.24576 | [8 empty] | 2015-03-31
DC_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40434 | 0.39504 | [8 empty] | 2015-03-31
DC_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40201 | 0.39287 | [8 empty] | 2015-03-31
DC_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.526 | 0.51994 | [8 empty] | 2015-03-31
DC_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.64676 | 0.63428 | [8 empty] | 2015-03-31
DC_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.44605 | 0.43739 | [8 empty] | 2015-03-31
DC_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.44761 | 0.43892 | [8 empty] | 2015-03-31
DC_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.60358 | 0.59252 | [8 empty] | 2015-03-31
DC_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67723 | 0.66285 | [8 empty] | 2015-03-31
DC_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64967 | 0.65156 | [8 empty] | 2015-03-31
DC_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.28908 | 0.25596 | [8 empty] | 2015-03-31
DC_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.28903 | 0.25343 | [8 empty] | 2015-03-31
DC_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.36556 | 0.32883 | [8 empty] | 2015-03-31
DC_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.43589 | 0.40015 | [8 empty] | 2015-03-31
DC_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.35065 | 0.31026 | [8 empty] | 2015-03-31
DC_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.35162 | 0.31141 | [8 empty] | 2015-03-31
DC_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.43119 | 0.39044 | [8 empty] | 2015-03-31
DC_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46641 | 0.42639 | [8 empty] | 2015-03-31
IL_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8782 | 1.7653 | 1.804 | 1.7058 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0025 | 1.8479 | 1.9191 | 1.7998 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5149 | 1.436 | 1.4012 | 1.3501 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8643 | 1.7293 | 1.7295 | 1.6191 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.735 | 1.623 | 1.6212 | 1.5421 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 572.0976 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 678.0416 | 741.608 | 678.0416 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 614.4752 | 593.2864 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 614.4752 | 635.664 | 593.2864 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 741.608 | 699.2304 | 699.2304 | 656.8528 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.4497 | 0.41159 | 0.43744 | 0.40239 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.53656 | 0.48279 | 0.52146 | 0.47869 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.47091 | 0.44278 | 0.4413 | 0.42336 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.49006 | 0.44079 | 0.45447 | 0.4153 | [6 empty] | 2015-03-31
IL_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.53029 | 0.48866 | 0.50056 | 0.4706 | [6 empty] | 2015-03-31
IL_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10530.8336 | 9916.3584 | 10149.4352 | 9789.2256 | [6 empty] | 2015-03-31
IL_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25447.7488 | 25023.9728 | 25023.9728 | 24663.7632 | [6 empty] | 2015-03-31
IL_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 208074.0163 | 203815.0675 | 203793.8787 | 199852.7619 | [6 empty] | 2015-03-31
IL_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 24261.176 | 22311.8064 | 23795.0224 | 21930.408 | [6 empty] | 2015-03-31
IL_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IL_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
IL_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
IL_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
IL_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
IL_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
IL_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
IL_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
IL_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
IL_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
IL_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
IL_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
IL_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IL_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IL_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IL_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IL_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IL_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IL_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IL_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IL_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IL_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 431.9451 | 426.0345 | 421.0514 | 415.7635 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 431.9451 | 426.0345 | 421.0514 | 415.7635 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
IL_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 409.9796 | 404.3694 | 399.6458 | 394.6178 | [6 empty] | 2015-03-31
IL_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 409.9796 | 404.3694 | 399.6458 | 394.6178 | [6 empty] | 2015-03-31
IL_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.9893 | 4.8758 | 5.3571 | 5.2189 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 2034.072 | 1003.0845 | 1982.7169 | 978.9017 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 1003.0845 | 0 | 978.9017 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 2034.072 | 2006.1754 | 1982.7169 | 1957.8319 | [6 empty] | 2015-03-31
IL_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1003.2858 | 980.4519 | 1077.2308 | 1049.442 | [6 empty] | 2015-03-31
IL_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2373.1104 | 2331.741 | 2313.3547 | 2275.6309 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IL_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.29 | 10.6457 | 10.8956 | 10.5129 | [6 empty] | 2015-03-31
IL_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.5832 | 34.032 | 35.9687 | 35.47 | [6 empty] | 2015-03-31
IL_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 292.6237 | 286.6374 | 286.607 | 281.0518 | [6 empty] | 2015-03-31
IL_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.8882 | 30.3548 | 34.2074 | 31.5195 | [6 empty] | 2015-03-31
IL_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.5362 | 43.3441 | 43.5027 | 43.4265 | [6 empty] | 2015-03-31
IL_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.81006 | 0.79549 | 0.81426 | 0.79925 | [6 empty] | 2015-03-31
IL_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.1918 | 9.9611 | 10.254 | 10.014 | [6 empty] | 2015-03-31
IL_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.70215 | 0.67822 | 0.70443 | 0.68043 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.9727 | 5.4113 | 10.696 | 5.2808 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.4113 | 0 | 5.2808 | [6 empty] | 2015-03-31
IL_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.9182 | 32.4677 | 32.088 | 31.685 | [6 empty] | 2015-03-31
IL_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 21.6866 | 21.193 | 23.285 | 22.6843 | [6 empty] | 2015-03-31
IL_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.955 | 43.1884 | 42.8464 | 42.1472 | [6 empty] | 2015-03-31
IL_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.9033 | 3.8715 | 3.8941 | 3.8696 | [6 empty] | 2015-03-31
IL_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
IL_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
IL_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IL_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
IL_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4832.6139 | 4686.1051 | 4969.7153 | 4814.5888 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.6445 | 9.4846 | 9.3997 | 9.3237 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 42.6093 | 40.5871 | 41.3156 | 39.8966 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.9036 | 6.6399 | 6.7202 | 6.4789 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.071 | 5.725 | 5.884 | 5.5683 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3538.5296 | 3432.5856 | 3347.8304 | 3305.4528 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13454.888 | 12204.7488 | 13137.056 | 12014.0496 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2585.0336 | 2457.9008 | 2563.8448 | 2436.712 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2161.2576 | 1991.7472 | 2140.0688 | 1970.5584 | [6 empty] | 2015-03-31
IL_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IL_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | Yes | Yes | Yes | [6 empty] | 2015-03-31
IL_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.5728 | 2.3833 | 4.0531 | 2.7535 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3915 | 2.3271 | 2.2744 | 2.2331 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.4506 | 13.1077 | 14.1025 | 12.892 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8168 | 1.7229 | 1.8012 | 1.7136 | [6 empty] | 2015-03-31
IL_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5188 | 1.4 | 1.4988 | 1.3857 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.5316 | 22.7583 | 25.9775 | 22.2728 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 26.1306 | 22.5817 | 25.5765 | 22.0499 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.746 | 20.8887 | 23.2977 | 20.5476 | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.9057 | 27.9981 | 32.0514 | 27.3863 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.7384 | 5.7175 | 6.5172 | 5.5254 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7966.9888 | 6822.7936 | 7797.4784 | 6674.472 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7839.856 | 6780.416 | 7670.3456 | 6610.9056 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7119.4368 | 6271.8848 | 6992.304 | 6165.9408 | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9873.9808 | 8411.9536 | 9619.7152 | 8221.2544 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2012.936 | 1716.2928 | 1949.3696 | 1652.7264 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
IL_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
IL_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IL_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IL_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IL_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
IL_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
IL_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
IL_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
IL_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 6829.4045 | 7795.4231 | 6683.6891 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7841.3604 | 6776.4113 | 7675.0707 | 6616.7961 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6268.3675 | 6777.6191 | 6166.0044 | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IL_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IL_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IL_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
IL_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IL_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IL_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5724 | 1.4332 | 1.6436 | 1.4923 | [6 empty] | 2015-03-31
IL_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 158.0965 | 144.1002 | 165.2491 | 150.043 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.6569 | 9.9991 | 11.4135 | 9.8605 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.4807 | 9.9215 | 11.2373 | 9.7618 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.433 | 9.2477 | 10.236 | 9.0967 | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.4575 | 12.3012 | 14.0821 | 12.0324 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4169 | 1.2022 | 1.3704 | 1.1618 | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
IL_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.4174 | 3.1148 | 3.572 | 3.2433 | [6 empty] | 2015-03-31
IL_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IL_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IL_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IL_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IL_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IL_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.439 | 97.8482 | 104.989 | 98.0387 | [6 empty] | 2015-03-31
IL_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2069 | 2.1017 | 2.1401 | 2.0176 | [6 empty] | 2015-03-31
IL_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.4669 | 5.2711 | 5.3818 | 5.1887 | [6 empty] | 2015-03-31
IL_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5965 | 2.4472 | 2.5603 | 2.405 | [6 empty] | 2015-03-31
IL_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5801 | 4.5447 | 4.4577 | 4.419 | [6 empty] | 2015-03-31
IL_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2015-03-31
IL_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1631.5376 | 1589.16 | 1610.3488 | 1546.7824 | [6 empty] | 2015-03-31
IL_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
IL_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1525.5936 | 1504.4048 | [6 empty] | 2015-03-31
IL_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
IL_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
IL_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
IL_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
IL_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IL_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IL_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IL_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IL_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | No | No | [6 empty] | 2015-03-31
IL_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1495 | 1.1084 | 1.1316 | 1.091 | [6 empty] | 2015-03-31
IL_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.07 | 1.0589 | 1.0643 | 1.0516 | [6 empty] | 2015-03-31
IL_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.68897 | 0.68257 | 0.64135 | 0.63109 | [6 empty] | 2015-03-31
IL_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.68403 | 0.67792 | 0.6364 | 0.62647 | [6 empty] | 2015-03-31
IL_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84385 | 0.84277 | 0.7753 | 0.76774 | [6 empty] | 2015-03-31
IL_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0443 | 1.0379 | 0.98237 | 0.96404 | [6 empty] | 2015-03-31
IL_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.74753 | 0.74172 | 0.72056 | 0.708 | [6 empty] | 2015-03-31
IL_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.76121 | 0.75431 | 0.73442 | 0.72126 | [6 empty] | 2015-03-31
IL_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0755 | 1.0684 | 1.0203 | 0.99545 | [6 empty] | 2015-03-31
IL_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7765 | 1.7509 | 1.6869 | 1.6504 | [6 empty] | 2015-03-31
IL_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7684 | 1.7432 | 1.6787 | 1.6428 | [6 empty] | 2015-03-31
IL_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2373 | 2.2185 | 2.0985 | 2.0527 | [6 empty] | 2015-03-31
IL_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6693 | 2.6318 | 2.5451 | 2.4797 | [6 empty] | 2015-03-31
IL_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.9508 | 1.9178 | 1.9088 | 1.8589 | [6 empty] | 2015-03-31
IL_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.9527 | 1.9235 | 1.911 | 1.8644 | [6 empty] | 2015-03-31
IL_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.5237 | 2.4841 | 2.4469 | 2.3775 | [6 empty] | 2015-03-31
IL_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.748 | 2.6981 | 2.6448 | 2.5615 | [6 empty] | 2015-03-31
IL_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2162 | 2.2157 | 2.188 | 2.1871 | [6 empty] | 2015-03-31
IL_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.2231 | 1.0866 | 1.1505 | 1.0176 | [6 empty] | 2015-03-31
IL_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.2237 | 1.0777 | 1.1509 | 1.0088 | [6 empty] | 2015-03-31
IL_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4713 | 1.3623 | 1.4201 | 1.26 | [6 empty] | 2015-03-31
IL_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.7223 | 1.6108 | 1.6319 | 1.5149 | [6 empty] | 2015-03-31
IL_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.408 | 1.2743 | 1.3619 | 1.2273 | [6 empty] | 2015-03-31
IL_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.4119 | 1.2782 | 1.3657 | 1.231 | [6 empty] | 2015-03-31
IL_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.706 | 1.5695 | 1.6428 | 1.4987 | [6 empty] | 2015-03-31
IL_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.8102 | 1.6786 | 1.7464 | 1.5972 | [6 empty] | 2015-03-31
IL_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IL_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
IL_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IL_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IL_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IL_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IL_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IL_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IL_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IL_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IL_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
IL_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IL_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
IL_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
IL_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
IL_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | 339.0208 | 339.0208 | [6 empty] | 2015-03-31
IL_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 211.888 | 211.888 | [6 empty] | 2015-03-31
IL_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 211.888 | [6 empty] | 2015-03-31
IL_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | 360.2096 | 339.0208 | [6 empty] | 2015-03-31
IL_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 572.0976 | 572.0976 | [6 empty] | 2015-03-31
IL_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 593.2864 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
IL_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 783.9856 | 762.7968 | 741.608 | [6 empty] | 2015-03-31
IL_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 974.6848 | 953.496 | 911.1184 | [6 empty] | 2015-03-31
IL_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
IL_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
IL_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 868.7408 | 847.552 | [6 empty] | 2015-03-31
IL_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 995.8736 | 995.8736 | 953.496 | [6 empty] | 2015-03-31
IL_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 932.3072 | 932.3072 | 932.3072 | [6 empty] | 2015-03-31
IL_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
IL_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
IL_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 508.5312 | 466.1536 | [6 empty] | 2015-03-31
IL_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
IL_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
IL_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
IL_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 614.4752 | 550.9088 | [6 empty] | 2015-03-31
IL_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 635.664 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
IL_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IL_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15298 | 0.15093 | 0.14204 | 0.13869 | [6 empty] | 2015-03-31
IL_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15141 | 0.14944 | 0.14045 | 0.13721 | [6 empty] | 2015-03-31
IL_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.20076 | 0.20162 | 0.18296 | 0.18161 | [6 empty] | 2015-03-31
IL_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.26001 | 0.25791 | 0.24553 | 0.23947 | [6 empty] | 2015-03-31
IL_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16116 | 0.15935 | 0.15673 | 0.15278 | [6 empty] | 2015-03-31
IL_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16551 | 0.16375 | 0.16124 | 0.15746 | [6 empty] | 2015-03-31
IL_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.26598 | 0.26252 | 0.25406 | 0.24586 | [6 empty] | 2015-03-31
IL_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.42911 | 0.42075 | 0.41045 | 0.39835 | [6 empty] | 2015-03-31
IL_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.42647 | 0.41826 | 0.40774 | 0.39584 | [6 empty] | 2015-03-31
IL_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.56912 | 0.56293 | 0.53487 | 0.52265 | [6 empty] | 2015-03-31
IL_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.69874 | 0.68642 | 0.67179 | 0.64991 | [6 empty] | 2015-03-31
IL_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.45941 | 0.44999 | 0.4565 | 0.44144 | [6 empty] | 2015-03-31
IL_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.46112 | 0.45182 | 0.45832 | 0.44323 | [6 empty] | 2015-03-31
IL_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.63086 | 0.61816 | 0.61851 | 0.59583 | [6 empty] | 2015-03-31
IL_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.72018 | 0.70384 | 0.70079 | 0.67302 | [6 empty] | 2015-03-31
IL_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.66206 | 0.66185 | 0.66476 | 0.66446 | [6 empty] | 2015-03-31
IL_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.30471 | 0.27201 | 0.28747 | 0.25532 | [6 empty] | 2015-03-31
IL_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.30489 | 0.26912 | 0.28761 | 0.25241 | [6 empty] | 2015-03-31
IL_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.38711 | 0.35482 | 0.36437 | 0.32744 | [6 empty] | 2015-03-31
IL_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.46643 | 0.43131 | 0.44509 | 0.40747 | [6 empty] | 2015-03-31
IL_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.36505 | 0.32183 | 0.35757 | 0.31326 | [6 empty] | 2015-03-31
IL_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.36631 | 0.32311 | 0.35886 | 0.31452 | [6 empty] | 2015-03-31
IL_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.45172 | 0.40756 | 0.43925 | 0.39183 | [6 empty] | 2015-03-31
IL_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.4897 | 0.44812 | 0.47512 | 0.42815 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8265 | 1.7175 | 1.7377 | 1.6375 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9047 | 1.757 | 1.8403 | 1.726 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4093 | 1.3398 | 1.3897 | 1.3385 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.794 | 1.6663 | 1.6704 | 1.5663 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6609 | 1.556 | 1.5444 | 1.4696 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 614.4752 | 593.2864 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 635.664 | 593.2864 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 699.2304 | 656.8528 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44291 | 0.40562 | 0.43764 | 0.40257 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.51332 | 0.4609 | 0.51031 | 0.46795 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.44301 | 0.41822 | 0.43876 | 0.42056 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.47663 | 0.4296 | 0.45235 | 0.41392 | [6 empty] | 2015-03-31
IN_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.50975 | 0.47062 | 0.48941 | 0.46057 | [6 empty] | 2015-03-31
IN_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10424.8896 | 9831.6032 | 10170.624 | 9810.4144 | [6 empty] | 2015-03-31
IN_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24960.4064 | 24557.8192 | 24557.8192 | 24218.7984 | [6 empty] | 2015-03-31
IN_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 202967.5155 | 199132.3427 | 197564.3715 | 193792.7651 | [6 empty] | 2015-03-31
IN_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23710.2672 | 21845.6528 | 23519.568 | 21676.1424 | [6 empty] | 2015-03-31
IN_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IN_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
IN_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
IN_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
IN_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
IN_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
IN_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
IN_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
IN_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
IN_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
IN_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
IN_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
IN_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IN_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IN_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IN_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IN_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IN_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IN_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IN_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IN_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IN_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 419.0126 | 413.4866 | 398.4545 | 393.3729 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 419.0126 | 413.4866 | 398.4545 | 393.3729 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
IN_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 397.7007 | 392.461 | 378.1974 | 373.3679 | [6 empty] | 2015-03-31
IN_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 397.7007 | 392.461 | 378.1974 | 373.3679 | [6 empty] | 2015-03-31
IN_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.9032 | 4.787 | 5.1815 | 5.0479 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1973.0482 | 973.5411 | 1876.3613 | 926.1835 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 973.5411 | 0 | 926.1835 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1973.0482 | 1947.0537 | 1876.3613 | 1852.4273 | [6 empty] | 2015-03-31
IN_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 985.9678 | 962.5949 | 1041.9194 | 1015.0594 | [6 empty] | 2015-03-31
IN_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2302.1009 | 2263.1091 | 2189.2466 | 2153.1079 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IN_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.1896 | 10.5518 | 10.9167 | 10.535 | [6 empty] | 2015-03-31
IN_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.8737 | 33.4171 | 35.3049 | 34.811 | [6 empty] | 2015-03-31
IN_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 285.4442 | 280.0449 | 277.8385 | 272.5331 | [6 empty] | 2015-03-31
IN_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.087 | 29.7125 | 33.8128 | 31.1603 | [6 empty] | 2015-03-31
IN_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.2333 | 43.0432 | 43.7214 | 43.645 | [6 empty] | 2015-03-31
IN_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.7954 | 0.78227 | 0.81002 | 0.79639 | [6 empty] | 2015-03-31
IN_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.9745 | 9.8465 | 10.1735 | 9.9544 | [6 empty] | 2015-03-31
IN_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.6876 | 0.66532 | 0.69881 | 0.67606 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.6442 | 5.2519 | 10.122 | 4.9964 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.2519 | 0 | 4.9964 | [6 empty] | 2015-03-31
IN_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 31.9326 | 31.5115 | 30.3659 | 29.9786 | [6 empty] | 2015-03-31
IN_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 21.3123 | 20.807 | 22.5217 | 21.9411 | [6 empty] | 2015-03-31
IN_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 42.639 | 41.9164 | 40.5469 | 39.8774 | [6 empty] | 2015-03-31
IN_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8772 | 3.8472 | 3.8781 | 3.8549 | [6 empty] | 2015-03-31
IN_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
IN_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
IN_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IN_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
IN_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4726.4529 | 4586.2994 | 4872.745 | 4716.3622 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.377 | 9.225 | 9.0067 | 8.991 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 40.9276 | 38.909 | 38.8383 | 38.3023 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.5992 | 6.3428 | 6.4883 | 6.2371 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.7759 | 5.4447 | 5.6569 | 5.339 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3390.208 | 3326.6416 | 3199.5088 | 3199.5088 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13115.8672 | 11865.728 | 12395.448 | 11717.4064 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2500.2784 | 2373.1456 | 2521.4672 | 2394.3344 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2076.5024 | 1906.992 | 2097.6912 | 1928.1808 | [6 empty] | 2015-03-31
IN_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
IN_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IN_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.483 | 2.3145 | 3.8501 | 2.5968 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3006 | 2.2459 | 2.1729 | 2.1626 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.0782 | 12.7367 | 13.2943 | 12.5811 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.754 | 1.6621 | 1.7666 | 1.6776 | [6 empty] | 2015-03-31
IN_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.457 | 1.3401 | 1.4634 | 1.3485 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.7841 | 21.9935 | 25.7518 | 22.0965 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.3581 | 21.6151 | 25.334 | 21.7725 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.0656 | 20.2192 | 23.0719 | 20.2508 | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.096 | 27.1999 | 31.913 | 27.1964 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.4959 | 5.5128 | 6.5842 | 5.5988 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7733.912 | 6589.7168 | 7733.912 | 6632.0944 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7606.7792 | 6483.7728 | 7606.7792 | 6526.1504 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6928.7376 | 6059.9968 | 6928.7376 | 6081.1856 | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9640.904 | 8157.688 | 9577.3376 | 8157.688 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1949.3696 | 1652.7264 | 1970.5584 | 1673.9152 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
IN_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
IN_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IN_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IN_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IN_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
IN_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
IN_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
IN_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
IN_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7737.387 | 6599.8874 | 7727.7037 | 6630.8019 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7609.5549 | 6486.3578 | 7602.3084 | 6533.5665 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6067.4553 | 6777.6191 | 6076.9267 | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IN_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IN_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IN_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
IN_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IN_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IN_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5358 | 1.4047 | 1.5891 | 1.447 | [6 empty] | 2015-03-31
IN_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 154.4107 | 141.231 | 159.7728 | 145.4862 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.3285 | 9.7368 | 11.3143 | 9.7824 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.1413 | 9.5693 | 11.1307 | 9.639 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.1341 | 8.9513 | 10.1369 | 8.9653 | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.1017 | 11.9505 | 14.0213 | 11.949 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3659 | 1.1592 | 1.3845 | 1.1773 | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
IN_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.3377 | 3.0528 | 3.4536 | 3.1448 | [6 empty] | 2015-03-31
IN_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IN_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IN_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IN_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IN_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IN_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 103.3607 | 97.517 | 103.5651 | 97.0968 | [6 empty] | 2015-03-31
IN_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0935 | 1.9698 | 2.0647 | 1.9376 | [6 empty] | 2015-03-31
IN_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3185 | 5.1278 | 5.3672 | 5.1398 | [6 empty] | 2015-03-31
IN_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5451 | 2.3967 | 2.5565 | 2.4031 | [6 empty] | 2015-03-31
IN_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.4434 | 4.4083 | 4.3519 | 4.3117 | [6 empty] | 2015-03-31
IN_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
IN_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1589.16 | 1546.7824 | 1610.3488 | 1546.7824 | [6 empty] | 2015-03-31
IN_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
IN_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | 1525.5936 | 1504.4048 | [6 empty] | 2015-03-31
IN_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
IN_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
IN_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
IN_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
IN_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IN_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IN_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IN_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IN_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IN_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1183 | 1.0782 | 1.1286 | 1.0808 | [6 empty] | 2015-03-31
IN_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0541 | 1.0552 | 1.0669 | 1.0538 | [6 empty] | 2015-03-31
IN_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.63944 | 0.63377 | 0.61187 | 0.60317 | [6 empty] | 2015-03-31
IN_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.63489 | 0.62947 | 0.607 | 0.59864 | [6 empty] | 2015-03-31
IN_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.76423 | 0.76901 | 0.77023 | 0.76155 | [6 empty] | 2015-03-31
IN_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.95987 | 0.95544 | 0.94318 | 0.92797 | [6 empty] | 2015-03-31
IN_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.6949 | 0.68947 | 0.68218 | 0.67046 | [6 empty] | 2015-03-31
IN_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.70725 | 0.70355 | 0.69509 | 0.6839 | [6 empty] | 2015-03-31
IN_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.99722 | 0.99347 | 0.99181 | 0.97014 | [6 empty] | 2015-03-31
IN_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6619 | 1.648 | 1.62 | 1.5872 | [6 empty] | 2015-03-31
IN_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6544 | 1.6408 | 1.6121 | 1.5799 | [6 empty] | 2015-03-31
IN_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0483 | 2.0269 | 2.0772 | 2.0413 | [6 empty] | 2015-03-31
IN_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4687 | 2.4373 | 2.4437 | 2.3861 | [6 empty] | 2015-03-31
IN_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8194 | 1.7944 | 1.8169 | 1.7729 | [6 empty] | 2015-03-31
IN_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8245 | 1.7994 | 1.822 | 1.7783 | [6 empty] | 2015-03-31
IN_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3372 | 2.301 | 2.3461 | 2.2467 | [6 empty] | 2015-03-31
IN_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5481 | 2.5142 | 2.563 | 2.4878 | [6 empty] | 2015-03-31
IN_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1128 | 2.1777 | 2.0859 | 2.0886 | [6 empty] | 2015-03-31
IN_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1536 | 1.0141 | 1.0822 | 0.98572 | [6 empty] | 2015-03-31
IN_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1541 | 1.0057 | 1.1093 | 0.98155 | [6 empty] | 2015-03-31
IN_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4105 | 1.2509 | 1.352 | 1.2494 | [6 empty] | 2015-03-31
IN_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6143 | 1.5038 | 1.5799 | 1.4719 | [6 empty] | 2015-03-31
IN_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3217 | 1.1948 | 1.3064 | 1.1752 | [6 empty] | 2015-03-31
IN_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3248 | 1.1961 | 1.3102 | 1.1789 | [6 empty] | 2015-03-31
IN_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5888 | 1.4585 | 1.5825 | 1.4422 | [6 empty] | 2015-03-31
IN_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7058 | 1.5742 | 1.6725 | 1.5317 | [6 empty] | 2015-03-31
IN_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IN_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
IN_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IN_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IN_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IN_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IN_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IN_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IN_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IN_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IN_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
IN_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IN_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
IN_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
IN_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
IN_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 339.0208 | 339.0208 | [6 empty] | 2015-03-31
IN_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
IN_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
IN_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 360.2096 | 360.2096 | [6 empty] | 2015-03-31
IN_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
IN_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
IN_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 741.608 | 762.7968 | 741.608 | [6 empty] | 2015-03-31
IN_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | 932.3072 | 911.1184 | [6 empty] | 2015-03-31
IN_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
IN_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
IN_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 826.3632 | 847.552 | 826.3632 | [6 empty] | 2015-03-31
IN_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | 995.8736 | 953.496 | [6 empty] | 2015-03-31
IN_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 932.3072 | 911.1184 | 911.1184 | [6 empty] | 2015-03-31
IN_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
IN_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
IN_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 508.5312 | 466.1536 | [6 empty] | 2015-03-31
IN_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
IN_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
IN_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
IN_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 614.4752 | 550.9088 | [6 empty] | 2015-03-31
IN_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
IN_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IN_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14252 | 0.14069 | 0.14006 | 0.13716 | [6 empty] | 2015-03-31
IN_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14106 | 0.13931 | 0.13847 | 0.13571 | [6 empty] | 2015-03-31
IN_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18385 | 0.18552 | 0.18371 | 0.18207 | [6 empty] | 2015-03-31
IN_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.24004 | 0.23861 | 0.24226 | 0.23715 | [6 empty] | 2015-03-31
IN_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15027 | 0.14897 | 0.15103 | 0.1473 | [6 empty] | 2015-03-31
IN_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15466 | 0.15351 | 0.15526 | 0.15159 | [6 empty] | 2015-03-31
IN_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.2469 | 0.24464 | 0.25557 | 0.2483 | [6 empty] | 2015-03-31
IN_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40526 | 0.39773 | 0.4061 | 0.39504 | [6 empty] | 2015-03-31
IN_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40279 | 0.39539 | 0.40349 | 0.39262 | [6 empty] | 2015-03-31
IN_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.52721 | 0.52332 | 0.5359 | 0.52398 | [6 empty] | 2015-03-31
IN_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.65194 | 0.64154 | 0.66082 | 0.64129 | [6 empty] | 2015-03-31
IN_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.43286 | 0.42485 | 0.44344 | 0.42891 | [6 empty] | 2015-03-31
IN_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.43452 | 0.42647 | 0.44511 | 0.43068 | [6 empty] | 2015-03-31
IN_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.58996 | 0.57962 | 0.60263 | 0.5831 | [6 empty] | 2015-03-31
IN_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67326 | 0.65977 | 0.69903 | 0.67353 | [6 empty] | 2015-03-31
IN_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64148 | 0.66149 | 0.64321 | 0.6442 | [6 empty] | 2015-03-31
IN_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.29099 | 0.25753 | 0.28646 | 0.25496 | [6 empty] | 2015-03-31
IN_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29116 | 0.25478 | 0.28585 | 0.25243 | [6 empty] | 2015-03-31
IN_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.36688 | 0.33021 | 0.36301 | 0.32992 | [6 empty] | 2015-03-31
IN_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.44122 | 0.40602 | 0.44412 | 0.40725 | [6 empty] | 2015-03-31
IN_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.3464 | 0.30508 | 0.34977 | 0.30605 | [6 empty] | 2015-03-31
IN_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34743 | 0.30621 | 0.35103 | 0.30728 | [6 empty] | 2015-03-31
IN_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.42592 | 0.38422 | 0.43066 | 0.38392 | [6 empty] | 2015-03-31
IN_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46586 | 0.42516 | 0.46896 | 0.42521 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8515 | 1.7374 | 1.5782 | 1.4684 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.008 | 1.8537 | 1.8088 | 1.652 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5213 | 1.4458 | 1.5188 | 1.4514 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8489 | 1.7096 | 1.6459 | 1.5069 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.743 | 1.6284 | 1.8517 | 1.744 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 805.1744 | 741.608 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 635.664 | 741.608 | 678.0416 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 826.3632 | 783.9856 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.45549 | 0.41694 | 0.49352 | 0.45352 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.54686 | 0.49143 | 0.57724 | 0.52718 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.48407 | 0.45502 | 0.48469 | 0.46318 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.49612 | 0.44879 | 0.52524 | 0.48088 | [6 empty] | 2015-03-31
KS_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.54669 | 0.50366 | 0.59092 | 0.55654 | [6 empty] | 2015-03-31
KS_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10636.7776 | 10022.3024 | 11336.008 | 10933.4208 | [6 empty] | 2015-03-31
KS_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25553.6928 | 25108.728 | 27863.272 | 27481.8736 | [6 empty] | 2015-03-31
KS_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 208116.3939 | 203836.2563 | 226995.6147 | 222291.7011 | [6 empty] | 2015-03-31
KS_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 24515.4416 | 22523.6944 | 27100.4752 | 24939.2176 | [6 empty] | 2015-03-31
KS_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
KS_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
KS_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
KS_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
KS_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
KS_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
KS_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
KS_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
KS_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
KS_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
KS_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
KS_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
KS_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
KS_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
KS_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
KS_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
KS_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
KS_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
KS_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
KS_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
KS_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
KS_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 418.472 | 412.5994 | 321.643 | 315.6464 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 418.472 | 412.5994 | 321.643 | 315.6464 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
KS_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 397.1979 | 391.6142 | 305.2916 | 299.5888 | [6 empty] | 2015-03-31
KS_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 397.1979 | 391.6142 | 305.2916 | 299.5888 | [6 empty] | 2015-03-31
KS_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.1063 | 4.9875 | 4.9289 | 4.821 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1970.5122 | 971.452 | 1514.5966 | 743.1789 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 971.452 | 0 | 743.1789 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1970.5122 | 1942.9326 | 1514.5966 | 1486.3593 | [6 empty] | 2015-03-31
KS_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1026.7966 | 1002.9244 | 991.1255 | 969.4311 | [6 empty] | 2015-03-31
KS_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2299.0894 | 2258.1955 | 1767.1525 | 1727.6852 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
KS_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.4097 | 10.759 | 12.1624 | 11.7341 | [6 empty] | 2015-03-31
KS_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.7309 | 34.1627 | 39.9018 | 39.3318 | [6 empty] | 2015-03-31
KS_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 292.6823 | 286.6664 | 319.2161 | 312.6181 | [6 empty] | 2015-03-31
KS_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 35.2509 | 30.6326 | 38.8086 | 35.8607 | [6 empty] | 2015-03-31
KS_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 44.0391 | 43.8447 | 48.2924 | 48.2082 | [6 empty] | 2015-03-31
KS_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.82972 | 0.81334 | 0.91729 | 0.90011 | [6 empty] | 2015-03-31
KS_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.4621 | 10.2091 | 11.5833 | 11.312 | [6 empty] | 2015-03-31
KS_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.72017 | 0.69442 | 0.79692 | 0.76956 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.6305 | 5.2406 | 8.1707 | 4.0092 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.2406 | 0 | 4.0092 | [6 empty] | 2015-03-31
KS_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 31.8914 | 31.4439 | 24.5121 | 24.0551 | [6 empty] | 2015-03-31
KS_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.1948 | 21.6788 | 21.4238 | 20.9548 | [6 empty] | 2015-03-31
KS_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 42.5839 | 41.8265 | 32.7306 | 31.9981 | [6 empty] | 2015-03-31
KS_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.9182 | 3.8842 | 3.9488 | 3.9235 | [6 empty] | 2015-03-31
KS_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
KS_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | YES | [6 empty] | 2015-03-31
KS_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
KS_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
KS_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4852.7231 | 4701.6042 | 4771.682 | 4615.0368 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.2709 | 9.1713 | 8.2871 | 8.1412 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 40.3545 | 38.9687 | 32.6338 | 30.1004 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8799 | 6.6004 | 6.3754 | 6.0538 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.0334 | 5.6884 | 5.2859 | 4.8688 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3474.9632 | 3411.3968 | 3729.2288 | 3665.6624 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13221.8112 | 12289.504 | 14683.8384 | 13370.1328 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2606.2224 | 2479.0896 | 2860.488 | 2733.3552 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2182.4464 | 2012.936 | 2373.1456 | 2182.4464 | [6 empty] | 2015-03-31
KS_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
KS_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | No | No | [6 empty] | 2015-03-31
KS_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.7839 | 2.5456 | 3.9613 | 2.6774 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3565 | 2.3171 | 2.5264 | 2.4819 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.1967 | 13.1817 | 15.6636 | 14.3573 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8299 | 1.7344 | 2.011 | 1.9096 | [6 empty] | 2015-03-31
KS_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5302 | 1.4092 | 1.6673 | 1.5358 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.9646 | 23.1184 | 28.7304 | 25.4375 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 26.6381 | 23.0441 | 28.467 | 25.2623 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 24.141 | 21.4036 | 25.3728 | 23.5755 | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 33.3974 | 28.6054 | 27.8658 | 24.9565 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.8785 | 5.8484 | 6.2206 | 5.4816 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8094.1216 | 6928.7376 | 8899.296 | 7627.968 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7988.1776 | 6907.5488 | 8750.9744 | 7585.5904 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7246.5696 | 6420.2064 | 7966.9888 | 7077.0592 | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 10022.3024 | 8581.464 | 10954.6096 | 9365.4496 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2055.3136 | 1758.6704 | 2203.6352 | 1843.4256 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
KS_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
KS_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
KS_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
KS_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
KS_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
KS_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
KS_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
KS_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
KS_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 6937.4462 | 7852.8447 | 7633.3712 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 6915.1768 | 7852.8447 | 7580.8017 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6422.8762 | 6777.6191 | 6777.6191 | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
KS_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
KS_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
KS_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
KS_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
KS_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
KS_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.6151 | 1.4644 | 1.6136 | 1.4295 | [6 empty] | 2015-03-31
KS_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 162.3881 | 147.2329 | 162.2392 | 143.7266 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.8471 | 10.1573 | 13.0213 | 11.1762 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.7037 | 10.1247 | 12.8248 | 11.0992 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.6066 | 9.4757 | 11.6705 | 10.3581 | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.6735 | 12.568 | 15.9463 | 13.7266 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4463 | 1.2298 | 1.5464 | 1.2898 | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
KS_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.5101 | 3.1825 | 3.5069 | 3.1067 | [6 empty] | 2015-03-31
KS_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
KS_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
KS_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
KS_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
KS_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
KS_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.8329 | 97.43 | 102.3581 | 91.9011 | [6 empty] | 2015-03-31
KS_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2184 | 2.128 | 1.9733 | 1.8567 | [6 empty] | 2015-03-31
KS_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.5756 | 5.3947 | 5.3594 | 5.2134 | [6 empty] | 2015-03-31
KS_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6335 | 2.4834 | 2.7894 | 2.6613 | [6 empty] | 2015-03-31
KS_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5943 | 4.561 | 4.2595 | 4.2176 | [6 empty] | 2015-03-31
KS_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 783.9856 | 720.4192 | [6 empty] | 2015-03-31
KS_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1673.9152 | 1610.3488 | 1843.4256 | 1779.8592 | [6 empty] | 2015-03-31
KS_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 868.7408 | 826.3632 | [6 empty] | 2015-03-31
KS_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1546.7824 | 1525.5936 | 1716.2928 | 1695.104 | [6 empty] | 2015-03-31
KS_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
KS_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
KS_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
KS_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
KS_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
KS_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
KS_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
KS_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
KS_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | No | No | [6 empty] | 2015-03-31
KS_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1724 | 1.1343 | 1.2911 | 1.2457 | [6 empty] | 2015-03-31
KS_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0854 | 1.0746 | 1.1953 | 1.1809 | [6 empty] | 2015-03-31
KS_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.67953 | 0.67371 | 0.52736 | 0.51598 | [6 empty] | 2015-03-31
KS_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.67422 | 0.6687 | 0.52193 | 0.51082 | [6 empty] | 2015-03-31
KS_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84271 | 0.8391 | 0.65186 | 0.63354 | [6 empty] | 2015-03-31
KS_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.054 | 1.048 | 0.91267 | 0.89047 | [6 empty] | 2015-03-31
KS_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.74378 | 0.73566 | 0.61029 | 0.59301 | [6 empty] | 2015-03-31
KS_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.75577 | 0.7496 | 0.62422 | 0.60764 | [6 empty] | 2015-03-31
KS_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0858 | 1.0746 | 0.93731 | 0.90706 | [6 empty] | 2015-03-31
KS_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7541 | 1.7296 | 1.4857 | 1.4406 | [6 empty] | 2015-03-31
KS_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7454 | 1.7215 | 1.4749 | 1.4303 | [6 empty] | 2015-03-31
KS_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2365 | 2.2165 | 1.8894 | 1.8186 | [6 empty] | 2015-03-31
KS_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6869 | 2.6497 | 2.486 | 2.4083 | [6 empty] | 2015-03-31
KS_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.9457 | 1.914 | 1.6818 | 1.6299 | [6 empty] | 2015-03-31
KS_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.9513 | 1.9197 | 1.687 | 1.6346 | [6 empty] | 2015-03-31
KS_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.5341 | 2.4918 | 2.2128 | 2.1324 | [6 empty] | 2015-03-31
KS_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.7684 | 2.7166 | 2.5703 | 2.4713 | [6 empty] | 2015-03-31
KS_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1591 | 2.2282 | 2.3131 | 2.3081 | [6 empty] | 2015-03-31
KS_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.2206 | 1.0752 | 1.0728 | 0.93312 | [6 empty] | 2015-03-31
KS_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.2235 | 1.0718 | 1.0719 | 0.92157 | [6 empty] | 2015-03-31
KS_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.5225 | 1.3658 | 1.3375 | 1.1893 | [6 empty] | 2015-03-31
KS_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.7387 | 1.6291 | 1.6601 | 1.5227 | [6 empty] | 2015-03-31
KS_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.4149 | 1.2774 | 1.2717 | 1.122 | [6 empty] | 2015-03-31
KS_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.4186 | 1.2812 | 1.2752 | 1.1249 | [6 empty] | 2015-03-31
KS_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.7201 | 1.5805 | 1.5703 | 1.3966 | [6 empty] | 2015-03-31
KS_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.8223 | 1.6846 | 1.7528 | 1.5855 | [6 empty] | 2015-03-31
KS_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
KS_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
KS_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
KS_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
KS_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
KS_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
KS_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
KS_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
KS_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
KS_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
KS_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
KS_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
KS_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
KS_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
KS_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 296.6432 | 296.6432 | 275.4544 | [6 empty] | 2015-03-31
KS_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 381.3984 | 402.5872 | 402.5872 | [6 empty] | 2015-03-31
KS_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 254.2656 | 233.0768 | [6 empty] | 2015-03-31
KS_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
KS_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 381.3984 | 423.776 | 402.5872 | [6 empty] | 2015-03-31
KS_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
KS_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
KS_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 805.1744 | 847.552 | 826.3632 | [6 empty] | 2015-03-31
KS_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 995.8736 | 1123.0064 | 1080.6288 | [6 empty] | 2015-03-31
KS_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 720.4192 | 699.2304 | [6 empty] | 2015-03-31
KS_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 720.4192 | 699.2304 | [6 empty] | 2015-03-31
KS_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | 995.8736 | 953.496 | [6 empty] | 2015-03-31
KS_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 1038.2512 | 1165.384 | 1123.0064 | [6 empty] | 2015-03-31
KS_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 953.496 | 1038.2512 | 1038.2512 | [6 empty] | 2015-03-31
KS_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 402.5872 | 466.1536 | 423.776 | [6 empty] | 2015-03-31
KS_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 381.3984 | 466.1536 | 423.776 | [6 empty] | 2015-03-31
KS_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 593.2864 | 529.72 | [6 empty] | 2015-03-31
KS_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 635.664 | 741.608 | 678.0416 | [6 empty] | 2015-03-31
KS_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
KS_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
KS_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
KS_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 783.9856 | 720.4192 | [6 empty] | 2015-03-31
KS_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
KS_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15828 | 0.15636 | 0.16531 | 0.16116 | [6 empty] | 2015-03-31
KS_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15656 | 0.15474 | 0.16334 | 0.15929 | [6 empty] | 2015-03-31
KS_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.20532 | 0.20575 | 0.20772 | 0.20106 | [6 empty] | 2015-03-31
KS_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.27224 | 0.27027 | 0.29126 | 0.28418 | [6 empty] | 2015-03-31
KS_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.1632 | 0.16118 | 0.17731 | 0.17211 | [6 empty] | 2015-03-31
KS_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16753 | 0.1656 | 0.18222 | 0.17727 | [6 empty] | 2015-03-31
KS_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.27907 | 0.27538 | 0.29911 | 0.28946 | [6 empty] | 2015-03-31
KS_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.4409 | 0.43276 | 0.4741 | 0.45972 | [6 empty] | 2015-03-31
KS_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.43804 | 0.43008 | 0.47069 | 0.45646 | [6 empty] | 2015-03-31
KS_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.58269 | 0.57612 | 0.60295 | 0.58034 | [6 empty] | 2015-03-31
KS_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.72539 | 0.71302 | 0.79335 | 0.76857 | [6 empty] | 2015-03-31
KS_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.46563 | 0.45545 | 0.51546 | 0.49722 | [6 empty] | 2015-03-31
KS_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.46733 | 0.45728 | 0.51731 | 0.49889 | [6 empty] | 2015-03-31
KS_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.64365 | 0.63007 | 0.70252 | 0.67409 | [6 empty] | 2015-03-31
KS_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.74892 | 0.73177 | 0.82025 | 0.78866 | [6 empty] | 2015-03-31
KS_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.66049 | 0.68066 | 0.73817 | 0.73657 | [6 empty] | 2015-03-31
KS_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.3109 | 0.27956 | 0.33619 | 0.29777 | [6 empty] | 2015-03-31
KS_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.31077 | 0.27649 | 0.3359 | 0.2941 | [6 empty] | 2015-03-31
KS_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.39629 | 0.36267 | 0.42683 | 0.37527 | [6 empty] | 2015-03-31
KS_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.48424 | 0.44958 | 0.52977 | 0.48592 | [6 empty] | 2015-03-31
KS_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.37142 | 0.32701 | 0.40582 | 0.35479 | [6 empty] | 2015-03-31
KS_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.37263 | 0.32823 | 0.40695 | 0.35585 | [6 empty] | 2015-03-31
KS_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.46122 | 0.41603 | 0.50111 | 0.4457 | [6 empty] | 2015-03-31
KS_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.50449 | 0.46249 | 0.55937 | 0.50598 | [6 empty] | 2015-03-31
KY_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7149 | 1.6086 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.807 | 1.6697 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4216 | 1.3422 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6855 | 1.5638 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6039 | 1.4842 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 572.0976 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 720.4192 | 678.0416 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44968 | 0.4121 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.51623 | 0.46511 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.45368 | 0.42831 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.47715 | 0.4308 | [8 empty] | 2015-03-31
KY_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.51185 | 0.47365 | [8 empty] | 2015-03-31
KY_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10615.5888 | 10022.3024 | [8 empty] | 2015-03-31
KY_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24875.6512 | 24494.2528 | [8 empty] | 2015-03-31
KY_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 199979.8947 | 196229.4771 | [8 empty] | 2015-03-31
KY_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23773.8336 | 21909.2192 | [8 empty] | 2015-03-31
KY_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
KY_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
KY_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
KY_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
KY_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
KY_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
KY_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
KY_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
KY_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
KY_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
KY_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
KY_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
KY_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | [8 empty] | 2015-03-31
KY_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
KY_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
KY_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
KY_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
KY_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
KY_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
KY_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
KY_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
KY_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
KY_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 383.1851 | 377.7537 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 383.1851 | 377.7537 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
KY_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 363.6956 | 358.5486 | [8 empty] | 2015-03-31
KY_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 363.6956 | 358.5486 | [8 empty] | 2015-03-31
KY_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.8155 | 4.6941 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1804.4008 | 889.4092 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 889.4092 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1804.4008 | 1778.8818 | [8 empty] | 2015-03-31
KY_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 968.3248 | 943.9153 | [8 empty] | 2015-03-31
KY_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2105.2399 | 2067.5162 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
KY_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.3969 | 10.7483 | [8 empty] | 2015-03-31
KY_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.7757 | 33.3212 | [8 empty] | 2015-03-31
KY_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 281.2359 | 275.9648 | [8 empty] | 2015-03-31
KY_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.1748 | 29.7996 | [8 empty] | 2015-03-31
KY_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 44.1608 | 43.9667 | [8 empty] | 2015-03-31
KY_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.81143 | 0.79789 | [8 empty] | 2015-03-31
KY_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.1747 | 9.9634 | [8 empty] | 2015-03-31
KY_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.69983 | 0.67759 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.7341 | 4.798 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.798 | [8 empty] | 2015-03-31
KY_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 29.2022 | 28.7883 | [8 empty] | 2015-03-31
KY_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.9309 | 20.4033 | [8 empty] | 2015-03-31
KY_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.9931 | 38.2941 | [8 empty] | 2015-03-31
KY_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8769 | 3.8468 | [8 empty] | 2015-03-31
KY_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | [8 empty] | 2015-03-31
KY_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
KY_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
KY_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
KY_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4652.721 | 4511.6045 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.81 | 8.79 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 37.5185 | 36.8333 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2894 | 6.0384 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4646 | 5.1414 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3284.264 | 3263.0752 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12607.336 | 11865.728 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2521.4672 | 2373.1456 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2076.5024 | 1906.992 | [8 empty] | 2015-03-31
KY_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
KY_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
KY_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
KY_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.4519 | 2.2896 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2216 | 2.2061 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.5315 | 12.736 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7603 | 1.668 | [8 empty] | 2015-03-31
KY_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4579 | 1.3405 | [8 empty] | 2015-03-31
KY_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.9675 | 22.2714 | [8 empty] | 2015-03-31
KY_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.5364 | 21.875 | [8 empty] | 2015-03-31
KY_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.2313 | 20.4476 | [8 empty] | 2015-03-31
KY_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.3966 | 27.5779 | [8 empty] | 2015-03-31
KY_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | [8 empty] | 2015-03-31
KY_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.6705 | 5.6922 | [8 empty] | 2015-03-31
KY_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
KY_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7797.4784 | 6674.472 | [8 empty] | 2015-03-31
KY_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7670.3456 | 6568.528 | [8 empty] | 2015-03-31
KY_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6971.1152 | 6144.752 | [8 empty] | 2015-03-31
KY_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9725.6592 | 8284.8208 | [8 empty] | 2015-03-31
KY_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | [8 empty] | 2015-03-31
KY_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1991.7472 | 1716.2928 | [8 empty] | 2015-03-31
KY_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
KY_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
KY_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
KY_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
KY_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
KY_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
KY_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
KY_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
KY_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
KY_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7792.4355 | 6683.2866 | [8 empty] | 2015-03-31
KY_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7663.0567 | 6564.3114 | [8 empty] | 2015-03-31 | AL
KY_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6135.9798 | [8 empty] | 2015-03-31 | AR
KY_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31 | CO
KY_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31 | CT
KY_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31 | DC
KY_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31 | DE
KY_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31 | GA
KY_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31 | IA
KY_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31 | KY
KY_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31 | MA
KY_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31 | MT
KY_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31 | NC
KY_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31 | NE
KY_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31 | NJ
KY_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31 | NY
KY_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31 | OK
KY_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31 | RI
KY_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31 | SC
KY_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31 | TX
KY_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31 | UT
KY_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31 | VA
KY_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31 | WI
KY_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
KY_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
KY_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | [8 empty] | 2015-03-31
KY_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
KY_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
KY_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31 | AL
KY_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31 | AR
KY_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31 | CO
KY_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31 | CT
KY_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31 | DC
KY_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31 | DE
KY_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31 | GA
KY_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.505 | 1.3782 | [8 empty] | 2015-03-31 | IA
KY_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 151.3129 | 138.5703 | [8 empty] | 2015-03-31 | KY
KY_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.4091 | 9.8599 | [8 empty] | 2015-03-31 | MA
KY_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.2197 | 9.6843 | [8 empty] | 2015-03-31 | MT
KY_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.2069 | 9.0524 | [8 empty] | 2015-03-31 | NC
KY_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.2338 | 12.1166 | [8 empty] | 2015-03-31 | NE
KY_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | [8 empty] | 2015-03-31 | NJ
KY_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4026 | 1.1969 | [8 empty] | 2015-03-31 | NY
KY_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31 | OK
KY_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.2707 | 2.9953 | [8 empty] | 2015-03-31 | RI
KY_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31 | SC
KY_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31 | TX
KY_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31 | UT
KY_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31 | VA
KY_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31 | WI
KY_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
KY_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
KY_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 101.4941 | 95.7083 | [8 empty] | 2015-03-31
KY_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9903 | 1.8773 | [8 empty] | 2015-03-31
KY_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3848 | 5.1863 | [8 empty] | 2015-03-31
KY_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5752 | 2.4259 | [8 empty] | 2015-03-31
KY_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.2852 | 4.2505 | [8 empty] | 2015-03-31
KY_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2015-03-31
KY_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1610.3488 | 1546.7824 | [8 empty] | 2015-03-31
KY_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | [8 empty] | 2015-03-31
KY_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1525.5936 | [8 empty] | 2015-03-31
KY_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
KY_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
KY_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
KY_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
KY_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
KY_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
KY_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
KY_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
KY_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
KY_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1323 | 1.0905 | [8 empty] | 2015-03-31
KY_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0744 | 1.063 | [8 empty] | 2015-03-31
KY_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.59316 | 0.58888 | [8 empty] | 2015-03-31
KY_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.58849 | 0.58449 | [8 empty] | 2015-03-31
KY_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.73821 | 0.74242 | [8 empty] | 2015-03-31
KY_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.91358 | 0.91154 | [8 empty] | 2015-03-31
KY_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.64536 | 0.64182 | [8 empty] | 2015-03-31
KY_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.65785 | 0.65504 | [8 empty] | 2015-03-31
KY_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.95152 | 0.94595 | [8 empty] | 2015-03-31
KY_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5585 | 1.5383 | [8 empty] | 2015-03-31
KY_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5508 | 1.5311 | [8 empty] | 2015-03-31
KY_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.985 | 1.963 | [8 empty] | 2015-03-31
KY_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3526 | 2.3266 | [8 empty] | 2015-03-31
KY_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7098 | 1.6868 | [8 empty] | 2015-03-31
KY_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.715 | 1.6919 | [8 empty] | 2015-03-31
KY_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2094 | 2.1516 | [8 empty] | 2015-03-31
KY_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4444 | 2.4078 | [8 empty] | 2015-03-31
KY_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.049 | 2.0556 | [8 empty] | 2015-03-31
KY_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0522 | 0.96626 | [8 empty] | 2015-03-31
KY_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0804 | 0.95859 | [8 empty] | 2015-03-31
KY_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3061 | 1.2136 | [8 empty] | 2015-03-31
KY_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5357 | 1.4375 | [8 empty] | 2015-03-31
KY_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2535 | 1.1308 | [8 empty] | 2015-03-31
KY_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2568 | 1.1342 | [8 empty] | 2015-03-31
KY_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5129 | 1.3895 | [8 empty] | 2015-03-31
KY_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6132 | 1.4954 | [8 empty] | 2015-03-31
KY_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
KY_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
KY_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
KY_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
KY_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
KY_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
KY_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
KY_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
KY_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
KY_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
KY_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
KY_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
KY_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | [8 empty] | 2015-03-31
KY_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
KY_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 275.4544 | [8 empty] | 2015-03-31
KY_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | [8 empty] | 2015-03-31
KY_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
KY_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
KY_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | [8 empty] | 2015-03-31
KY_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 572.0976 | [8 empty] | 2015-03-31
KY_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 572.0976 | [8 empty] | 2015-03-31
KY_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 741.608 | [8 empty] | 2015-03-31
KY_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | [8 empty] | 2015-03-31
KY_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | [8 empty] | 2015-03-31
KY_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | [8 empty] | 2015-03-31
KY_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 826.3632 | [8 empty] | 2015-03-31
KY_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 974.6848 | 953.496 | [8 empty] | 2015-03-31
KY_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | [8 empty] | 2015-03-31
KY_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | [8 empty] | 2015-03-31
KY_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | [8 empty] | 2015-03-31
KY_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | [8 empty] | 2015-03-31
KY_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 593.2864 | [8 empty] | 2015-03-31
KY_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
KY_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
KY_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2015-03-31
KY_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2015-03-31
KY_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
KY_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.144 | 0.14255 | [8 empty] | 2015-03-31
KY_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14244 | 0.14109 | [8 empty] | 2015-03-31
KY_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18658 | 0.18806 | [8 empty] | 2015-03-31
KY_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.24547 | 0.24479 | [8 empty] | 2015-03-31
KY_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.14879 | 0.14765 | [8 empty] | 2015-03-31
KY_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15293 | 0.15195 | [8 empty] | 2015-03-31
KY_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.25541 | 0.25353 | [8 empty] | 2015-03-31
KY_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40976 | 0.40287 | [8 empty] | 2015-03-31
KY_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40719 | 0.40047 | [8 empty] | 2015-03-31
KY_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.53555 | 0.53149 | [8 empty] | 2015-03-31
KY_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.66222 | 0.65335 | [8 empty] | 2015-03-31
KY_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.43143 | 0.42386 | [8 empty] | 2015-03-31
KY_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.43318 | 0.42556 | [8 empty] | 2015-03-31
KY_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.58892 | 0.5821 | [8 empty] | 2015-03-31
KY_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.69127 | 0.67876 | [8 empty] | 2015-03-31
KY_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65032 | 0.65273 | [8 empty] | 2015-03-31
KY_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.29051 | 0.2611 | [8 empty] | 2015-03-31
KY_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29004 | 0.25851 | [8 empty] | 2015-03-31
KY_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.36602 | 0.33603 | [8 empty] | 2015-03-31
KY_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.4471 | 0.41476 | [8 empty] | 2015-03-31
KY_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34635 | 0.30519 | [8 empty] | 2015-03-31
KY_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34747 | 0.30634 | [8 empty] | 2015-03-31
KY_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.42603 | 0.38459 | [8 empty] | 2015-03-31
KY_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46822 | 0.43054 | [8 empty] | 2015-03-31
MD_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7505 | 1.6474 | 1.7307 | 1.6282 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8976 | 1.742 | 1.8631 | 1.7432 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3695 | 1.3 | 1.3429 | 1.2972 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7423 | 1.6107 | 1.6732 | 1.5646 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5868 | 1.4874 | 1.5414 | 1.4634 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 550.9088 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 656.8528 | 741.608 | 678.0416 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 593.2864 | 572.0976 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.43606 | 0.39969 | 0.43299 | 0.39788 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52368 | 0.46945 | 0.51902 | 0.47614 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.43068 | 0.40618 | 0.42469 | 0.40717 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.47207 | 0.4248 | 0.45297 | 0.41271 | [6 empty] | 2015-03-31
MD_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.4914 | 0.45316 | 0.47927 | 0.44998 | [6 empty] | 2015-03-31
MD_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10340.1344 | 9746.848 | 10022.3024 | 9662.0928 | [6 empty] | 2015-03-31
MD_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24536.6304 | 24134.0432 | 24642.5744 | 24303.5536 | [6 empty] | 2015-03-31
MD_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 198645.0003 | 194703.8835 | 200467.2371 | 196589.6867 | [6 empty] | 2015-03-31
MD_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23456.0016 | 21612.576 | 23561.9456 | 21739.7088 | [6 empty] | 2015-03-31
MD_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MD_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
MD_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
MD_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
MD_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
MD_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
MD_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
MD_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
MD_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
MD_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
MD_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
MD_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
MD_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MD_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MD_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MD_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MD_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MD_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MD_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MD_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MD_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MD_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 396.8551 | 391.295 | 396.3566 | 390.9955 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 396.8551 | 391.295 | 396.3566 | 390.9955 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
MD_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 376.6758 | 371.3964 | 376.1995 | 371.1186 | [6 empty] | 2015-03-31
MD_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 376.6758 | 371.3964 | 376.1995 | 371.1186 | [6 empty] | 2015-03-31
MD_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.5336 | 4.4252 | 4.6064 | 4.5014 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1868.7531 | 921.2921 | 1866.3755 | 920.5868 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 921.2921 | 0 | 920.5868 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1868.7531 | 1842.6001 | 1866.3755 | 1841.1735 | [6 empty] | 2015-03-31
MD_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 911.6361 | 889.8371 | 926.277 | 905.1596 | [6 empty] | 2015-03-31
MD_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2180.3705 | 2141.6957 | 2177.6759 | 2139.9521 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MD_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0867 | 10.4546 | 10.7525 | 10.3755 | [6 empty] | 2015-03-31
MD_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.269 | 32.8318 | 35.4383 | 34.9461 | [6 empty] | 2015-03-31
MD_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 279.3447 | 273.8179 | 281.9128 | 276.4574 | [6 empty] | 2015-03-31
MD_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.734 | 29.3964 | 33.8773 | 31.2482 | [6 empty] | 2015-03-31
MD_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.8705 | 42.6821 | 42.9523 | 42.8773 | [6 empty] | 2015-03-31
MD_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.78148 | 0.7693 | 0.79005 | 0.77743 | [6 empty] | 2015-03-31
MD_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.8533 | 9.6634 | 9.9118 | 9.7813 | [6 empty] | 2015-03-31
MD_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.67361 | 0.65258 | 0.68198 | 0.66029 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.0813 | 4.97 | 10.0687 | 4.9662 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.97 | 0 | 4.9662 | [6 empty] | 2015-03-31
MD_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 30.244 | 29.8203 | 30.206 | 29.7974 | [6 empty] | 2015-03-31
MD_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.7055 | 19.2343 | 20.022 | 19.5656 | [6 empty] | 2015-03-31
MD_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 40.3842 | 39.6668 | 40.3335 | 39.6364 | [6 empty] | 2015-03-31
MD_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8436 | 3.8147 | 3.8444 | 3.8225 | [6 empty] | 2015-03-31
MD_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
MD_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
MD_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MD_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
MD_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4528.3746 | 4397.5864 | 4561.0415 | 4425.7301 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.0285 | 8.9015 | 9.0725 | 8.9435 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 38.7809 | 36.9916 | 39.1702 | 37.3106 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.524 | 6.2559 | 6.5202 | 6.2787 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6938 | 5.3614 | 5.6869 | 5.3729 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3305.4528 | 3241.8864 | 3305.4528 | 3241.8864 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12713.28 | 11590.2736 | 12819.224 | 11653.84 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2542.656 | 2436.712 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2097.6912 | 1928.1808 | 2118.88 | 1970.5584 | [6 empty] | 2015-03-31
MD_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
MD_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MD_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.04 | 2.0423 | 3.1666 | 2.0716 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2376 | 2.1936 | 2.2373 | 2.1937 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.6396 | 12.4459 | 13.7528 | 12.5167 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7673 | 1.6748 | 1.7887 | 1.7015 | [6 empty] | 2015-03-31
MD_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4721 | 1.355 | 1.4891 | 1.3771 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.6976 | 21.8311 | 25.8192 | 21.8875 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.2229 | 21.3841 | 25.3605 | 21.456 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.9997 | 20.1707 | 23.1387 | 20.23 | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.7807 | 26.9508 | 31.7922 | 26.8675 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.3993 | 5.4349 | 6.4193 | 5.4424 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7712.7232 | 6547.3392 | 7755.1008 | 6568.528 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7564.4016 | 6420.2064 | 7606.7792 | 6441.3952 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6907.5488 | 6059.9968 | 6949.9264 | 6081.1856 | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9534.96 | 8094.1216 | 9534.96 | 8072.9328 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1928.1808 | 1631.5376 | 1928.1808 | 1631.5376 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
MD_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
MD_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MD_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MD_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MD_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
MD_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
MD_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
MD_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
MD_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7711.4307 | 6551.1532 | 7747.9178 | 6568.083 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7568.9784 | 6417.0281 | 7610.2754 | 6438.5983 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6052.8986 | 6777.6191 | 6070.6972 | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MD_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MD_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MD_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MD_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MD_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MD_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4513 | 1.3373 | 1.4762 | 1.3525 | [6 empty] | 2015-03-31
MD_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 145.9205 | 134.4569 | 148.4197 | 135.9806 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.2905 | 9.6649 | 11.3439 | 9.6899 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.0819 | 9.467 | 11.1424 | 9.4989 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.1051 | 8.9299 | 10.1662 | 8.9561 | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.9632 | 11.8411 | 13.9682 | 11.8045 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3456 | 1.1428 | 1.3498 | 1.1444 | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
MD_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.1542 | 2.9064 | 3.2082 | 2.9393 | [6 empty] | 2015-03-31
MD_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MD_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MD_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MD_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MD_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MD_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.3622 | 97.23 | 102.706 | 97.0175 | [6 empty] | 2015-03-31
MD_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0776 | 1.9378 | 2.0632 | 1.9129 | [6 empty] | 2015-03-31
MD_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3167 | 5.1267 | 5.2861 | 5.0739 | [6 empty] | 2015-03-31
MD_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.538 | 2.3891 | 2.5279 | 2.3727 | [6 empty] | 2015-03-31
MD_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.3658 | 4.328 | 4.3357 | 4.2945 | [6 empty] | 2015-03-31
MD_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
MD_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1589.16 | 1546.7824 | 1589.16 | 1525.5936 | [6 empty] | 2015-03-31
MD_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
MD_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | 1504.4048 | 1483.216 | [6 empty] | 2015-03-31
MD_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
MD_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
MD_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
MD_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
MD_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MD_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MD_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MD_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MD_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MD_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.118 | 1.078 | 1.1115 | 1.0669 | [6 empty] | 2015-03-31
MD_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0496 | 1.0498 | 1.0551 | 1.0541 | [6 empty] | 2015-03-31
MD_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.61732 | 0.6097 | 0.60635 | 0.59428 | [6 empty] | 2015-03-31
MD_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.61308 | 0.60572 | 0.60188 | 0.59014 | [6 empty] | 2015-03-31
MD_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.75732 | 0.75498 | 0.74463 | 0.73752 | [6 empty] | 2015-03-31
MD_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.93557 | 0.9286 | 0.92419 | 0.90447 | [6 empty] | 2015-03-31
MD_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.695 | 0.689 | 0.69263 | 0.68127 | [6 empty] | 2015-03-31
MD_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.70688 | 0.70259 | 0.7046 | 0.69499 | [6 empty] | 2015-03-31
MD_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.9813 | 0.97282 | 0.97604 | 0.9531 | [6 empty] | 2015-03-31
MD_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6244 | 1.596 | 1.6065 | 1.5654 | [6 empty] | 2015-03-31
MD_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6172 | 1.5893 | 1.5991 | 1.5585 | [6 empty] | 2015-03-31
MD_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0237 | 2.0052 | 2.0192 | 1.9702 | [6 empty] | 2015-03-31
MD_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4156 | 2.3777 | 2.4064 | 2.3381 | [6 empty] | 2015-03-31
MD_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8287 | 1.8016 | 1.8427 | 1.8018 | [6 empty] | 2015-03-31
MD_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8335 | 1.8063 | 1.8478 | 1.8066 | [6 empty] | 2015-03-31
MD_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3516 | 2.3129 | 2.3606 | 2.2945 | [6 empty] | 2015-03-31
MD_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5218 | 2.4864 | 2.532 | 2.4617 | [6 empty] | 2015-03-31
MD_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1248 | 2.1301 | 2.1267 | 2.1279 | [6 empty] | 2015-03-31
MD_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1283 | 0.99286 | 1.1062 | 0.97241 | [6 empty] | 2015-03-31
MD_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1309 | 0.98506 | 1.109 | 0.9644 | [6 empty] | 2015-03-31
MD_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3942 | 1.2387 | 1.3674 | 1.2178 | [6 empty] | 2015-03-31
MD_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5853 | 1.4687 | 1.5679 | 1.4409 | [6 empty] | 2015-03-31
MD_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3216 | 1.1968 | 1.3277 | 1.1965 | [6 empty] | 2015-03-31
MD_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3245 | 1.1981 | 1.3309 | 1.1983 | [6 empty] | 2015-03-31
MD_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5944 | 1.466 | 1.5956 | 1.4544 | [6 empty] | 2015-03-31
MD_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6949 | 1.5647 | 1.6913 | 1.5521 | [6 empty] | 2015-03-31
MD_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MD_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
MD_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MD_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MD_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MD_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MD_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MD_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MD_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MD_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MD_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
MD_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MD_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
MD_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
MD_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
MD_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
MD_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
MD_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
MD_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | 360.2096 | 339.0208 | [6 empty] | 2015-03-31
MD_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
MD_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
MD_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 741.608 | 741.608 | 720.4192 | [6 empty] | 2015-03-31
MD_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | 911.1184 | 889.9296 | [6 empty] | 2015-03-31
MD_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 635.664 | [6 empty] | 2015-03-31
MD_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
MD_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | 868.7408 | 847.552 | [6 empty] | 2015-03-31
MD_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | 974.6848 | 932.3072 | [6 empty] | 2015-03-31
MD_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | 932.3072 | 932.3072 | [6 empty] | 2015-03-31
MD_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
MD_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
MD_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 508.5312 | 466.1536 | [6 empty] | 2015-03-31
MD_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 550.9088 | [6 empty] | 2015-03-31
MD_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
MD_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
MD_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 614.4752 | 550.9088 | [6 empty] | 2015-03-31
MD_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
MD_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MD_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14244 | 0.13999 | 0.13967 | 0.13575 | [6 empty] | 2015-03-31
MD_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14109 | 0.13872 | 0.13823 | 0.13441 | [6 empty] | 2015-03-31
MD_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18356 | 0.18404 | 0.18188 | 0.17962 | [6 empty] | 2015-03-31
MD_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23862 | 0.23636 | 0.23693 | 0.23044 | [6 empty] | 2015-03-31
MD_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15569 | 0.15423 | 0.15715 | 0.15392 | [6 empty] | 2015-03-31
MD_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15994 | 0.1586 | 0.16143 | 0.15839 | [6 empty] | 2015-03-31
MD_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24852 | 0.24576 | 0.24935 | 0.24183 | [6 empty] | 2015-03-31
MD_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40434 | 0.39504 | 0.40362 | 0.39002 | [6 empty] | 2015-03-31
MD_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40201 | 0.39287 | 0.40118 | 0.38778 | [6 empty] | 2015-03-31
MD_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.526 | 0.51994 | 0.52875 | 0.51542 | [6 empty] | 2015-03-31
MD_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.64676 | 0.63428 | 0.64944 | 0.62674 | [6 empty] | 2015-03-31
MD_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.44605 | 0.43739 | 0.4567 | 0.44348 | [6 empty] | 2015-03-31
MD_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.44761 | 0.43892 | 0.45836 | 0.44503 | [6 empty] | 2015-03-31
MD_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.60358 | 0.59252 | 0.61438 | 0.59413 | [6 empty] | 2015-03-31
MD_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67723 | 0.66285 | 0.68729 | 0.6615 | [6 empty] | 2015-03-31
MD_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64967 | 0.65156 | 0.65406 | 0.65451 | [6 empty] | 2015-03-31
MD_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.28908 | 0.25596 | 0.28569 | 0.25147 | [6 empty] | 2015-03-31
MD_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.28903 | 0.25343 | 0.28583 | 0.24884 | [6 empty] | 2015-03-31
MD_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.36556 | 0.32883 | 0.36165 | 0.32502 | [6 empty] | 2015-03-31
MD_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.43589 | 0.40015 | 0.43484 | 0.39501 | [6 empty] | 2015-03-31
MD_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.35065 | 0.31026 | 0.35734 | 0.31434 | [6 empty] | 2015-03-31
MD_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.35162 | 0.31141 | 0.35837 | 0.31557 | [6 empty] | 2015-03-31
MD_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.43119 | 0.39044 | 0.43715 | 0.39161 | [6 empty] | 2015-03-31
MD_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46641 | 0.42639 | 0.47091 | 0.42501 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8782 | 1.7653 | 1.7901 | 1.6858 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0025 | 1.8479 | 1.9144 | 1.7905 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5149 | 1.436 | 1.4294 | 1.3705 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8643 | 1.7293 | 1.733 | 1.6213 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.735 | 1.623 | 1.6368 | 1.555 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 572.0976 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 678.0416 | 741.608 | 678.0416 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 614.4752 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 741.608 | 699.2304 | 720.4192 | 678.0416 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.4497 | 0.41159 | 0.44507 | 0.40916 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.53656 | 0.48279 | 0.52804 | 0.48356 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.47091 | 0.44278 | 0.45615 | 0.43688 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.49006 | 0.44079 | 0.46607 | 0.42734 | [6 empty] | 2015-03-31
MO_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.53029 | 0.48866 | 0.51446 | 0.48334 | [6 empty] | 2015-03-31
MO_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10530.8336 | 9916.3584 | 10276.568 | 9916.3584 | [6 empty] | 2015-03-31
MO_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25447.7488 | 25023.9728 | 25384.1824 | 25023.9728 | [6 empty] | 2015-03-31
MO_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 208074.0163 | 203815.0675 | 207078.1427 | 202925.1379 | [6 empty] | 2015-03-31
MO_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 24261.176 | 22311.8064 | 24239.9872 | 22311.8064 | [6 empty] | 2015-03-31
MO_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MO_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
MO_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
MO_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
MO_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
MO_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
MO_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
MO_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
MO_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
MO_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
MO_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
MO_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
MO_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MO_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MO_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MO_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MO_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MO_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MO_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MO_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MO_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MO_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 431.9451 | 426.0345 | 412.0585 | 406.6235 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 431.9451 | 426.0345 | 412.0585 | 406.6235 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
MO_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 409.9796 | 404.3694 | 391.0982 | 385.9511 | [6 empty] | 2015-03-31
MO_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 409.9796 | 404.3694 | 391.0982 | 385.9511 | [6 empty] | 2015-03-31
MO_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.9893 | 4.8758 | 5.3287 | 5.1917 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 2034.072 | 1003.0845 | 1940.3966 | 957.3817 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 1003.0845 | 0 | 957.3817 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 2034.072 | 2006.1754 | 1940.3966 | 1914.719 | [6 empty] | 2015-03-31
MO_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1003.2858 | 980.4519 | 1071.5326 | 1043.9831 | [6 empty] | 2015-03-31
MO_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2373.1104 | 2331.741 | 2263.9017 | 2225.5439 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MO_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.29 | 10.6457 | 11.025 | 10.6378 | [6 empty] | 2015-03-31
MO_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.5832 | 34.032 | 36.501 | 35.9749 | [6 empty] | 2015-03-31
MO_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 292.6237 | 286.6374 | 291.2086 | 285.3838 | [6 empty] | 2015-03-31
MO_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.8882 | 30.3548 | 34.857 | 32.0775 | [6 empty] | 2015-03-31
MO_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.5362 | 43.3441 | 44.0023 | 43.9251 | [6 empty] | 2015-03-31
MO_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.81006 | 0.79549 | 0.82784 | 0.81242 | [6 empty] | 2015-03-31
MO_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.1918 | 9.9611 | 10.438 | 10.1881 | [6 empty] | 2015-03-31
MO_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.70215 | 0.67822 | 0.71767 | 0.69258 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.9727 | 5.4113 | 10.4675 | 5.1647 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.4113 | 0 | 5.1647 | [6 empty] | 2015-03-31
MO_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.9182 | 32.4677 | 31.4026 | 30.9884 | [6 empty] | 2015-03-31
MO_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 21.6866 | 21.193 | 23.1618 | 22.5663 | [6 empty] | 2015-03-31
MO_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 43.955 | 43.1884 | 41.9313 | 41.2207 | [6 empty] | 2015-03-31
MO_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.9033 | 3.8715 | 3.904 | 3.8783 | [6 empty] | 2015-03-31
MO_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
MO_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
MO_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MO_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
MO_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4832.6139 | 4686.1051 | 4980.6924 | 4812.9044 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.6445 | 9.4846 | 9.2508 | 9.1289 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 42.6093 | 40.5871 | 40.3388 | 38.6923 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.9036 | 6.6399 | 6.7093 | 6.4605 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.071 | 5.725 | 5.8668 | 5.5441 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3538.5296 | 3432.5856 | 3411.3968 | 3347.8304 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13454.888 | 12204.7488 | 13221.8112 | 12162.3712 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2585.0336 | 2457.9008 | 2606.2224 | 2479.0896 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2161.2576 | 1991.7472 | 2182.4464 | 2012.936 | [6 empty] | 2015-03-31
MO_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MO_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | Yes | Yes | Yes | [6 empty] | 2015-03-31
MO_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.5728 | 2.3833 | 4.0423 | 2.7448 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3915 | 2.3271 | 2.3148 | 2.2726 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.4506 | 13.1077 | 14.1947 | 13.0474 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8168 | 1.7229 | 1.8272 | 1.7367 | [6 empty] | 2015-03-31
MO_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5188 | 1.4 | 1.522 | 1.4061 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.5316 | 22.7583 | 26.5252 | 22.6532 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 26.1306 | 22.5817 | 26.1359 | 22.484 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.746 | 20.8887 | 23.7783 | 20.9863 | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.9057 | 27.9981 | 32.7747 | 27.8799 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.7384 | 5.7175 | 6.7272 | 5.6946 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7966.9888 | 6822.7936 | 7966.9888 | 6801.6048 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7839.856 | 6780.416 | 7839.856 | 6738.0384 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7119.4368 | 6271.8848 | 7140.6256 | 6293.0736 | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9873.9808 | 8411.9536 | 9831.6032 | 8369.576 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2012.936 | 1716.2928 | 2012.936 | 1716.2928 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
MO_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
MO_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MO_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MO_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MO_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
MO_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
MO_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
MO_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
MO_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 6829.4045 | 7852.8447 | 6797.8332 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7841.3604 | 6776.4113 | 7842.9496 | 6747.0648 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6268.3675 | 6777.6191 | 6297.6292 | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MO_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MO_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MO_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
MO_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MO_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MO_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5724 | 1.4332 | 1.6472 | 1.4882 | [6 empty] | 2015-03-31
MO_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 158.0965 | 144.1002 | 165.6169 | 149.6323 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.6569 | 9.9991 | 11.6541 | 9.9529 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.4807 | 9.9215 | 11.483 | 9.8785 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.433 | 9.2477 | 10.4472 | 9.2909 | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.4575 | 12.3012 | 14.3999 | 12.2493 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4169 | 1.2022 | 1.4145 | 1.1974 | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
MO_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.4174 | 3.1148 | 3.5799 | 3.2344 | [6 empty] | 2015-03-31
MO_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MO_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MO_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MO_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MO_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MO_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.439 | 97.8482 | 104.9343 | 97.4009 | [6 empty] | 2015-03-31
MO_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2069 | 2.1017 | 2.1463 | 2.0326 | [6 empty] | 2015-03-31
MO_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.4669 | 5.2711 | 5.4899 | 5.2884 | [6 empty] | 2015-03-31
MO_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5965 | 2.4472 | 2.6033 | 2.4468 | [6 empty] | 2015-03-31
MO_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5801 | 4.5447 | 4.4748 | 4.4349 | [6 empty] | 2015-03-31
MO_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 635.664 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
MO_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1631.5376 | 1589.16 | 1652.7264 | 1589.16 | [6 empty] | 2015-03-31
MO_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 741.608 | [6 empty] | 2015-03-31
MO_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1546.7824 | 1525.5936 | [6 empty] | 2015-03-31
MO_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
MO_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
MO_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
MO_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
MO_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MO_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MO_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MO_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MO_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | No | No | [6 empty] | 2015-03-31
MO_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1495 | 1.1084 | 1.1544 | 1.112 | [6 empty] | 2015-03-31
MO_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.07 | 1.0589 | 1.0801 | 1.0673 | [6 empty] | 2015-03-31
MO_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.68897 | 0.68257 | 0.64239 | 0.63149 | [6 empty] | 2015-03-31
MO_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.68403 | 0.67792 | 0.63733 | 0.62678 | [6 empty] | 2015-03-31
MO_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84385 | 0.84277 | 0.79027 | 0.77956 | [6 empty] | 2015-03-31
MO_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0443 | 1.0379 | 1.0005 | 0.98135 | [6 empty] | 2015-03-31
MO_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.74753 | 0.74172 | 0.71778 | 0.70287 | [6 empty] | 2015-03-31
MO_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.76121 | 0.75431 | 0.73012 | 0.71711 | [6 empty] | 2015-03-31
MO_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0755 | 1.0684 | 1.0327 | 1.0063 | [6 empty] | 2015-03-31
MO_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7765 | 1.7509 | 1.6892 | 1.6511 | [6 empty] | 2015-03-31
MO_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7684 | 1.7432 | 1.6808 | 1.6433 | [6 empty] | 2015-03-31
MO_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2373 | 2.2185 | 2.1392 | 2.0883 | [6 empty] | 2015-03-31
MO_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6693 | 2.6318 | 2.5868 | 2.5188 | [6 empty] | 2015-03-31
MO_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.9508 | 1.9178 | 1.9025 | 1.8528 | [6 empty] | 2015-03-31
MO_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.9527 | 1.9235 | 1.9083 | 1.8583 | [6 empty] | 2015-03-31
MO_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.5237 | 2.4841 | 2.4618 | 2.3838 | [6 empty] | 2015-03-31
MO_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.748 | 2.6981 | 2.6733 | 2.586 | [6 empty] | 2015-03-31
MO_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2162 | 2.2157 | 2.1858 | 2.1835 | [6 empty] | 2015-03-31
MO_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.2231 | 1.0866 | 1.1617 | 1.0251 | [6 empty] | 2015-03-31
MO_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.2237 | 1.0777 | 1.1644 | 1.016 | [6 empty] | 2015-03-31
MO_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4713 | 1.3623 | 1.4415 | 1.2881 | [6 empty] | 2015-03-31
MO_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.7223 | 1.6108 | 1.6594 | 1.5392 | [6 empty] | 2015-03-31
MO_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.408 | 1.2743 | 1.3728 | 1.2321 | [6 empty] | 2015-03-31
MO_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.4119 | 1.2782 | 1.3766 | 1.234 | [6 empty] | 2015-03-31
MO_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.706 | 1.5695 | 1.6617 | 1.5094 | [6 empty] | 2015-03-31
MO_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.8102 | 1.6786 | 1.7545 | 1.6069 | [6 empty] | 2015-03-31
MO_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MO_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
MO_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MO_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MO_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MO_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MO_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MO_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MO_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MO_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MO_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
MO_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MO_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
MO_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
MO_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 275.4544 | 275.4544 | [6 empty] | 2015-03-31
MO_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | 360.2096 | 360.2096 | [6 empty] | 2015-03-31
MO_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 211.888 | [6 empty] | 2015-03-31
MO_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
MO_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | 381.3984 | 360.2096 | [6 empty] | 2015-03-31
MO_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 593.2864 | 593.2864 | [6 empty] | 2015-03-31
MO_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 593.2864 | 593.2864 | 572.0976 | [6 empty] | 2015-03-31
MO_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 783.9856 | 783.9856 | 762.7968 | [6 empty] | 2015-03-31
MO_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 974.6848 | 995.8736 | 953.496 | [6 empty] | 2015-03-31
MO_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
MO_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
MO_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 889.9296 | 868.7408 | [6 empty] | 2015-03-31
MO_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 995.8736 | 1017.0624 | 974.6848 | [6 empty] | 2015-03-31
MO_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 932.3072 | 953.496 | 953.496 | [6 empty] | 2015-03-31
MO_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 423.776 | 381.3984 | [6 empty] | 2015-03-31
MO_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 423.776 | 360.2096 | [6 empty] | 2015-03-31
MO_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 529.72 | 487.3424 | [6 empty] | 2015-03-31
MO_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
MO_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
MO_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
MO_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
MO_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 635.664 | 699.2304 | 614.4752 | [6 empty] | 2015-03-31
MO_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MO_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15298 | 0.15093 | 0.14869 | 0.1451 | [6 empty] | 2015-03-31
MO_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15141 | 0.14944 | 0.14704 | 0.14357 | [6 empty] | 2015-03-31
MO_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.20076 | 0.20162 | 0.19275 | 0.19044 | [6 empty] | 2015-03-31
MO_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.26001 | 0.25791 | 0.2576 | 0.25119 | [6 empty] | 2015-03-31
MO_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16116 | 0.15935 | 0.16009 | 0.15576 | [6 empty] | 2015-03-31
MO_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16551 | 0.16375 | 0.16454 | 0.16041 | [6 empty] | 2015-03-31
MO_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.26598 | 0.26252 | 0.2654 | 0.25662 | [6 empty] | 2015-03-31
MO_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.42911 | 0.42075 | 0.42594 | 0.41313 | [6 empty] | 2015-03-31
MO_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.42647 | 0.41826 | 0.42312 | 0.41053 | [6 empty] | 2015-03-31
MO_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.56912 | 0.56293 | 0.55914 | 0.54555 | [6 empty] | 2015-03-31
MO_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.69874 | 0.68642 | 0.69991 | 0.67704 | [6 empty] | 2015-03-31
MO_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.45941 | 0.44999 | 0.46504 | 0.44891 | [6 empty] | 2015-03-31
MO_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.46112 | 0.45182 | 0.46694 | 0.4507 | [6 empty] | 2015-03-31
MO_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.63086 | 0.61816 | 0.63477 | 0.61066 | [6 empty] | 2015-03-31
MO_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.72018 | 0.70384 | 0.72695 | 0.69765 | [6 empty] | 2015-03-31
MO_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.66206 | 0.66185 | 0.67476 | 0.67397 | [6 empty] | 2015-03-31
MO_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.30471 | 0.27201 | 0.29796 | 0.26556 | [6 empty] | 2015-03-31
MO_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.30489 | 0.26912 | 0.29792 | 0.26255 | [6 empty] | 2015-03-31
MO_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.38711 | 0.35482 | 0.37856 | 0.34258 | [6 empty] | 2015-03-31
MO_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.46643 | 0.43131 | 0.46399 | 0.42498 | [6 empty] | 2015-03-31
MO_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.36505 | 0.32183 | 0.36647 | 0.3201 | [6 empty] | 2015-03-31
MO_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.36631 | 0.32311 | 0.36772 | 0.32146 | [6 empty] | 2015-03-31
MO_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.45172 | 0.40756 | 0.452 | 0.40266 | [6 empty] | 2015-03-31
MO_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.4897 | 0.44812 | 0.48978 | 0.44192 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.756 | 1.6489 | 1.6665 | 1.5672 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9547 | 1.7986 | 1.7873 | 1.6688 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4093 | 1.3357 | 1.3112 | 1.2604 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7514 | 1.6208 | 1.6014 | 1.5013 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6148 | 1.5086 | 1.5034 | 1.4289 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 550.9088 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 593.2864 | 572.0976 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 593.2864 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 678.0416 | 635.664 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.43607 | 0.39956 | 0.4299 | 0.39555 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.5447 | 0.49016 | 0.50901 | 0.46708 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.44231 | 0.41623 | 0.41844 | 0.40223 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.47374 | 0.42706 | 0.44385 | 0.40618 | [6 empty] | 2015-03-31
NJ_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.49761 | 0.45843 | 0.4773 | 0.44907 | [6 empty] | 2015-03-31
NJ_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10297.7568 | 9704.4704 | 10043.4912 | 9683.2816 | [6 empty] | 2015-03-31
NJ_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24790.896 | 24367.12 | 24494.2528 | 24155.232 | [6 empty] | 2015-03-31
NJ_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 202183.5299 | 198051.7139 | 198305.9795 | 194640.3171 | [6 empty] | 2015-03-31
NJ_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23561.9456 | 21718.52 | 23244.1136 | 21443.0656 | [6 empty] | 2015-03-31
NJ_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NJ_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
NJ_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
NJ_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
NJ_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
NJ_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
NJ_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
NJ_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
NJ_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
NJ_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
NJ_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
NJ_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
NJ_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NJ_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NJ_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NJ_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
NJ_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
NJ_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
NJ_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NJ_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NJ_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NJ_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 400.2151 | 394.2566 | 380.3838 | 375.2628 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 400.2151 | 394.2566 | 380.3838 | 375.2628 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
NJ_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 379.8646 | 374.2015 | 361.0361 | 356.1801 | [6 empty] | 2015-03-31
NJ_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 379.8646 | 374.2015 | 361.0361 | 356.1801 | [6 empty] | 2015-03-31
NJ_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.7032 | 4.5932 | 4.8008 | 4.6859 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1884.6034 | 928.2647 | 1791.245 | 883.5446 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 928.2647 | 0 | 883.5446 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1884.6034 | 1856.5483 | 1791.245 | 1767.1525 | [6 empty] | 2015-03-31
NJ_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 945.7555 | 923.6189 | 965.3655 | 942.2748 | [6 empty] | 2015-03-31
NJ_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2198.9153 | 2157.863 | 2089.8651 | 2053.8849 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NJ_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0564 | 10.4253 | 10.7709 | 10.3935 | [6 empty] | 2015-03-31
NJ_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.6341 | 33.1571 | 35.2004 | 34.7382 | [6 empty] | 2015-03-31
NJ_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 284.3283 | 278.5295 | 278.8762 | 273.7157 | [6 empty] | 2015-03-31
NJ_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.8649 | 29.544 | 33.4101 | 30.8427 | [6 empty] | 2015-03-31
NJ_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.662 | 42.4739 | 43.0852 | 43.0102 | [6 empty] | 2015-03-31
NJ_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.78314 | 0.77003 | 0.79437 | 0.78155 | [6 empty] | 2015-03-31
NJ_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.893 | 9.6884 | 9.9674 | 9.8331 | [6 empty] | 2015-03-31
NJ_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.675 | 0.65347 | 0.68482 | 0.66299 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.1667 | 5.0077 | 9.6629 | 4.7664 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.0077 | 0 | 4.7664 | [6 empty] | 2015-03-31
NJ_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 30.5001 | 30.046 | 28.9887 | 28.5985 | [6 empty] | 2015-03-31
NJ_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.4431 | 19.9646 | 20.8669 | 20.3678 | [6 empty] | 2015-03-31
NJ_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 40.7261 | 39.967 | 38.7081 | 38.0416 | [6 empty] | 2015-03-31
NJ_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8437 | 3.8136 | 3.8388 | 3.8162 | [6 empty] | 2015-03-31
NJ_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
NJ_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
NJ_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NJ_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
NJ_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4709.081 | 4579.1618 | 4650.5031 | 4509.5496 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.1861 | 9.0357 | 8.7892 | 8.7166 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 39.6968 | 37.6572 | 37.4237 | 36.1392 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.6177 | 6.3577 | 6.2491 | 6.012 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.7902 | 5.4578 | 5.4307 | 5.111 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3411.3968 | 3326.6416 | 3241.8864 | 3178.32 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13031.112 | 11780.9728 | 12692.0912 | 11632.6512 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2563.8448 | 2436.712 | 2500.2784 | 2394.3344 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2161.2576 | 1991.7472 | 2076.5024 | 1906.992 | [6 empty] | 2015-03-31
NJ_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
NJ_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NJ_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.1483 | 2.0574 | 3.3937 | 2.2458 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3112 | 2.2541 | 2.1903 | 2.1567 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.98 | 12.6468 | 13.6249 | 12.4934 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8015 | 1.709 | 1.7571 | 1.6704 | [6 empty] | 2015-03-31
NJ_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5082 | 1.3913 | 1.4562 | 1.3435 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.816 | 22.0114 | 25.3383 | 21.6576 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.3661 | 21.5904 | 24.9038 | 21.265 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.1358 | 20.3444 | 22.7211 | 19.9672 | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.7375 | 26.9612 | 31.2582 | 26.6296 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.3882 | 5.4373 | 6.2999 | 5.3506 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7755.1008 | 6610.9056 | 7606.7792 | 6504.9616 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7606.7792 | 6483.7728 | 7479.6464 | 6377.8288 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6949.9264 | 6102.3744 | 6822.7936 | 5996.4304 | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9513.7712 | 8094.1216 | 9386.6384 | 7988.1776 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1906.992 | 1631.5376 | 1885.8032 | 1610.3488 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
NJ_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | [6 empty] | 2015-03-31
NJ_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
NJ_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
NJ_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NJ_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
NJ_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
NJ_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
NJ_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7746.9431 | 6605.2482 | 7603.6221 | 6499.0923 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7611.9281 | 6478.9206 | 7473.2262 | 6381.2614 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6105.023 | 6777.6191 | 5991.8113 | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NJ_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NJ_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NJ_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
NJ_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NJ_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NJ_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4876 | 1.3696 | 1.5039 | 1.3801 | [6 empty] | 2015-03-31
NJ_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 149.5716 | 137.7016 | 151.2113 | 138.7634 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.3425 | 9.7447 | 11.1326 | 9.5881 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.1448 | 9.5584 | 10.9417 | 9.4143 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.1649 | 9.0067 | 9.9827 | 8.8397 | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.9442 | 11.8457 | 13.7336 | 11.7 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3433 | 1.1433 | 1.3247 | 1.1251 | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
NJ_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.2331 | 2.9765 | 3.2685 | 2.9995 | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NJ_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NJ_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NJ_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NJ_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 103.772 | 98.4435 | 102.6347 | 97.0394 | [6 empty] | 2015-03-31
NJ_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1224 | 1.9814 | 1.9779 | 1.8292 | [6 empty] | 2015-03-31
NJ_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3626 | 5.1771 | 5.2615 | 5.05 | [6 empty] | 2015-03-31
NJ_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5534 | 2.4063 | 2.5189 | 2.3658 | [6 empty] | 2015-03-31
NJ_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.3761 | 4.3384 | 4.21 | 4.1692 | [6 empty] | 2015-03-31
NJ_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 635.664 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
NJ_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1610.3488 | 1546.7824 | 1589.16 | 1525.5936 | [6 empty] | 2015-03-31
NJ_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
NJ_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | 1504.4048 | 1483.216 | [6 empty] | 2015-03-31
NJ_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
NJ_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
NJ_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
NJ_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
NJ_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NJ_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NJ_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NJ_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NJ_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NJ_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1276 | 1.0886 | 1.1064 | 1.0619 | [6 empty] | 2015-03-31
NJ_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0497 | 1.0497 | 1.0499 | 1.0488 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.63609 | 0.63302 | 0.56756 | 0.55832 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.63175 | 0.62878 | 0.56312 | 0.55419 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.78437 | 0.78667 | 0.68921 | 0.68283 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.96384 | 0.95715 | 0.87631 | 0.86028 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.7217 | 0.71608 | 0.64911 | 0.63856 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.73486 | 0.72841 | 0.66275 | 0.65229 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0113 | 1.0071 | 0.92213 | 0.90025 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6755 | 1.6504 | 1.5217 | 1.4881 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.668 | 1.6434 | 1.5143 | 1.4813 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1057 | 2.0881 | 1.8942 | 1.8553 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4967 | 2.4593 | 2.2993 | 2.2403 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.9023 | 1.8694 | 1.746 | 1.7 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.9041 | 1.8744 | 1.7509 | 1.7052 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.453 | 2.4143 | 2.2351 | 2.1733 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.6196 | 2.5697 | 2.4176 | 2.3423 | [6 empty] | 2015-03-31
NJ_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1343 | 2.1988 | 2.051 | 2.0533 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1487 | 1.0188 | 1.052 | 0.92377 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1493 | 1.0107 | 1.0527 | 0.91567 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4267 | 1.2846 | 1.2988 | 1.1459 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6255 | 1.5117 | 1.4992 | 1.3813 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3595 | 1.2347 | 1.2581 | 1.1293 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3628 | 1.2381 | 1.2591 | 1.133 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6486 | 1.5192 | 1.5115 | 1.3773 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.748 | 1.6193 | 1.6123 | 1.4786 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NJ_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 317.832 | 317.832 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 211.888 | 211.888 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 211.888 | 211.888 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | 339.0208 | 339.0208 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 572.0976 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 762.7968 | 720.4192 | 699.2304 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 889.9296 | 868.7408 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 614.4752 | 593.2864 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 656.8528 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 847.552 | 805.1744 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 974.6848 | 953.496 | 932.3072 | 911.1184 | [6 empty] | 2015-03-31
NJ_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 932.3072 | 911.1184 | 911.1184 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 381.3984 | 339.0208 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 381.3984 | 339.0208 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 487.3424 | 487.3424 | 444.9648 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 593.2864 | 550.9088 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 593.2864 | 529.72 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14618 | 0.1442 | 0.13485 | 0.13181 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14482 | 0.14286 | 0.1334 | 0.13047 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.19143 | 0.19224 | 0.17213 | 0.1711 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.24432 | 0.24216 | 0.23035 | 0.225 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16387 | 0.16213 | 0.15068 | 0.1473 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16808 | 0.16642 | 0.15518 | 0.15183 | [6 empty] | 2015-03-31
NJ_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.25516 | 0.25209 | 0.24094 | 0.23367 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.41431 | 0.40618 | 0.39352 | 0.38226 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.41191 | 0.40396 | 0.39106 | 0.37998 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.54593 | 0.54022 | 0.50699 | 0.49701 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.66273 | 0.65056 | 0.63503 | 0.61521 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.46634 | 0.45683 | 0.4418 | 0.42783 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.46791 | 0.45847 | 0.44344 | 0.42957 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.63054 | 0.61813 | 0.5938 | 0.57342 | [6 empty] | 2015-03-31
NJ_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.69657 | 0.68035 | 0.66802 | 0.64277 | [6 empty] | 2015-03-31
NJ_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64537 | 0.66571 | 0.64637 | 0.64722 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.2922 | 0.26037 | 0.27628 | 0.24484 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29238 | 0.25776 | 0.27649 | 0.24215 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.37209 | 0.33953 | 0.34954 | 0.3118 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.44263 | 0.40772 | 0.42382 | 0.38667 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.36059 | 0.32037 | 0.34443 | 0.30245 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.36166 | 0.32147 | 0.34549 | 0.30367 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.44427 | 0.40327 | 0.4216 | 0.37707 | [6 empty] | 2015-03-31
NJ_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.47672 | 0.4361 | 0.45666 | 0.41208 | [6 empty] | 2015-03-31
NY_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6627 | 1.5625 | 1.6137 | 1.5192 | 1.4907 | 1.4104 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8164 | 1.6728 | 1.7819 | 1.6627 | 1.6148 | 1.533 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3447 | 1.2771 | 1.267 | 1.2156 | 1.3321 | 1.3095 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6269 | 1.5108 | 1.5316 | 1.4304 | 1.3923 | 1.3151 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5152 | 1.4192 | 1.4774 | 1.3945 | 1.5027 | 1.4497 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 593.2864 | 550.9088 | 614.4752 | 572.0976 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 656.8528 | 741.608 | 678.0416 | 720.4192 | 678.0416 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 572.0976 | 550.9088 | 593.2864 | 593.2864 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 572.0976 | 614.4752 | 550.9088 | 593.2864 | 550.9088 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 656.8528 | 635.664 | 678.0416 | 656.8528 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42936 | 0.39417 | 0.42347 | 0.39025 | 0.43176 | 0.40086 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52171 | 0.46953 | 0.52065 | 0.47798 | 0.50971 | 0.47834 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.42911 | 0.40506 | 0.40433 | 0.38792 | 0.42509 | 0.41789 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.45308 | 0.40999 | 0.42907 | 0.39368 | 0.42378 | 0.39533 |  |  |  |  | 2015-03-31
NY_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.47829 | 0.4422 | 0.47148 | 0.44458 | 0.47956 | 0.46264 |  |  |  |  | 2015-03-31
NY_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10276.568 | 9704.4704 | 9979.9248 | 9640.904 | 10340.1344 | 9958.736 |  |  |  |  | 2015-03-31
NY_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24515.4416 | 24134.0432 | 24197.6096 | 23879.7776 | 25235.8608 | 24918.0288 |  |  |  |  | 2015-03-31
NY_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 199047.5875 | 195148.8483 | 195360.7363 | 191631.5075 | 203497.2355 | 199895.1395 |  |  |  |  | 2015-03-31
NY_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22905.0928 | 21167.6112 | 22883.904 | 21146.4224 | 23519.568 | 21782.0864 |  |  |  |  | 2015-03-31
NY_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NY_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NY_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NY_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
NY_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
NY_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
NY_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
NY_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
NY_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
NY_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
NY_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
NY_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
NY_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NY_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NY_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NY_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NY_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NY_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NY_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 381.5146 | 375.7593 | 368.0468 | 362.8121 | 339.1445 | 334.1798 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 381.5146 | 375.7593 | 368.0468 | 362.8121 | 339.1445 | 334.1798 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
NY_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 362.1079 | 356.6565 | 349.3262 | 344.3644 | 321.8972 | 317.1867 |  |  |  |  | 2015-03-31
NY_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 362.1079 | 356.6565 | 349.3262 | 344.3644 | 321.8972 | 317.1867 |  |  |  |  | 2015-03-31
NY_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.6466 | 4.5347 | 5.2545 | 5.1309 | 5.0804 | 4.9463 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1796.4756 | 884.7127 | 1733.0743 | 854.2294 | 1597.0786 | 786.8148 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 884.7127 | 0 | 854.2294 | 0 | 786.8148 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1796.4756 | 1769.3716 | 1733.0743 | 1708.5063 | 1597.0786 | 1573.6312 |  |  |  |  | 2015-03-31
NY_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 934.3718 | 911.8707 | 1056.6 | 1031.7546 | 1021.5866 | 994.63 |  |  |  |  | 2015-03-31
NY_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2096.0467 | 2056.5794 | 2022.1842 | 1985.7285 | 1863.364 | 1829.1273 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
NY_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0382 | 10.4086 | 10.7192 | 10.3434 | 11.1041 | 10.6785 |  |  |  |  | 2015-03-31
NY_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.2525 | 32.8242 | 34.799 | 34.3428 | 36.2784 | 35.821 |  |  |  |  | 2015-03-31
NY_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 279.927 | 274.449 | 274.7336 | 269.4914 | 286.1676 | 281.0993 |  |  |  |  | 2015-03-31
NY_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.9193 | 30.4277 | 32.8936 | 30.415 | 33.8184 | 31.3189 |  |  |  |  | 2015-03-31
NY_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.6664 | 42.4788 | 42.9031 | 42.8287 | 44.9747 | 44.8818 |  |  |  |  | 2015-03-31
NY_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.77923 | 0.76654 | 0.79434 | 0.78097 | 0.83947 | 0.82438 |  |  |  |  | 2015-03-31
NY_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.8279 | 9.6304 | 9.9703 | 9.8313 | 10.5554 | 10.3163 |  |  |  |  | 2015-03-31
NY_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.66916 | 0.64861 | 0.68365 | 0.66175 | 0.72154 | 0.69815 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.6916 | 4.7727 | 9.3495 | 4.6083 | 8.6153 | 4.2446 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.7727 | 0 | 4.6083 | 0 | 4.2446 |  |  |  |  | 2015-03-31
NY_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 29.0749 | 28.6363 | 28.0485 | 27.6496 | 25.8459 | 25.4676 |  |  |  |  | 2015-03-31
NY_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.197 | 19.7106 | 22.839 | 22.302 | 22.0822 | 21.4995 |  |  |  |  | 2015-03-31
NY_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.8231 | 38.0919 | 37.4526 | 36.7794 | 34.5115 | 33.8768 |  |  |  |  | 2015-03-31
NY_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.827 | 3.7976 | 3.8297 | 3.8068 | 3.8658 | 3.8405 |  |  |  |  | 2015-03-31
NY_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 558.9246 | 539.0675 | 578.3419 | 554.265 | 571.9776 | 548.2349 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.9788 | 8.8347 | 8.538 | 8.4294 | 8.1302 | 8.0859 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 38.4585 | 36.5763 | 36.2904 | 34.986 | 33.9443 | 33.4114 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2284 | 5.991 | 6.1535 | 5.9231 | 5.728 | 5.5398 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4223 | 5.1082 | 5.3245 | 5.0281 | 4.9091 | 4.6418 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3326.6416 | 3241.8864 | 3135.9424 | 3093.5648 | 3178.32 | 3157.1312 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12776.8464 | 11611.4624 | 12543.7696 | 11484.3296 | 12734.4688 | 11992.8608 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2500.2784 | 2373.1456 | 2521.4672 | 2394.3344 | 2563.8448 | 2457.9008 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2076.5024 | 1928.1808 | 2076.5024 | 1928.1808 | 2097.6912 | 1949.3696 |  |  |  |  | 2015-03-31
NY_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
NY_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NY_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.0532 | 2.0527 | 3.936 | 2.6643 | 3.8834 | 2.6218 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.247 | 2.1944 | 2.1279 | 2.098 | 2.1581 | 2.1429 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.7097 | 12.459 | 13.4561 | 12.3228 | 13.662 | 12.871 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7533 | 1.667 | 1.7666 | 1.6847 | 1.7898 | 1.7166 |  |  |  |  | 2015-03-31
NY_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.459 | 1.3479 | 1.462 | 1.354 | 1.47 | 1.3694 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 24.8524 | 21.2132 | 25.0443 | 21.6182 | 25.3606 | 21.8478 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.3871 | 20.7599 | 24.6194 | 21.2258 | 24.9282 | 21.4954 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.2773 | 19.6262 | 22.4998 | 19.846 | 22.7881 | 20.1229 |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 30.684 | 26.1099 | 30.6519 | 26.2456 | 27.7719 | 25.2761 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | 11.1636 | 14.9958 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.2093 | 5.3019 | 6.0865 | 5.1619 | 6.2334 | 5.4389 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7458.4576 | 6356.64 | 7522.024 | 6483.7728 | 7606.7792 | 6547.3392 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7310.136 | 6229.5072 | 7394.8912 | 6377.8288 | 7479.6464 | 6441.3952 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6674.472 | 5890.4864 | 6759.2272 | 5954.0528 | 6843.9824 | 6038.808 |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9217.128 | 7839.856 | 9195.9392 | 7882.2336 | 9365.4496 | 8051.744 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1864.6144 | 1589.16 | 1822.2368 | 1546.7824 | 1906.992 | 1631.5376 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
NY_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | n/a | VFD |  |  |  |  | 2015-03-31
NY_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
NY_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
NY_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NY_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7457.8008 | 6365.7088 | 7515.3707 | 6487.269 | 7610.3177 | 6556.1538 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7318.1666 | 6229.6979 | 7387.8777 | 6369.5016 | 7480.5363 | 6450.4216 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6685.0452 | 5889.5117 | 6751.8323 | 5955.4513 | 6777.6191 | 6038.5326 |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NY_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NY_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NY_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
NY_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
NY_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
NY_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4428 | 1.338 | 1.602 | 1.466 | 1.5374 | 1.4056 |  |  |  |  | 2015-03-31
NY_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 145.062 | 134.5242 | 161.071 | 147.3971 | 154.5774 | 141.3237 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.9191 | 9.3914 | 11.0034 | 9.5707 | 11.1424 | 9.6723 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.7147 | 9.1907 | 10.8168 | 9.3969 | 10.9524 | 9.5163 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.8625 | 8.6888 | 9.8855 | 8.7861 | 10.0122 | 8.9087 |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.4813 | 11.4716 | 13.4672 | 11.5312 | 13.7211 | 11.8037 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | 2.2687 | 3.0475 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3056 | 1.1148 | 1.2798 | 1.0854 | 1.3404 | 1.1436 |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
NY_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.1356 | 2.9078 | 3.4816 | 3.1861 | 3.3413 | 3.0548 |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
NY_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.5649 | 98.053 | 104.1182 | 98.1333 | 100.3897 | 94.3961 |  |  |  |  | 2015-03-31
NY_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9739 | 1.838 | 1.9202 | 1.7727 | 1.7774 | 1.6452 |  |  |  |  | 2015-03-31
NY_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2282 | 5.0441 | 5.1695 | 4.9592 | 4.9297 | 4.7986 |  |  |  |  | 2015-03-31
NY_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5054 | 2.3585 | 2.4829 | 2.3304 | 2.5517 | 2.3978 |  |  |  |  | 2015-03-31
NY_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.1591 | 4.1216 | 4.1021 | 4.0616 | 3.9118 | 3.8782 |  |  |  |  | 2015-03-31
NY_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 593.2864 | 656.8528 | 614.4752 |  |  |  |  | 2015-03-31
NY_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1567.9712 | 1504.4048 | 1546.7824 | 1483.216 | 1589.16 | 1546.7824 |  |  |  |  | 2015-03-31
NY_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 741.608 | 699.2304 | 741.608 | 699.2304 | 762.7968 | 720.4192 |  |  |  |  | 2015-03-31
NY_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1483.216 | 1462.0272 | 1483.216 | 1462.0272 | 1546.7824 | 1525.5936 |  |  |  |  | 2015-03-31
NY_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
NY_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
NY_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
NY_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
NY_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
NY_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
NY_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
NY_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.0993 | 1.0606 | 1.087 | 1.055 | 1.1179 | 1.0774 |  |  |  |  | 2015-03-31
NY_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0497 | 1.0375 | 1.0554 | 1.0419 | 1.0803 | 1.0683 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.58528 | 0.58017 | 0.53384 | 0.52597 | 0.47489 | 0.46975 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.58095 | 0.57611 | 0.52929 | 0.52171 | 0.47034 | 0.46266 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.7221 | 0.72481 | 0.63408 | 0.62731 | 0.58502 | 0.57934 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.88005 | 0.87563 | 0.82982 | 0.81615 | 0.76818 | 0.75084 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.65932 | 0.65538 | 0.63604 | 0.62571 | 0.56172 | 0.55082 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.6721 | 0.66908 | 0.64945 | 0.63975 | 0.57573 | 0.56414 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.92704 | 0.92042 | 0.88366 | 0.86381 | 0.81069 | 0.7852 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5545 | 1.5323 | 1.4458 | 1.4154 | 1.338 | 1.3123 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5473 | 1.5257 | 1.4381 | 1.4081 | 1.3302 | 1.305 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.9525 | 1.9339 | 1.7555 | 1.7262 | 1.6707 | 1.6335 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3016 | 2.2702 | 2.1923 | 2.139 | 2.077 | 2.0142 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7534 | 1.7288 | 1.7142 | 1.6752 | 1.5727 | 1.5253 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7583 | 1.7336 | 1.7192 | 1.6799 | 1.5781 | 1.5308 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2511 | 2.2202 | 2.1669 | 2.1073 | 2.0114 | 1.9421 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4129 | 2.3791 | 2.3355 | 2.2643 | 2.1959 | 2.1109 |  |  |  |  | 2015-03-31
NY_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1116 | 2.117 | 2.0446 | 2.0351 | 2.102 | 2.0976 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0461 | 0.93562 | 0.99173 | 0.87179 | 0.90434 | 0.80035 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0468 | 0.92778 | 0.99221 | 0.86338 | 0.907 | 0.79181 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2724 | 1.1868 | 1.2152 | 1.0604 | 1.1194 | 0.99853 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4884 | 1.3904 | 1.4239 | 1.3152 | 1.3282 | 1.2276 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2516 | 1.1371 | 1.2256 | 1.1062 | 1.1353 | 1.0158 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2548 | 1.141 | 1.2289 | 1.1093 | 1.1376 | 1.0197 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5107 | 1.3968 | 1.4582 | 1.3303 | 1.3595 | 1.2309 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6013 | 1.4864 | 1.5622 | 1.4355 | 1.449 | 1.3161 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
NY_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 169.5104 | 169.5104 | 169.5104 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | 169.5104 | 169.5104 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 233.0768 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 317.832 | 317.832 | 296.6432 | 317.832 | 296.6432 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 211.888 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 339.0208 | 317.832 | 339.0208 | 317.832 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 550.9088 | 529.72 | 529.72 | 550.9088 | 529.72 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 508.5312 | 529.72 | 529.72 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 720.4192 | 678.0416 | 656.8528 | 699.2304 | 678.0416 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 868.7408 | 868.7408 | 847.552 | 889.9296 | 847.552 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 614.4752 | 635.664 | 614.4752 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 614.4752 | 635.664 | 614.4752 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | 826.3632 | 805.1744 | 826.3632 | 805.1744 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 932.3072 | 889.9296 | 953.496 | 911.1184 |  |  |  |  | 2015-03-31
NY_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 932.3072 | 911.1184 | 911.1184 | 953.496 | 953.496 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 381.3984 | 339.0208 | 360.2096 | 339.0208 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 381.3984 | 317.832 | 360.2096 | 317.832 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 466.1536 | 402.5872 | 466.1536 | 423.776 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 572.0976 | 529.72 | 572.0976 | 529.72 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 487.3424 | 423.776 | 487.3424 | 423.776 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 487.3424 | 423.776 | 487.3424 | 423.776 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 572.0976 | 529.72 | 593.2864 | 529.72 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 635.664 | 572.0976 | 635.664 | 572.0976 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.13619 | 0.13453 | 0.12887 | 0.12631 | 0.1264 | 0.12363 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.1348 | 0.13323 | 0.12737 | 0.12492 | 0.12484 | 0.12215 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.17896 | 0.18051 | 0.15917 | 0.15863 | 0.16139 | 0.16067 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.22704 | 0.2256 | 0.22108 | 0.21651 | 0.2228 | 0.21667 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15392 | 0.15289 | 0.15168 | 0.14871 | 0.14659 | 0.14287 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15836 | 0.1574 | 0.15618 | 0.15343 | 0.15156 | 0.1479 |  |  |  |  | 2015-03-31
NY_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.23774 | 0.23558 | 0.23469 | 0.22805 | 0.23524 | 0.22623 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.39222 | 0.38494 | 0.37988 | 0.36984 | 0.38575 | 0.37452 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.38989 | 0.38277 | 0.37728 | 0.36741 | 0.383 | 0.37195 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.5153 | 0.51109 | 0.47652 | 0.46669 | 0.49524 | 0.48422 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.62254 | 0.61215 | 0.6136 | 0.5956 | 0.63008 | 0.60772 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.44323 | 0.43522 | 0.44486 | 0.43198 | 0.44527 | 0.4296 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.44486 | 0.43681 | 0.44655 | 0.43354 | 0.44716 | 0.43154 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.59414 | 0.58402 | 0.58572 | 0.56591 | 0.59139 | 0.56706 |  |  |  |  | 2015-03-31
NY_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.65526 | 0.64141 | 0.65548 | 0.63146 | 0.66942 | 0.6392 |  |  |  |  | 2015-03-31
NY_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65182 | 0.65373 | 0.6519 | 0.64884 | 0.67081 | 0.66941 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.2728 | 0.24366 | 0.26322 | 0.23393 | 0.26173 | 0.23406 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27306 | 0.2411 | 0.26336 | 0.23111 | 0.26197 | 0.23104 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.34647 | 0.31944 | 0.3299 | 0.29063 | 0.32961 | 0.29889 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.41275 | 0.38112 | 0.40711 | 0.37268 | 0.41235 | 0.37736 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34086 | 0.30353 | 0.34188 | 0.30196 | 0.34234 | 0.30072 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34191 | 0.30483 | 0.34299 | 0.303 | 0.34373 | 0.30212 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.41739 | 0.37986 | 0.41254 | 0.36979 | 0.41544 | 0.37007 |  |  |  |  | 2015-03-31
NY_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.44702 | 0.4098 | 0.44777 | 0.40526 | 0.4483 | 0.40307 |  |  |  |  | 2015-03-31
OH_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7274 | 1.6219 | 1.6763 | 1.5764 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8458 | 1.7105 | 1.7883 | 1.6756 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.42 | 1.3411 | 1.3619 | 1.3086 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6916 | 1.5713 | 1.6156 | 1.5122 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5982 | 1.4828 | 1.5339 | 1.4438 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 572.0976 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 678.0416 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 614.4752 | 593.2864 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 635.664 | 593.2864 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 699.2304 | 656.8528 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44686 | 0.4097 | 0.43784 | 0.40275 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52376 | 0.47346 | 0.51168 | 0.46971 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.45316 | 0.42799 | 0.43461 | 0.41759 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.4726 | 0.42689 | 0.45154 | 0.41314 | [6 empty] | 2015-03-31
OH_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.51004 | 0.47209 | 0.4895 | 0.46076 | [6 empty] | 2015-03-31
OH_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10573.2112 | 9979.9248 | 10191.8128 | 9831.6032 | [6 empty] | 2015-03-31
OH_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24790.896 | 24388.3088 | 24663.7632 | 24345.9312 | [6 empty] | 2015-03-31
OH_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 199068.7763 | 195318.3587 | 198920.4547 | 195212.4147 | [6 empty] | 2015-03-31
OH_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23667.8896 | 21803.2752 | 23561.9456 | 21718.52 | [6 empty] | 2015-03-31
OH_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OH_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
OH_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
OH_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
OH_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
OH_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
OH_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
OH_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
OH_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
OH_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
OH_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
OH_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
OH_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OH_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OH_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OH_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
OH_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
OH_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
OH_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OH_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OH_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OH_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 388.936 | 383.553 | 379.7074 | 374.5133 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 388.936 | 383.553 | 379.7074 | 374.5133 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
OH_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 369.1603 | 364.0529 | 360.401 | 355.4656 | [6 empty] | 2015-03-31
OH_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 369.1603 | 364.0529 | 360.401 | 355.4656 | [6 empty] | 2015-03-31
OH_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.9978 | 4.8773 | 4.9566 | 4.8393 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1831.5048 | 903.0627 | 1788.075 | 881.7788 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 903.0627 | 0 | 881.7788 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1831.5048 | 1806.1443 | 1788.075 | 1763.507 | [6 empty] | 2015-03-31
OH_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1004.9913 | 980.7483 | 996.7032 | 973.1068 | [6 empty] | 2015-03-31
OH_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2136.9406 | 2099.2168 | 2086.2195 | 2049.7638 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OH_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.3581 | 10.7115 | 10.9272 | 10.5452 | [6 empty] | 2015-03-31
OH_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.6284 | 33.1811 | 35.4667 | 34.9864 | [6 empty] | 2015-03-31
OH_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 279.9538 | 274.6821 | 279.7522 | 274.5275 | [6 empty] | 2015-03-31
OH_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.0144 | 29.6669 | 33.8654 | 31.2277 | [6 empty] | 2015-03-31
OH_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 44.0085 | 43.8149 | 43.7506 | 43.6744 | [6 empty] | 2015-03-31
OH_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.81104 | 0.79698 | 0.81002 | 0.79649 | [6 empty] | 2015-03-31
OH_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.1744 | 9.9578 | 10.1755 | 9.9542 | [6 empty] | 2015-03-31
OH_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.69881 | 0.67641 | 0.69886 | 0.67625 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.8802 | 4.8717 | 9.6457 | 4.7569 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.8717 | 0 | 4.7569 | [6 empty] | 2015-03-31
OH_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 29.6405 | 29.2303 | 28.9372 | 28.5413 | [6 empty] | 2015-03-31
OH_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 21.7235 | 21.1995 | 21.5443 | 21.0343 | [6 empty] | 2015-03-31
OH_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.5783 | 38.882 | 38.6392 | 37.9656 | [6 empty] | 2015-03-31
OH_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8808 | 3.8499 | 3.8617 | 3.8383 | [6 empty] | 2015-03-31
OH_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
OH_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
OH_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OH_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
OH_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4779.3056 | 4630.5264 | 4719.4664 | 4573.1984 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.8804 | 8.859 | 8.72 | 8.6956 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 38.0159 | 37.3193 | 39.5887 | 35.2642 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3812 | 6.1327 | 6.2858 | 6.0459 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5583 | 5.2372 | 5.4649 | 5.1434 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3263.0752 | 3241.8864 | 3199.5088 | 3178.32 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12564.9584 | 11823.3504 | 12988.7344 | 11166.4976 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2521.4672 | 2394.3344 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2097.6912 | 1928.1808 | 2097.6912 | 1928.1808 | [6 empty] | 2015-03-31
OH_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
OH_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OH_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.6401 | 2.4346 | 3.6259 | 2.4241 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2048 | 2.1893 | 2.1713 | 2.1571 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.4778 | 12.681 | 13.9289 | 11.9859 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7702 | 1.6789 | 1.7714 | 1.683 | [6 empty] | 2015-03-31
OH_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4689 | 1.3525 | 1.4671 | 1.3529 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.9061 | 22.3082 | 25.7709 | 22.1366 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.4804 | 21.9178 | 25.3517 | 21.7814 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.1946 | 20.4486 | 23.0964 | 20.2825 | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.1995 | 27.519 | 31.9033 | 27.2246 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.6178 | 5.6532 | 6.5353 | 5.5531 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7776.2896 | 6695.6608 | 7733.912 | 6653.2832 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7649.1568 | 6568.528 | 7606.7792 | 6526.1504 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6949.9264 | 6144.752 | 6928.7376 | 6081.1856 | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9662.0928 | 8263.632 | 9577.3376 | 8178.8768 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1991.7472 | 1695.104 | 1970.5584 | 1673.9152 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
OH_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
OH_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
OH_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
OH_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OH_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
OH_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
OH_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
OH_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
OH_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7774.0012 | 6694.3259 | 7733.4247 | 6642.8371 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7646.2539 | 6577.173 | 7607.6268 | 6536.2363 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6136.2765 | 6777.6191 | 6086.4404 | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OH_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OH_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OH_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
OH_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OH_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OH_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5454 | 1.4145 | 1.5428 | 1.4088 | [6 empty] | 2015-03-31
OH_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 155.3764 | 142.2181 | 155.1132 | 141.6445 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.3821 | 9.8762 | 11.3227 | 9.8002 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.1951 | 9.7033 | 11.1385 | 9.6429 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.1908 | 9.0529 | 10.1476 | 8.9793 | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.1472 | 12.0907 | 14.017 | 11.9614 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3915 | 1.1887 | 1.3742 | 1.1677 | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
OH_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.3585 | 3.0741 | 3.3529 | 3.0617 | [6 empty] | 2015-03-31
OH_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OH_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OH_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OH_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OH_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OH_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.4346 | 96.5086 | 102.5672 | 96.3758 | [6 empty] | 2015-03-31
OH_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0265 | 1.9101 | 1.9876 | 1.861 | [6 empty] | 2015-03-31
OH_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3839 | 5.1808 | 5.3475 | 5.1192 | [6 empty] | 2015-03-31
OH_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5706 | 2.4215 | 2.5513 | 2.3977 | [6 empty] | 2015-03-31
OH_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.3111 | 4.2752 | 4.245 | 4.2051 | [6 empty] | 2015-03-31
OH_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
OH_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1610.3488 | 1546.7824 | 1610.3488 | 1525.5936 | [6 empty] | 2015-03-31
OH_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
OH_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1525.5936 | 1504.4048 | [6 empty] | 2015-03-31
OH_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
OH_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
OH_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
OH_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
OH_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OH_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OH_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OH_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OH_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OH_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1321 | 1.0894 | 1.1244 | 1.0764 | [6 empty] | 2015-03-31
OH_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0718 | 1.0601 | 1.067 | 1.0539 | [6 empty] | 2015-03-31
OH_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.60232 | 0.59821 | 0.57658 | 0.56805 | [6 empty] | 2015-03-31
OH_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.59757 | 0.59374 | 0.57185 | 0.56365 | [6 empty] | 2015-03-31
OH_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.75015 | 0.75419 | 0.71769 | 0.71001 | [6 empty] | 2015-03-31
OH_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.92629 | 0.92401 | 0.89551 | 0.8845 | [6 empty] | 2015-03-31
OH_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.66587 | 0.6622 | 0.64986 | 0.63894 | [6 empty] | 2015-03-31
OH_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.67843 | 0.67557 | 0.66303 | 0.65139 | [6 empty] | 2015-03-31
OH_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.96929 | 0.9633 | 0.93956 | 0.91808 | [6 empty] | 2015-03-31
OH_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5815 | 1.5615 | 1.5397 | 1.5075 | [6 empty] | 2015-03-31
OH_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5738 | 1.5543 | 1.5319 | 1.5003 | [6 empty] | 2015-03-31
OH_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0177 | 2.0047 | 1.9518 | 1.9193 | [6 empty] | 2015-03-31
OH_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3859 | 2.359 | 2.3353 | 2.2868 | [6 empty] | 2015-03-31
OH_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7604 | 1.7367 | 1.7432 | 1.7001 | [6 empty] | 2015-03-31
OH_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7657 | 1.7419 | 1.7483 | 1.7054 | [6 empty] | 2015-03-31
OH_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2713 | 2.2056 | 2.2453 | 2.1819 | [6 empty] | 2015-03-31
OH_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4915 | 2.4532 | 2.4471 | 2.3798 | [6 empty] | 2015-03-31
OH_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0668 | 2.0733 | 2.0376 | 2.0405 | [6 empty] | 2015-03-31
OH_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0601 | 0.97525 | 1.0617 | 0.93725 | [6 empty] | 2015-03-31
OH_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0895 | 0.96755 | 1.0638 | 0.93274 | [6 empty] | 2015-03-31
OH_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3209 | 1.2299 | 1.3132 | 1.1792 | [6 empty] | 2015-03-31
OH_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5513 | 1.4543 | 1.5162 | 1.405 | [6 empty] | 2015-03-31
OH_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2773 | 1.1562 | 1.2629 | 1.1334 | [6 empty] | 2015-03-31
OH_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2807 | 1.1599 | 1.2668 | 1.1372 | [6 empty] | 2015-03-31
OH_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5439 | 1.4219 | 1.525 | 1.3842 | [6 empty] | 2015-03-31
OH_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6375 | 1.5191 | 1.6154 | 1.4805 | [6 empty] | 2015-03-31
OH_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OH_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
OH_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OH_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OH_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OH_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OH_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OH_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OH_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OH_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OH_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
OH_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OH_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
OH_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
OH_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
OH_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 339.0208 | 339.0208 | [6 empty] | 2015-03-31
OH_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
OH_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
OH_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | 360.2096 | 339.0208 | [6 empty] | 2015-03-31
OH_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 572.0976 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
OH_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 572.0976 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
OH_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 741.608 | 741.608 | 720.4192 | [6 empty] | 2015-03-31
OH_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 932.3072 | 889.9296 | [6 empty] | 2015-03-31
OH_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | 614.4752 | 614.4752 | [6 empty] | 2015-03-31
OH_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
OH_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | 847.552 | 826.3632 | [6 empty] | 2015-03-31
OH_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 974.6848 | 953.496 | 974.6848 | 932.3072 | [6 empty] | 2015-03-31
OH_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | 911.1184 | 911.1184 | [6 empty] | 2015-03-31
OH_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
OH_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
OH_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 508.5312 | 466.1536 | [6 empty] | 2015-03-31
OH_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
OH_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
OH_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
OH_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 614.4752 | 529.72 | [6 empty] | 2015-03-31
OH_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
OH_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OH_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14318 | 0.1418 | 0.13921 | 0.13634 | [6 empty] | 2015-03-31
OH_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14161 | 0.14032 | 0.13764 | 0.13489 | [6 empty] | 2015-03-31
OH_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18572 | 0.18714 | 0.17995 | 0.17862 | [6 empty] | 2015-03-31
OH_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.24458 | 0.24381 | 0.23947 | 0.2344 | [6 empty] | 2015-03-31
OH_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15168 | 0.15052 | 0.15073 | 0.14722 | [6 empty] | 2015-03-31
OH_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15584 | 0.15483 | 0.15512 | 0.15175 | [6 empty] | 2015-03-31
OH_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.25614 | 0.25412 | 0.25156 | 0.24429 | [6 empty] | 2015-03-31
OH_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40806 | 0.40127 | 0.40414 | 0.39317 | [6 empty] | 2015-03-31
OH_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40546 | 0.39885 | 0.40152 | 0.39075 | [6 empty] | 2015-03-31
OH_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.53422 | 0.52988 | 0.52677 | 0.5158 | [6 empty] | 2015-03-31
OH_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.66048 | 0.65135 | 0.65513 | 0.63566 | [6 empty] | 2015-03-31
OH_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.43884 | 0.43102 | 0.44293 | 0.42856 | [6 empty] | 2015-03-31
OH_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.44061 | 0.43275 | 0.44462 | 0.43035 | [6 empty] | 2015-03-31
OH_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.59705 | 0.58765 | 0.59965 | 0.57853 | [6 empty] | 2015-03-31
OH_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.69414 | 0.68112 | 0.691 | 0.6656 | [6 empty] | 2015-03-31
OH_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64884 | 0.65121 | 0.64673 | 0.64785 | [6 empty] | 2015-03-31
OH_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.28752 | 0.25859 | 0.28349 | 0.25235 | [6 empty] | 2015-03-31
OH_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.28745 | 0.256 | 0.28337 | 0.24966 | [6 empty] | 2015-03-31
OH_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.36339 | 0.33402 | 0.35774 | 0.32447 | [6 empty] | 2015-03-31
OH_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.4444 | 0.41258 | 0.43901 | 0.40229 | [6 empty] | 2015-03-31
OH_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34849 | 0.30801 | 0.34919 | 0.30575 | [6 empty] | 2015-03-31
OH_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34963 | 0.30917 | 0.35045 | 0.30701 | [6 empty] | 2015-03-31
OH_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.42863 | 0.3878 | 0.42858 | 0.38223 | [6 empty] | 2015-03-31
OH_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46841 | 0.43067 | 0.46609 | 0.42162 | [6 empty] | 2015-03-31
PA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7644 | 1.6611 | 1.7307 | 1.6282 | 1.4279 | 1.3483 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.92 | 1.7652 | 1.8631 | 1.7432 | 1.5446 | 1.4547 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3816 | 1.3161 | 1.3429 | 1.2972 | 1.3253 | 1.3077 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7478 | 1.6225 | 1.6732 | 1.5646 | 1.3085 | 1.2378 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.593 | 1.4904 | 1.5414 | 1.4634 | 1.5191 | 1.4699 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 550.9088 | 614.4752 | 572.0976 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 678.0416 | 741.608 | 678.0416 | 699.2304 | 656.8528 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 593.2864 | 572.0976 | 593.2864 | 593.2864 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 635.664 | 572.0976 | 593.2864 | 550.9088 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 635.664 | 678.0416 | 635.664 | 678.0416 | 656.8528 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.43475 | 0.39843 | 0.43299 | 0.39788 | 0.43288 | 0.40296 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52886 | 0.47465 | 0.51902 | 0.47614 | 0.49291 | 0.46424 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.43113 | 0.40632 | 0.42469 | 0.40717 | 0.42293 | 0.41731 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.46988 | 0.42399 | 0.45297 | 0.41271 | 0.41346 | 0.38739 |  |  |  |  | 2015-03-31
PA_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.48863 | 0.45062 | 0.47927 | 0.44998 | 0.48477 | 0.46908 |  |  |  |  | 2015-03-31
PA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10276.568 | 9704.4704 | 10022.3024 | 9662.0928 | 10509.6448 | 10107.0576 |  |  |  |  | 2015-03-31
PA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24536.6304 | 24155.232 | 24642.5744 | 24303.5536 | 25172.2944 | 24875.6512 |  |  |  |  | 2015-03-31
PA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 199301.8531 | 195403.1139 | 200467.2371 | 196589.6867 | 200912.2019 | 197500.8051 |  |  |  |  | 2015-03-31
PA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23328.8688 | 21527.8208 | 23561.9456 | 21739.7088 | 23371.2464 | 21654.9536 |  |  |  |  | 2015-03-31
PA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
PA_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
PA_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
PA_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
PA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
PA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
PA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
PA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
PA_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
PA_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
PA_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
PA_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
PA_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
PA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
PA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
PA_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
PA_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
PA_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
PA_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 403.4395 | 397.7607 | 396.3566 | 390.9955 | 321.102 | 316.3057 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 403.4395 | 397.7607 | 396.3566 | 390.9955 | 321.102 | 316.3057 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
PA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 382.9211 | 377.5359 | 376.1995 | 371.1186 | 304.7756 | 300.2239 |  |  |  |  | 2015-03-31
PA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 382.9211 | 377.5359 | 376.1995 | 371.1186 | 304.7756 | 300.2239 |  |  |  |  | 2015-03-31
PA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.6069 | 4.4899 | 4.6064 | 4.5014 | 5.083 | 4.955 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1899.8197 | 936.5148 | 1866.3755 | 920.5868 | 1512.0479 | 744.7322 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 936.5148 | 0 | 920.5868 | 0 | 744.7322 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1899.8197 | 1873.0327 | 1866.3755 | 1841.1735 | 1512.0479 | 1489.4628 |  |  |  |  | 2015-03-31
PA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 926.3753 | 902.8582 | 926.277 | 905.1596 | 1022.1144 | 996.3751 |  |  |  |  | 2015-03-31
PA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2216.5092 | 2177.0419 | 2177.6759 | 2139.9521 | 1764.141 | 1731.1723 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
PA_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0383 | 10.409 | 10.7525 | 10.3755 | 11.2787 | 10.8477 |  |  |  |  | 2015-03-31
PA_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.2874 | 32.8533 | 35.4383 | 34.9461 | 36.1832 | 35.7522 |  |  |  |  | 2015-03-31
PA_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 280.2631 | 274.7792 | 281.9128 | 276.4574 | 282.5548 | 277.733 |  |  |  |  | 2015-03-31
PA_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.5431 | 29.2771 | 33.8773 | 31.2482 | 33.5991 | 31.1314 |  |  |  |  | 2015-03-31
PA_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.6534 | 42.4657 | 42.9523 | 42.8773 | 45.8239 | 45.7297 |  |  |  |  | 2015-03-31
PA_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.77821 | 0.76584 | 0.79005 | 0.77743 | 0.86076 | 0.84443 |  |  |  |  | 2015-03-31
PA_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.8151 | 9.6225 | 9.9118 | 9.7813 | 10.8336 | 10.5763 |  |  |  |  | 2015-03-31
PA_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.67003 | 0.64926 | 0.68198 | 0.66029 | 0.73896 | 0.71468 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.2486 | 5.0522 | 10.0687 | 4.9662 | 8.157 | 4.0176 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.0522 | 0 | 4.9662 | 0 | 4.0176 |  |  |  |  | 2015-03-31
PA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 30.7458 | 30.313 | 30.206 | 29.7974 | 24.4709 | 24.1054 |  |  |  |  | 2015-03-31
PA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.0241 | 19.5158 | 20.022 | 19.5656 | 22.0936 | 21.5372 |  |  |  |  | 2015-03-31
PA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 41.0542 | 40.3222 | 40.3335 | 39.6364 | 32.6755 | 32.0649 |  |  |  |  | 2015-03-31
PA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8428 | 3.8137 | 3.8444 | 3.8225 | 3.8822 | 3.8558 |  |  |  |  | 2015-03-31
PA_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4614.8288 | 4482.5621 | 4561.0415 | 4425.7301 | 4719.5478 | 4566.9631 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.1867 | 9.0508 | 9.0725 | 8.9435 | 7.5791 | 7.6098 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 39.6887 | 37.8243 | 39.1702 | 37.3106 | 31.8198 | 31.3157 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.567 | 6.3121 | 6.5202 | 6.2787 | 5.5816 | 5.3501 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.74 | 5.4128 | 5.6869 | 5.3729 | 4.639 | 4.3765 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3263.0752 | 3305.4528 | 3241.8864 | 2987.6208 | 3008.8096 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12776.8464 | 11632.6512 | 12819.224 | 11653.84 | 12437.8256 | 11802.1616 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2542.656 | 2436.712 | 2521.4672 | 2415.5232 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2097.6912 | 1949.3696 | 2118.88 | 1970.5584 | 2034.1248 | 1906.992 |  |  |  |  | 2015-03-31
PA_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
PA_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | No |  |  |  |  | 2015-03-31
PA_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
PA_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.062 | 2.06 | 3.1666 | 2.0716 | 4.0078 | 2.717 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2605 | 2.2112 | 2.2373 | 2.1937 | 2.0959 | 2.0337 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.7011 | 12.4733 | 13.7528 | 12.5167 | 13.3437 | 12.6634 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7712 | 1.6802 | 1.7887 | 1.7015 | 1.7606 | 1.6876 |  |  |  |  | 2015-03-31
PA_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4772 | 1.3618 | 1.4891 | 1.3771 | 1.4323 | 1.3319 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.5182 | 21.7249 | 25.8192 | 21.8875 | 25.0717 | 21.5937 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.0472 | 21.2823 | 25.3605 | 21.456 | 24.6636 | 21.3429 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.8551 | 20.0888 | 23.1387 | 20.23 | 22.536 | 20.084 |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.4952 | 26.7486 | 31.7922 | 26.8675 | 26.2269 | 23.8796 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | 11.1636 | 14.9958 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.3332 | 5.3873 | 6.4193 | 5.4424 | 5.8781 | 5.3507 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7649.1568 | 6526.1504 | 7755.1008 | 6568.528 | 7522.024 | 6483.7728 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7522.024 | 6377.8288 | 7606.7792 | 6441.3952 | 7394.8912 | 6399.0176 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6865.1712 | 6038.808 | 6949.9264 | 6081.1856 | 6759.2272 | 6017.6192 |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9450.2048 | 8030.5552 | 9534.96 | 8072.9328 | 9323.072 | 8051.744 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1906.992 | 1610.3488 | 1928.1808 | 1631.5376 | 1906.992 | 1631.5376 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
PA_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | VFD | n/a | n/a |  |  |  |  | 2015-03-31
PA_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
PA_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
PA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
PA_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7657.6111 | 6519.2852 | 7747.9178 | 6568.083 | 7523.592 | 6479.9164 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7516.2395 | 6386.4738 | 7610.2754 | 6438.5983 | 7401.1631 | 6404.675 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6028.2984 | 6777.6191 | 6070.6972 | 6762.7022 | 6026.8787 |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
PA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
PA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
PA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
PA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
PA_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
PA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4591 | 1.3471 | 1.4762 | 1.3525 | 1.5234 | 1.3935 |  |  |  |  | 2015-03-31
PA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 146.7033 | 135.4366 | 148.4197 | 135.9806 | 153.166 | 140.1024 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.2117 | 9.6179 | 11.3439 | 9.6899 | 11.0155 | 9.5598 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.0047 | 9.422 | 11.1424 | 9.4989 | 10.8362 | 9.4488 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.0416 | 8.8936 | 10.1662 | 8.9561 | 9.9014 | 8.8915 |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.8377 | 11.7523 | 13.9682 | 11.8045 | 13.6403 | 11.7935 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | 2.2687 | 3.0475 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3317 | 1.1328 | 1.3498 | 1.1444 | 1.3414 | 1.1477 |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
PA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.1711 | 2.9275 | 3.2082 | 2.9393 | 3.3108 | 3.0284 |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
PA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.8761 | 97.9051 | 102.706 | 97.0175 | 98.6319 | 92.6698 |  |  |  |  | 2015-03-31
PA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0926 | 1.9528 | 2.0632 | 1.9129 | 1.6908 | 1.581 |  |  |  |  | 2015-03-31
PA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2988 | 5.1155 | 5.2861 | 5.0739 | 4.7013 | 4.5708 |  |  |  |  | 2015-03-31
PA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5303 | 2.384 | 2.5279 | 2.3727 | 2.4653 | 2.3552 |  |  |  |  | 2015-03-31
PA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.3662 | 4.3283 | 4.3357 | 4.2945 | 3.8039 | 3.7743 |  |  |  |  | 2015-03-31
PA_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 678.0416 | 614.4752 | 656.8528 | 614.4752 |  |  |  |  | 2015-03-31
PA_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1589.16 | 1525.5936 | 1589.16 | 1525.5936 | 1589.16 | 1525.5936 |  |  |  |  | 2015-03-31
PA_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 720.4192 | 762.7968 | 720.4192 |  |  |  |  | 2015-03-31
PA_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1483.216 | 1483.216 | 1504.4048 | 1483.216 | 1567.9712 | 1546.7824 |  |  |  |  | 2015-03-31
PA_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
PA_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
PA_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
PA_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
PA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
PA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
PA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
PA_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1142 | 1.0756 | 1.1115 | 1.0669 | 1.117 | 1.0753 |  |  |  |  | 2015-03-31
PA_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.057 | 1.0449 | 1.0551 | 1.0541 | 1.092 | 1.0813 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.63082 | 0.62503 | 0.60635 | 0.59428 | 0.42649 | 0.42101 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.62323 | 0.62091 | 0.60188 | 0.59014 | 0.42173 | 0.41661 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.7695 | 0.77236 | 0.74463 | 0.73752 | 0.51974 | 0.52019 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.94392 | 0.93846 | 0.92419 | 0.90447 | 0.7141 | 0.70118 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.70646 | 0.70185 | 0.69263 | 0.68127 | 0.51207 | 0.50457 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.71973 | 0.71414 | 0.7046 | 0.69499 | 0.52608 | 0.51851 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.9894 | 0.98642 | 0.97604 | 0.9531 | 0.75643 | 0.73579 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6513 | 1.6274 | 1.6065 | 1.5654 | 1.2267 | 1.2007 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6441 | 1.6207 | 1.5991 | 1.5585 | 1.2186 | 1.1932 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.0628 | 2.0391 | 2.0192 | 1.9702 | 1.523 | 1.4945 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4409 | 2.407 | 2.4064 | 2.3381 | 1.9397 | 1.8944 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8595 | 1.8293 | 1.8427 | 1.8018 | 1.4588 | 1.4198 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8611 | 1.8343 | 1.8478 | 1.8066 | 1.4643 | 1.4254 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3854 | 2.3508 | 2.3606 | 2.2945 | 1.8624 | 1.8048 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5554 | 2.5104 | 2.532 | 2.4617 | 2.0678 | 1.9947 |  |  |  |  | 2015-03-31
PA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1597 | 2.1646 | 2.1267 | 2.1279 | 2.0566 | 2.0723 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1344 | 1.0049 | 1.1062 | 0.97241 | 0.83378 | 0.7364 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1347 | 0.99702 | 1.109 | 0.9644 | 0.83528 | 0.72779 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4012 | 1.2605 | 1.3674 | 1.2178 | 1.0311 | 0.91152 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5919 | 1.4801 | 1.5679 | 1.4409 | 1.2643 | 1.164 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3309 | 1.2087 | 1.3277 | 1.1965 | 1.0598 | 0.95031 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3343 | 1.2121 | 1.3309 | 1.1983 | 1.0633 | 0.95434 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6075 | 1.4833 | 1.5956 | 1.4544 | 1.2676 | 1.149 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7045 | 1.5827 | 1.6913 | 1.5521 | 1.3695 | 1.241 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
PA_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 190.6992 | 169.5104 | 169.5104 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 190.6992 | 169.5104 | 169.5104 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 254.2656 | 254.2656 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 339.0208 | 317.832 | 296.6432 | 296.6432 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | 190.6992 | 190.6992 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 233.0768 | 190.6992 | 190.6992 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 360.2096 | 339.0208 | 317.832 | 317.832 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 550.9088 | 529.72 | 508.5312 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 572.0976 | 550.9088 | 529.72 | 508.5312 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 741.608 | 741.608 | 720.4192 | 656.8528 | 656.8528 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | 911.1184 | 889.9296 | 868.7408 | 847.552 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 635.664 | 593.2864 | 593.2864 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | 656.8528 | 635.664 | 614.4752 | 593.2864 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 847.552 | 868.7408 | 847.552 | 805.1744 | 762.7968 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | 974.6848 | 932.3072 | 932.3072 | 889.9296 |  |  |  |  | 2015-03-31
PA_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 932.3072 | 932.3072 | 932.3072 | 932.3072 | 932.3072 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | 360.2096 | 317.832 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | 360.2096 | 317.832 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 508.5312 | 466.1536 | 444.9648 | 402.5872 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 614.4752 | 550.9088 | 572.0976 | 529.72 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 508.5312 | 444.9648 | 466.1536 | 402.5872 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 508.5312 | 444.9648 | 466.1536 | 402.5872 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 614.4752 | 550.9088 | 572.0976 | 508.5312 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 656.8528 | 593.2864 | 614.4752 | 550.9088 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14205 | 0.1402 | 0.13967 | 0.13575 | 0.11951 | 0.11754 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14067 | 0.1389 | 0.13823 | 0.13441 | 0.11784 | 0.116 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18432 | 0.1853 | 0.18188 | 0.17962 | 0.14837 | 0.14887 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23692 | 0.23516 | 0.23693 | 0.23044 | 0.2162 | 0.21152 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15736 | 0.15592 | 0.15715 | 0.15392 | 0.13745 | 0.13488 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16162 | 0.16023 | 0.16143 | 0.15839 | 0.14259 | 0.13998 |  |  |  |  | 2015-03-31
PA_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24702 | 0.24428 | 0.24935 | 0.24183 | 0.22988 | 0.2224 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40433 | 0.39658 | 0.40362 | 0.39002 | 0.37097 | 0.36147 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.402 | 0.39441 | 0.40118 | 0.38778 | 0.36804 | 0.35878 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.52779 | 0.52293 | 0.52875 | 0.51542 | 0.46796 | 0.46027 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.64391 | 0.63283 | 0.64944 | 0.62674 | 0.61509 | 0.59594 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.45007 | 0.4414 | 0.4567 | 0.44348 | 0.42618 | 0.41332 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.45158 | 0.44303 | 0.45836 | 0.44503 | 0.42817 | 0.41535 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.60755 | 0.59642 | 0.61438 | 0.59413 | 0.56511 | 0.54441 |  |  |  |  | 2015-03-31
PA_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67511 | 0.66044 | 0.68729 | 0.6615 | 0.65782 | 0.63108 |  |  |  |  | 2015-03-31
PA_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65238 | 0.6541 | 0.65406 | 0.65451 | 0.65632 | 0.66131 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.2867 | 0.25512 | 0.28569 | 0.25147 | 0.25005 | 0.2247 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.28678 | 0.25257 | 0.28583 | 0.24884 | 0.24981 | 0.22159 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.363 | 0.32977 | 0.36165 | 0.32502 | 0.31346 | 0.2819 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.43206 | 0.39767 | 0.43484 | 0.39501 | 0.40349 | 0.37148 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.35077 | 0.31122 | 0.35734 | 0.31434 | 0.32999 | 0.29037 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.35188 | 0.31235 | 0.35837 | 0.31557 | 0.33126 | 0.29183 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.43119 | 0.39099 | 0.43715 | 0.39161 | 0.39944 | 0.3566 |  |  |  |  | 2015-03-31
PA_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46411 | 0.42447 | 0.47091 | 0.42501 | 0.43705 | 0.39521 |  |  |  |  | 2015-03-31
VA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8119 | 1.7055 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9211 | 1.7578 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3948 | 1.3293 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.8115 | 1.6778 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6173 | 1.5156 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 635.664 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.43996 | 0.40274 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.5164 | 0.45816 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.4306 | 0.40578 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.48167 | 0.4339 | [8 empty] | 2015-03-31
VA_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.49234 | 0.45339 | [8 empty] | 2015-03-31
VA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10340.1344 | 9746.848 | [8 empty] | 2015-03-31
VA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24579.008 | 24197.6096 | [8 empty] | 2015-03-31
VA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 199195.9091 | 195339.5475 | [8 empty] | 2015-03-31
VA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23540.7568 | 21697.3312 | [8 empty] | 2015-03-31
VA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
VA_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
VA_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
VA_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
VA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
VA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
VA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
VA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
VA_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
VA_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
VA_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
VA_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
VA_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | [8 empty] | 2015-03-31
VA_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
VA_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
VA_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
VA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
VA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
VA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
VA_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
VA_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
VA_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
VA_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 411.664 | 406.1907 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 411.664 | 406.1907 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
VA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 390.7277 | 385.5409 | [8 empty] | 2015-03-31
VA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 390.7277 | 385.5409 | [8 empty] | 2015-03-31
VA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.3026 | 4.212 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1938.4945 | 956.3625 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 956.3625 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1938.4945 | 1912.6585 | [8 empty] | 2015-03-31
VA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 865.1978 | 846.9779 | [8 empty] | 2015-03-31
VA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2261.6826 | 2223.1663 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
VA_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0936 | 10.4618 | [8 empty] | 2015-03-31
VA_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.3454 | 32.9085 | [8 empty] | 2015-03-31
VA_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 280.1231 | 274.7022 | [8 empty] | 2015-03-31
VA_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.8565 | 29.5029 | [8 empty] | 2015-03-31
VA_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.8967 | 42.7081 | [8 empty] | 2015-03-31
VA_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.77982 | 0.76798 | [8 empty] | 2015-03-31
VA_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.8273 | 9.6427 | [8 empty] | 2015-03-31
VA_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.67252 | 0.65166 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.4575 | 5.1592 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.1592 | [8 empty] | 2015-03-31
VA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 31.3726 | 30.9555 | [8 empty] | 2015-03-31
VA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 18.7017 | 18.3079 | [8 empty] | 2015-03-31
VA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 41.8911 | 41.1768 | [8 empty] | 2015-03-31
VA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8532 | 3.8247 | [8 empty] | 2015-03-31
VA_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | [8 empty] | 2015-03-31
VA_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
VA_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VA_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | [8 empty] | 2015-03-31
VA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4394.787 | 4284.1323 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.2413 | 9.12 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 40.0405 | 38.2495 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.6167 | 6.3504 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.7878 | 5.4388 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3284.264 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12713.28 | 11611.4624 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2500.2784 | 2351.9568 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2076.5024 | 1906.992 | [8 empty] | 2015-03-31
VA_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
VA_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
VA_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.8076 | 1.8567 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2626 | 2.2194 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.6477 | 12.4613 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7452 | 1.6509 | [8 empty] | 2015-03-31
VA_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4499 | 1.331 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.7008 | 21.8053 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.2233 | 21.356 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.9727 | 20.1216 | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.9483 | 27.0653 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.4564 | 5.4749 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7712.7232 | 6547.3392 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7564.4016 | 6399.0176 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6886.36 | 6038.808 | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9577.3376 | 8115.3104 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1928.1808 | 1652.7264 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
VA_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
VA_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
VA_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
VA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
VA_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
VA_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
VA_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
VA_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
VA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7712.363 | 6543.4193 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7569.1055 | 6408.5738 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6038.1723 | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | [8 empty] | 2015-03-31
VA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VA_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4038 | 1.2978 | [8 empty] | 2015-03-31
VA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 141.1398 | 130.4799 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.2919 | 9.6535 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.0821 | 9.4546 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.0933 | 8.9081 | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.0368 | 11.8914 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3576 | 1.1512 | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
VA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.0508 | 2.8204 | [8 empty] | 2015-03-31
VA_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VA_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VA_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VA_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VA_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 101.6463 | 96.7687 | [8 empty] | 2015-03-31
VA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1212 | 1.9803 | [8 empty] | 2015-03-31
VA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3505 | 5.1678 | [8 empty] | 2015-03-31
VA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5517 | 2.3986 | [8 empty] | 2015-03-31
VA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.4566 | 4.4202 | [8 empty] | 2015-03-31
VA_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2015-03-31
VA_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1610.3488 | 1546.7824 | [8 empty] | 2015-03-31
VA_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | [8 empty] | 2015-03-31
VA_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | [8 empty] | 2015-03-31
VA_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
VA_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
VA_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
VA_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
VA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
VA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | [8 empty] | 2015-03-31
VA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
VA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
VA_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1251 | 1.0866 | [8 empty] | 2015-03-31
VA_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0502 | 1.0506 | [8 empty] | 2015-03-31
VA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.65046 | 0.6444 | [8 empty] | 2015-03-31
VA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.6461 | 0.64031 | [8 empty] | 2015-03-31
VA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.79176 | 0.79401 | [8 empty] | 2015-03-31
VA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.9704 | 0.96475 | [8 empty] | 2015-03-31
VA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.70576 | 0.70031 | [8 empty] | 2015-03-31
VA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.71737 | 0.71259 | [8 empty] | 2015-03-31
VA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0081 | 0.99928 | [8 empty] | 2015-03-31
VA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.691 | 1.6665 | [8 empty] | 2015-03-31
VA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6839 | 1.6599 | [8 empty] | 2015-03-31
VA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1111 | 2.0853 | [8 empty] | 2015-03-31
VA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4937 | 2.4596 | [8 empty] | 2015-03-31
VA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8495 | 1.8219 | [8 empty] | 2015-03-31
VA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8543 | 1.8266 | [8 empty] | 2015-03-31
VA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3848 | 2.3493 | [8 empty] | 2015-03-31
VA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5758 | 2.5399 | [8 empty] | 2015-03-31
VA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1617 | 2.1663 | [8 empty] | 2015-03-31
VA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1744 | 1.0382 | [8 empty] | 2015-03-31
VA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1769 | 1.0304 | [8 empty] | 2015-03-31
VA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4484 | 1.294 | [8 empty] | 2015-03-31
VA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6373 | 1.5205 | [8 empty] | 2015-03-31
VA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3401 | 1.2122 | [8 empty] | 2015-03-31
VA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3432 | 1.2153 | [8 empty] | 2015-03-31
VA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6203 | 1.488 | [8 empty] | 2015-03-31
VA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7196 | 1.597 | [8 empty] | 2015-03-31
VA_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VA_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
VA_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VA_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VA_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VA_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VA_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VA_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VA_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VA_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VA_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
VA_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VA_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
VA_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | [8 empty] | 2015-03-31
VA_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 275.4544 | [8 empty] | 2015-03-31
VA_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | [8 empty] | 2015-03-31
VA_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
VA_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
VA_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | [8 empty] | 2015-03-31
VA_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 572.0976 | [8 empty] | 2015-03-31
VA_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 572.0976 | [8 empty] | 2015-03-31
VA_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 741.608 | [8 empty] | 2015-03-31
VA_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | [8 empty] | 2015-03-31
VA_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | [8 empty] | 2015-03-31
VA_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | [8 empty] | 2015-03-31
VA_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | [8 empty] | 2015-03-31
VA_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | [8 empty] | 2015-03-31
VA_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | [8 empty] | 2015-03-31
VA_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | [8 empty] | 2015-03-31
VA_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | [8 empty] | 2015-03-31
VA_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | [8 empty] | 2015-03-31
VA_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 572.0976 | [8 empty] | 2015-03-31
VA_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
VA_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
VA_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | [8 empty] | 2015-03-31
VA_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
VA_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VA_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14529 | 0.14336 | [8 empty] | 2015-03-31
VA_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14392 | 0.14205 | [8 empty] | 2015-03-31
VA_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18729 | 0.18808 | [8 empty] | 2015-03-31
VA_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.24207 | 0.24024 | [8 empty] | 2015-03-31
VA_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15231 | 0.15064 | [8 empty] | 2015-03-31
VA_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15643 | 0.15494 | [8 empty] | 2015-03-31
VA_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.249 | 0.24614 | [8 empty] | 2015-03-31
VA_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.41116 | 0.40319 | [8 empty] | 2015-03-31
VA_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.40885 | 0.40105 | [8 empty] | 2015-03-31
VA_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.5342 | 0.52925 | [8 empty] | 2015-03-31
VA_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.6545 | 0.64334 | [8 empty] | 2015-03-31
VA_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.43721 | 0.42848 | [8 empty] | 2015-03-31
VA_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.43877 | 0.43001 | [8 empty] | 2015-03-31
VA_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.59641 | 0.58507 | [8 empty] | 2015-03-31
VA_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67672 | 0.6622 | [8 empty] | 2015-03-31
VA_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64942 | 0.65107 | [8 empty] | 2015-03-31
VA_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.29531 | 0.26257 | [8 empty] | 2015-03-31
VA_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29519 | 0.26006 | [8 empty] | 2015-03-31
VA_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.37305 | 0.3361 | [8 empty] | 2015-03-31
VA_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.44259 | 0.40707 | [8 empty] | 2015-03-31
VA_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34758 | 0.30645 | [8 empty] | 2015-03-31
VA_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34856 | 0.30746 | [8 empty] | 2015-03-31
VA_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.42921 | 0.38747 | [8 empty] | 2015-03-31
VA_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46653 | 0.42661 | [8 empty] | 2015-03-31
WV_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6933 | 1.5874 | 1.5445 | 1.4538 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7817 | 1.6488 | 1.5877 | 1.4907 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.397 | 1.3224 | 1.3351 | 1.2919 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6571 | 1.535 | 1.4559 | 1.3621 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5962 | 1.4781 | 1.5447 | 1.4604 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 572.0976 | 635.664 | 593.2864 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 593.2864 | 572.0976 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 699.2304 | 656.8528 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44994 | 0.41242 | 0.44879 | 0.41357 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.51584 | 0.46606 | 0.49218 | 0.45408 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.44581 | 0.42202 | 0.42604 | 0.41227 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.47449 | 0.42875 | 0.44588 | 0.40803 | [6 empty] | 2015-03-31
WV_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.5094 | 0.4717 | 0.49296 | 0.46605 | [6 empty] | 2015-03-31
WV_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10636.7776 | 10022.3024 | 10573.2112 | 10213.0016 | [6 empty] | 2015-03-31
WV_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24918.0288 | 24557.8192 | 25172.2944 | 24875.6512 | [6 empty] | 2015-03-31
WV_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 200382.4819 | 196801.5747 | 201187.6563 | 197861.0147 | [6 empty] | 2015-03-31
WV_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23752.6448 | 21930.408 | 23731.456 | 21951.5968 | [6 empty] | 2015-03-31
WV_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WV_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
WV_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
WV_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
WV_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
WV_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
WV_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
WV_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
WV_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
WV_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
WV_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
WV_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
WV_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WV_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WV_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WV_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
WV_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
WV_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
WV_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WV_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WV_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WV_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 376.6247 | 371.2817 | 341.0138 | 336.3892 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 376.6247 | 371.2817 | 341.0138 | 336.3892 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
WV_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 357.4768 | 352.3959 | 323.6702 | 319.2773 | [6 empty] | 2015-03-31
WV_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 357.4768 | 352.3959 | 323.6702 | 319.2773 | [6 empty] | 2015-03-31
WV_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.6202 | 4.5067 | 4.9012 | 4.7914 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1773.4927 | 874.1707 | 1605.7962 | 792.0169 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 874.1707 | 0 | 792.0169 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1773.4927 | 1748.2906 | 1605.7962 | 1584.0353 | [6 empty] | 2015-03-31
WV_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 929.0508 | 906.2343 | 985.5715 | 963.4857 | [6 empty] | 2015-03-31
WV_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2069.2597 | 2032.1699 | 1873.6667 | 1841.1735 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WV_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.4154 | 10.7658 | 11.3476 | 10.9528 | [6 empty] | 2015-03-31
WV_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.8322 | 33.3971 | 36.1815 | 35.7592 | [6 empty] | 2015-03-31
WV_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 281.7946 | 276.7704 | 282.93 | 278.2412 | [6 empty] | 2015-03-31
WV_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.1637 | 29.8239 | 34.1132 | 31.5713 | [6 empty] | 2015-03-31
WV_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 44.2418 | 44.0477 | 45.5924 | 45.514 | [6 empty] | 2015-03-31
WV_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.8113 | 0.79793 | 0.84 | 0.82665 | [6 empty] | 2015-03-31
WV_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.1671 | 9.9619 | 10.5349 | 10.3165 | [6 empty] | 2015-03-31
WV_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.69926 | 0.6774 | 0.72241 | 0.70007 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.5674 | 4.7159 | 8.6628 | 4.2727 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.7159 | 0 | 4.2727 | [6 empty] | 2015-03-31
WV_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 28.7023 | 28.2951 | 25.9884 | 25.6359 | [6 empty] | 2015-03-31
WV_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.082 | 19.5888 | 21.3037 | 20.8263 | [6 empty] | 2015-03-31
WV_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.3255 | 37.638 | 34.7017 | 34.1008 | [6 empty] | 2015-03-31
WV_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8716 | 3.8417 | 3.8765 | 3.8539 | [6 empty] | 2015-03-31
WV_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
WV_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
WV_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WV_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
WV_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4490.2688 | 4356.153 | 4579.9823 | 4432.5721 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.7439 | 8.7043 | 8.0426 | 7.9636 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 36.9827 | 36.0802 | 33.8595 | 33.015 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2015 | 5.9532 | 5.7094 | 5.4994 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.3792 | 5.0586 | 4.8897 | 4.5991 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3263.0752 | 3241.8864 | 3114.7536 | 3114.7536 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12713.28 | 11844.5392 | 12670.9024 | 11844.5392 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 2500.2784 | 2394.3344 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2076.5024 | 1906.992 | 2055.3136 | 1906.992 | [6 empty] | 2015-03-31
WV_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
WV_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WV_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.2988 | 2.1722 | 3.8275 | 2.5778 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2165 | 2.1969 | 2.1083 | 2.1088 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.6344 | 12.7092 | 13.5915 | 12.7032 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7626 | 1.6706 | 1.7593 | 1.6775 | [6 empty] | 2015-03-31
WV_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4591 | 1.3417 | 1.4379 | 1.329 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.9571 | 22.2213 | 25.6369 | 21.9936 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.5093 | 21.8076 | 25.1821 | 21.6081 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.2328 | 20.4709 | 22.9686 | 20.2261 | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.3549 | 27.5402 | 28.963 | 26.3007 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.6087 | 5.6408 | 6.4818 | 5.5574 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7797.4784 | 6674.472 | 7691.5344 | 6589.7168 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7649.1568 | 6547.3392 | 7564.4016 | 6483.7728 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6971.1152 | 6144.752 | 6886.36 | 6059.9968 | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9704.4704 | 8263.632 | 9598.5264 | 8200.0656 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1991.7472 | 1695.104 | 1949.3696 | 1673.9152 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
WV_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
WV_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
WV_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
WV_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WV_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
WV_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
WV_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
WV_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
WV_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7789.2995 | 6668.2637 | 7693.2295 | 6599.9086 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7654.899 | 6544.0973 | 7556.7313 | 6484.2178 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6142.9933 | 6777.6191 | 6069.5318 | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WV_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WV_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WV_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
WV_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WV_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WV_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4684 | 1.3472 | 1.5161 | 1.3798 | [6 empty] | 2015-03-31
WV_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 147.6375 | 135.4489 | 152.4359 | 138.7307 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.4045 | 9.8377 | 11.2638 | 9.7369 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.2077 | 9.6545 | 11.064 | 9.5662 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.2076 | 9.0628 | 10.0915 | 8.9544 | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.2155 | 12.1 | 14.0518 | 12.0036 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3896 | 1.1861 | 1.3724 | 1.1686 | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
WV_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.1913 | 2.9278 | 3.295 | 2.9988 | [6 empty] | 2015-03-31
WV_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WV_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WV_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WV_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WV_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WV_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 100.5073 | 94.9287 | 99.0549 | 92.7291 | [6 empty] | 2015-03-31
WV_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9428 | 1.8243 | 1.7953 | 1.6789 | [6 empty] | 2015-03-31
WV_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3386 | 5.1453 | 5.0571 | 4.8824 | [6 empty] | 2015-03-31
WV_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5633 | 2.4136 | 2.5919 | 2.432 | [6 empty] | 2015-03-31
WV_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.2313 | 4.1968 | 3.9972 | 3.9623 | [6 empty] | 2015-03-31
WV_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
WV_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1610.3488 | 1546.7824 | 1610.3488 | 1546.7824 | [6 empty] | 2015-03-31
WV_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 783.9856 | 720.4192 | [6 empty] | 2015-03-31
WV_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1525.5936 | 1567.9712 | 1546.7824 | [6 empty] | 2015-03-31
WV_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
WV_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
WV_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
WV_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
WV_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WV_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WV_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WV_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WV_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WV_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1226 | 1.0819 | 1.1313 | 1.0831 | [6 empty] | 2015-03-31
WV_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0749 | 1.0634 | 1.0991 | 1.0868 | [6 empty] | 2015-03-31
WV_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.568 | 0.56387 | 0.47932 | 0.47237 | [6 empty] | 2015-03-31
WV_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.56352 | 0.55964 | 0.47492 | 0.46827 | [6 empty] | 2015-03-31
WV_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.70096 | 0.70277 | 0.58385 | 0.58526 | [6 empty] | 2015-03-31
WV_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.87978 | 0.87874 | 0.77042 | 0.75991 | [6 empty] | 2015-03-31
WV_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.62742 | 0.62503 | 0.55058 | 0.54508 | [6 empty] | 2015-03-31
WV_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.63901 | 0.63724 | 0.56292 | 0.55887 | [6 empty] | 2015-03-31
WV_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.91472 | 0.91042 | 0.80966 | 0.7985 | [6 empty] | 2015-03-31
WV_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4994 | 1.4799 | 1.3217 | 1.2939 | [6 empty] | 2015-03-31
WV_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.492 | 1.473 | 1.3143 | 1.287 | [6 empty] | 2015-03-31
WV_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8842 | 1.8756 | 1.6434 | 1.6159 | [6 empty] | 2015-03-31
WV_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2718 | 2.2489 | 2.0458 | 2.0006 | [6 empty] | 2015-03-31
WV_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6659 | 1.645 | 1.5153 | 1.4892 | [6 empty] | 2015-03-31
WV_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.6705 | 1.6501 | 1.5205 | 1.4912 | [6 empty] | 2015-03-31
WV_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.1394 | 2.0686 | 1.9394 | 1.8946 | [6 empty] | 2015-03-31
WV_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.3596 | 2.3265 | 2.1505 | 2.0949 | [6 empty] | 2015-03-31
WV_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0377 | 2.0468 | 2.0798 | 2.086 | [6 empty] | 2015-03-31
WV_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0479 | 0.93125 | 0.92164 | 0.81219 | [6 empty] | 2015-03-31
WV_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0497 | 0.92339 | 0.92378 | 0.80427 | [6 empty] | 2015-03-31
WV_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2846 | 1.1565 | 1.133 | 0.9975 | [6 empty] | 2015-03-31
WV_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4833 | 1.3864 | 1.3332 | 1.2347 | [6 empty] | 2015-03-31
WV_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2264 | 1.1061 | 1.1157 | 1.0032 | [6 empty] | 2015-03-31
WV_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2299 | 1.1096 | 1.1191 | 1.0067 | [6 empty] | 2015-03-31
WV_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.471 | 1.3476 | 1.3353 | 1.2151 | [6 empty] | 2015-03-31
WV_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.571 | 1.4562 | 1.4324 | 1.3159 | [6 empty] | 2015-03-31
WV_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WV_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
WV_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WV_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WV_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WV_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WV_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WV_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WV_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WV_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WV_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
WV_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WV_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 190.6992 | 169.5104 | [6 empty] | 2015-03-31
WV_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | [6 empty] | 2015-03-31
WV_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
WV_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 317.832 | 317.832 | [6 empty] | 2015-03-31
WV_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
WV_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
WV_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
WV_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
WV_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 529.72 | 529.72 | [6 empty] | 2015-03-31
WV_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 720.4192 | 678.0416 | 678.0416 | [6 empty] | 2015-03-31
WV_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | 889.9296 | 868.7408 | [6 empty] | 2015-03-31
WV_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 593.2864 | 593.2864 | 593.2864 | [6 empty] | 2015-03-31
WV_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 593.2864 | 593.2864 | [6 empty] | 2015-03-31
WV_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 805.1744 | 805.1744 | 783.9856 | [6 empty] | 2015-03-31
WV_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | 932.3072 | 911.1184 | [6 empty] | 2015-03-31
WV_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | 932.3072 | 932.3072 | [6 empty] | 2015-03-31
WV_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 381.3984 | 339.0208 | [6 empty] | 2015-03-31
WV_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 381.3984 | 339.0208 | [6 empty] | 2015-03-31
WV_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 466.1536 | 466.1536 | 423.776 | [6 empty] | 2015-03-31
WV_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 593.2864 | 550.9088 | [6 empty] | 2015-03-31
WV_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 466.1536 | 423.776 | [6 empty] | 2015-03-31
WV_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 466.1536 | 423.776 | [6 empty] | 2015-03-31
WV_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
WV_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
WV_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WV_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14059 | 0.13918 | 0.12903 | 0.12658 | [6 empty] | 2015-03-31
WV_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.13908 | 0.13776 | 0.12748 | 0.12514 | [6 empty] | 2015-03-31
WV_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18011 | 0.18204 | 0.1612 | 0.16162 | [6 empty] | 2015-03-31
WV_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23941 | 0.23906 | 0.22551 | 0.22175 | [6 empty] | 2015-03-31
WV_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.14728 | 0.14651 | 0.14018 | 0.13872 | [6 empty] | 2015-03-31
WV_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.1516 | 0.15103 | 0.14499 | 0.14362 | [6 empty] | 2015-03-31
WV_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24865 | 0.24719 | 0.23729 | 0.23227 | [6 empty] | 2015-03-31
WV_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.40211 | 0.3954 | 0.38489 | 0.37491 | [6 empty] | 2015-03-31
WV_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.39956 | 0.39301 | 0.38223 | 0.37244 | [6 empty] | 2015-03-31
WV_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.52026 | 0.51734 | 0.48667 | 0.47991 | [6 empty] | 2015-03-31
WV_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.64859 | 0.6407 | 0.62675 | 0.61046 | [6 empty] | 2015-03-31
WV_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.42809 | 0.42103 | 0.42233 | 0.41317 | [6 empty] | 2015-03-31
WV_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.42965 | 0.42277 | 0.42417 | 0.41505 | [6 empty] | 2015-03-31
WV_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.58052 | 0.57217 | 0.56562 | 0.55125 | [6 empty] | 2015-03-31
WV_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67672 | 0.66535 | 0.66252 | 0.64247 | [6 empty] | 2015-03-31
WV_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65026 | 0.65317 | 0.66371 | 0.66568 | [6 empty] | 2015-03-31
WV_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.28599 | 0.25626 | 0.26887 | 0.23976 | [6 empty] | 2015-03-31
WV_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.28572 | 0.25359 | 0.26875 | 0.23695 | [6 empty] | 2015-03-31
WV_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.35854 | 0.32722 | 0.33652 | 0.30019 | [6 empty] | 2015-03-31
WV_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.43809 | 0.40597 | 0.41963 | 0.38532 | [6 empty] | 2015-03-31
WV_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.3445 | 0.30384 | 0.33585 | 0.29595 | [6 empty] | 2015-03-31
WV_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34568 | 0.30503 | 0.33704 | 0.29714 | [6 empty] | 2015-03-31
WV_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.42151 | 0.38061 | 0.40815 | 0.36637 | [6 empty] | 2015-03-31
WV_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46268 | 0.42472 | 0.44994 | 0.40943 | [6 empty] | 2015-03-31
CO_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6926 | 1.5492 | 1.6592 | 1.526 | 1.6092 | 1.4945 | 1.6212 | 1.4858 |  |  | 2015-03-31
CO_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8735 | 1.6781 | 1.82 | 1.6665 | 1.7257 | 1.6103 | 1.6203 | 1.4932 |  |  | 2015-03-31
CO_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.6647 | 1.575 | 1.6033 | 1.5389 | 1.5063 | 1.4878 | 1.5134 | 1.5994 |  |  | 2015-03-31
CO_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.763 | 1.601 | 1.6778 | 1.5395 | 1.568 | 1.4733 | 1.518 | 1.4012 |  |  | 2015-03-31
CO_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 2.0266 | 1.8735 | 1.9221 | 1.8091 | 1.8386 | 1.7722 | 1.8441 | 1.8719 |  |  | 2015-03-31
CO_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 741.608 | 678.0416 | 720.4192 | 678.0416 | 720.4192 | 678.0416 |  |  | 2015-03-31
CO_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 847.552 | 762.7968 | 826.3632 | 741.608 | 783.9856 | 720.4192 | 720.4192 | 678.0416 |  |  | 2015-03-31
CO_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 741.608 | 699.2304 | 720.4192 | 699.2304 | 678.0416 | 678.0416 | 678.0416 | 720.4192 |  |  | 2015-03-31
CO_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 762.7968 | 699.2304 | 699.2304 | 656.8528 | 678.0416 | 635.664 |  |  | 2015-03-31
CO_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 911.1184 | 847.552 | 868.7408 | 805.1744 | 826.3632 | 805.1744 | 826.3632 | 847.552 |  |  | 2015-03-31
CO_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  | 2015-03-31
CO_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2015-03-31
CO_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2015-03-31
CO_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  | 2015-03-31
CO_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  | 2015-03-31
CO_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.54015 | 0.49437 | 0.5295 | 0.48698 | 0.51352 | 0.47693 | 0.51737 | 0.47416 |  |  | 2015-03-31
CO_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.59789 | 0.53552 | 0.58082 | 0.53184 | 0.55072 | 0.51388 | 0.51707 | 0.47651 |  |  | 2015-03-31
CO_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.53126 | 0.50263 | 0.51167 | 0.4911 | 0.4807 | 0.47479 | 0.48294 | 0.51041 |  |  | 2015-03-31
CO_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.56263 | 0.51092 | 0.53544 | 0.4913 | 0.5004 | 0.47016 | 0.48442 | 0.44714 |  |  | 2015-03-31
CO_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.64675 | 0.59789 | 0.6134 | 0.57734 | 0.58675 | 0.56556 | 0.58851 | 0.59737 |  |  | 2015-03-31
CO_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 12713.28 | 11992.8608 | 12268.3152 | 11844.5392 | 12268.3152 | 11802.1616 | 12564.9584 | 12098.8048 |  |  | 2015-03-31
CO_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 29621.9424 | 29176.9776 | 29770.264 | 29388.8656 | 29240.544 | 28880.3344 | 30003.3408 | 30172.8512 |  |  | 2015-03-31
CO_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 237844.2804 | 233288.6884 | 239454.6292 | 234814.282 | 231614.7731 | 227906.7331 | 236339.8756 | 239136.7972 |  |  | 2015-03-31
CO_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 28202.2928 | 25977.4688 | 28265.8592 | 26062.224 | 27587.8176 | 25532.504 | 27566.6288 | 26083.4128 |  |  | 2015-03-31
CO_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2015-03-31
CO_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | 2015-03-31
CO_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | 2015-03-31
CO_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | Yes | Yes | No | Yes | No |  |  | 2015-03-31
CO_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  | 2015-03-31
CO_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  | 2015-03-31
CO_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  | 2015-03-31
CO_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  | 2015-03-31
CO_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  | 2015-03-31
CO_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  | 2015-03-31
CO_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  | 2015-03-31
CO_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  | 2015-03-31
CO_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
CO_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
CO_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
CO_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes | No | Yes |  |  | 2015-03-31
CO_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes | No | Yes |  |  | 2015-03-31
CO_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes | No | Yes |  |  | 2015-03-31
CO_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
CO_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
CO_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
CO_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
CO_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 283.9865 | 278.2834 | 271.4965 | 265.9867 | 253.2441 | 248.6027 | 230.9168 | 231.7179 |  |  | 2015-03-31
CO_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 283.9865 | 278.2834 | 271.4965 | 265.9867 | 253.2441 | 248.6027 | 230.9168 | 231.7179 |  |  | 2015-03-31
CO_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Screw | Screw | Screw | Screw | Screw | Screw |  |  | 2015-03-31
CO_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Screw | Screw | Screw | Screw | Screw | Screw |  |  | 2015-03-31
CO_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 269.5399 | 264.1282 | 257.6845 | 252.458 | 240.3644 | 235.9583 | 219.1806 | 219.9348 |  |  | 2015-03-31
CO_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 269.5399 | 264.1282 | 257.6845 | 252.458 | 240.3644 | 235.9583 | 219.1806 | 219.9348 |  |  | 2015-03-31
CO_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.5458 | 4.4157 | 4.5358 | 4.4176 | 4.7491 | 4.5887 | 4.903 | 4.7569 |  |  | 2015-03-31
CO_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 2015-03-31
CO_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1337.2743 | 655.2096 | 1278.4601 | 626.2574 | 1192.5102 | 585.3271 | 1087.3718 | 545.5729 |  |  | 2015-03-31
CO_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 655.2096 | 0 | 626.2574 | 0 | 585.3271 | 0 | 545.5729 |  |  | 2015-03-31
CO_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1337.2743 | 1310.4191 | 1278.4601 | 1252.5147 | 1192.5102 | 1170.6541 | 1087.3718 | 1091.1442 |  |  | 2015-03-31
CO_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 914.0897 | 887.9335 | 912.0783 | 888.325 | 954.9677 | 922.7186 | 985.9186 | 956.5448 |  |  | 2015-03-31
CO_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1582.417 | 1542.0082 | 1529.7971 | 1491.4599 | 1426.9507 | 1393.982 | 1301.1435 | 1299.3049 |  |  | 2015-03-31
CO_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes | yes | yes |  |  | 2015-03-31
CO_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 13.6445 | 12.8671 | 13.167 | 12.7029 | 13.1546 | 12.6606 | 13.4928 | 12.9857 |  |  | 2015-03-31
CO_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 42.4023 | 39.5151 | 42.6228 | 39.8048 | 41.8694 | 41.3374 | 42.9668 | 43.2093 |  |  | 2015-03-31
CO_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 334.4922 | 310.4302 | 336.7439 | 330.2204 | 325.7313 | 320.4985 | 332.3533 | 336.303 |  |  | 2015-03-31
CO_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 40.378 | 35.3312 | 40.4585 | 35.4666 | 39.4866 | 36.719 | 39.4589 | 37.5014 |  |  | 2015-03-31
CO_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 52.5659 | 52.3334 | 53.0831 | 52.9915 | 53.7478 | 53.6427 | 55.9877 | 55.8737 |  |  | 2015-03-31
CO_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.99653 | 0.97712 | 1.0054 | 0.98687 | 1.0215 | 1.002 | 1.0527 | 1.0603 |  |  | 2015-03-31
CO_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 12.5588 | 12.2587 | 12.676 | 12.3721 | 12.8718 | 12.562 | 13.4151 | 13.5621 |  |  | 2015-03-31
CO_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.86273 | 0.83271 | 0.86892 | 0.83949 | 0.87993 | 0.85036 | 0.91385 | 0.91329 |  |  | 2015-03-31
CO_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 7.2141 | 3.5346 | 6.8968 | 3.3784 | 6.4332 | 3.1576 | 5.866 | 2.9432 |  |  | 2015-03-31
CO_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 3.5346 | 0 | 3.3784 | 0 | 3.1576 | 0 | 2.9432 |  |  | 2015-03-31
CO_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.6424 | 21.2078 | 20.6905 | 20.2706 | 19.2995 | 18.9458 | 17.598 | 17.659 |  |  | 2015-03-31
CO_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 19.7586 | 19.1932 | 19.7151 | 19.2017 | 20.6422 | 19.9451 | 21.3112 | 20.6763 |  |  | 2015-03-31
CO_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 29.3087 | 28.5603 | 28.3341 | 27.624 | 26.4293 | 25.8186 | 24.0991 | 24.0651 |  |  | 2015-03-31
CO_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.1888 | 4.1519 | 4.1784 | 4.1503 | 4.1842 | 4.1552 | 4.0376 | 4.0398 |  |  | 2015-03-31
CO_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | NO | NO | YES | YES | YES | YES |  |  | 2015-03-31
CO_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | YES | YES | YES | YES |  |  | 2015-03-31
CO_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
CO_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | NO | YES | YES | YES | YES |  |  | 2015-03-31
CO_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4472.3877 | 4320.8539 | 4426.6484 | 4281.4615 | 4422.015 | 4258.3203 | 4411.0447 | 4283.8331 |  |  | 2015-03-31
CO_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.346 | 8.279 | 8.2473 | 8.2074 | 7.3429 | 7.4565 | 7.1066 | 7.4091 |  |  | 2015-03-31
CO_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 33.9262 | 31.2864 | 33.8948 | 31.2277 | 33.2437 | 29.8927 | 33.1587 | 30.3005 |  |  | 2015-03-31
CO_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.432 | 6.0987 | 6.5866 | 6.2673 | 6.3548 | 6.0667 | 6.234 | 6.0928 |  |  | 2015-03-31
CO_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.2632 | 4.8306 | 5.379 | 4.9567 | 5.1072 | 4.7204 | 4.9093 | 4.6625 |  |  | 2015-03-31
CO_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3750.4176 | 3729.2288 | 3708.04 | 3686.8512 | 3305.4528 | 3347.8304 | 3199.5088 | 3326.6416 |  |  | 2015-03-31
CO_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 15277.1248 | 14090.552 | 15255.936 | 14048.1744 | 14959.2928 | 13454.888 | 14916.9152 | 13645.5872 |  |  | 2015-03-31
CO_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2902.8656 | 2754.544 | 2966.432 | 2818.1104 | 2860.488 | 2733.3552 | 2796.9216 | 2733.3552 |  |  | 2015-03-31
CO_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2373.1456 | 2182.4464 | 2415.5232 | 2224.824 | 2309.5792 | 2118.88 | 2203.6352 | 2097.6912 |  |  | 2015-03-31
CO_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD |  |  | 2015-03-31
CO_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD | VFD | VFD |  |  | 2015-03-31
CO_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  | 2015-03-31
CO_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  | 2015-03-31
CO_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2015-03-31
CO_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  | 2015-03-31
CO_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | No | No | No | Yes |  |  | 2015-03-31
CO_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.7661 | 2.523 | 3.8868 | 2.6158 | 4.3651 | 2.9843 | 4.9217 | 3.4103 |  |  | 2015-03-31
CO_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.5444 | 2.524 | 2.5143 | 2.5021 | 2.2386 | 2.2732 | 2.1665 | 2.2587 |  |  | 2015-03-31
CO_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 16.284 | 15.0169 | 16.2689 | 14.9887 | 15.9564 | 14.4411 | 15.9156 | 14.6381 |  |  | 2015-03-31
CO_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 2.0289 | 1.9237 | 2.0776 | 1.9769 | 2.0045 | 1.9136 | 1.9664 | 1.9219 |  |  | 2015-03-31
CO_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.6602 | 1.5237 | 1.6967 | 1.5635 | 1.611 | 1.489 | 1.5485 | 1.4707 |  |  | 2015-03-31
CO_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 22.3183 | 20.2351 | 20.3608 | 17.7489 | 19.7128 | 16.9094 | 19.2159 | 16.3702 |  |  | 2015-03-31
CO_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 22.107 | 20.1736 | 20.0249 | 17.6151 | 19.4181 | 16.8188 | 18.9213 | 16.067 |  |  | 2015-03-31
CO_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 19.7339 | 18.2923 | 18.2518 | 16.0879 | 17.69 | 15.7456 | 17.2334 | 15.2841 |  |  | 2015-03-31
CO_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 25.5659 | 21.9241 | 25.357 | 21.6673 | 24.5449 | 21.1802 | 24.2319 | 20.4448 |  |  | 2015-03-31
CO_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.6766 | 7.5779 | 7.7348 | 7.6383 | 7.7466 | 7.6776 | 9.9964 | 9.9964 |  |  | 2015-03-31
CO_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.4989 | 4.8121 | 5.1718 | 4.3939 | 5.0117 | 4.2093 | 5.5503 | 4.3321 |  |  | 2015-03-31
CO_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 8.4441 | 8.4441 | 7.5494 | 7.5494 | 7.0043 | 7.0043 | 7.0043 | 7.0043 |  |  | 2015-03-31
CO_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 9195.9392 | 7903.4224 | 9174.7504 | 7861.0448 | 8878.1072 | 7606.7792 | 8645.0304 | 7373.7024 |  |  | 2015-03-31
CO_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 9047.6176 | 7861.0448 | 9005.24 | 7797.4784 | 8750.9744 | 7564.4016 | 8517.8976 | 7225.3808 |  |  | 2015-03-31
CO_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 8221.2544 | 7331.3248 | 8221.2544 | 7246.5696 | 7966.9888 | 7098.248 | 7755.1008 | 6886.36 |  |  | 2015-03-31
CO_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 11505.5184 | 9873.9808 | 11420.7632 | 9746.848 | 11039.3648 | 9534.96 | 10912.232 | 9195.9392 |  |  | 2015-03-31
CO_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3453.7744 | 3411.3968 | 3474.9632 | 3432.5856 | 3496.152 | 3453.7744 | 4492.0256 | 4492.0256 |  |  | 2015-03-31
CO_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2351.9568 | 1991.7472 | 2330.768 | 1970.5584 | 2246.0128 | 1885.8032 | 2500.2784 | 1949.3696 |  |  | 2015-03-31
CO_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  | 2015-03-31
CO_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a |  |  | 2015-03-31
CO_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD | VFD | VFD |  |  | 2015-03-31
CO_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD | n/a | VFD |  |  | 2015-03-31
CO_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |  |  | 2015-03-31
CO_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | Yes | Yes | No | No | No | No |  |  | 2015-03-31
CO_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | Yes | No | Yes | No | No | No | No |  |  | 2015-03-31
CO_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | Yes | No | Yes | No | No | No | No |  |  | 2015-03-31
CO_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | Yes | No | Yes | No | No | No | No |  |  | 2015-03-31
CO_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7852.8447 | 7852.8447 | 7852.8447 | 7852.8447 | 7611.9917 | 7852.8447 | 7369.274 |  |  | 2015-03-31
CO_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7852.8447 | 7852.8447 | 7799.8092 | 7852.8447 | 7571.182 | 7852.8447 | 7232.7757 |  |  | 2015-03-31
CO_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 |  |  | 2015-03-31
CO_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  | 2015-03-31
CO_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 1434.9903 | 1434.9903 | 2584.9912 | 2584.9912 |  |  | 2015-03-31
CO_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  | 2015-03-31
CO_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  | 2015-03-31
CO_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | No | DifferentialDryBulb | No | DifferentialDryBulb | No |  |  | 2015-03-31
CO_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  | 2015-03-31
CO_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  | 2015-03-31
CO_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  | 2015-03-31
CO_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | No | Yes | No | Yes | Yes | Yes | Yes |  |  | 2015-03-31
CO_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2015-03-31
CO_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No | Yes | Yes |  |  | 2015-03-31
CO_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | Yes | Yes | Yes | Yes |  |  | 2015-03-31
CO_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  | 2015-03-31
CO_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no | no | no |  |  | 2015-03-31
CO_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.4935 | 1.3235 | 1.4933 | 1.3138 | 1.5254 | 1.3476 | 1.5333 | 1.341 |  |  | 2015-03-31
CO_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 150.1631 | 133.0673 | 150.136 | 132.0945 | 153.372 | 135.4944 | 154.165 | 134.8252 |  |  | 2015-03-31
CO_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 13.4508 | 11.5684 | 13.4197 | 11.5105 | 12.9926 | 11.1449 | 12.6651 | 10.7895 |  |  | 2015-03-31
CO_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 13.2584 | 11.5133 | 13.1983 | 11.4199 | 12.7983 | 11.0851 | 12.4709 | 10.5897 |  |  | 2015-03-31
CO_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 12.0399 | 10.729 | 12.0297 | 10.6035 | 11.6594 | 10.3778 | 11.3585 | 10.0737 |  |  | 2015-03-31
CO_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 16.7416 | 14.45 | 16.6048 | 14.2808 | 16.073 | 13.9598 | 15.868 | 13.475 |  |  | 2015-03-31
CO_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.3403 | 2.3102 | 2.358 | 2.3286 | 2.3616 | 2.3406 | 3.0475 | 3.0475 |  |  | 2015-03-31
CO_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.6531 | 1.3909 | 1.6314 | 1.3743 | 1.5809 | 1.3278 | 1.7508 | 1.3665 |  |  | 2015-03-31
CO_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  | 2015-03-31
CO_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.2459 | 2.8763 | 3.2453 | 2.8553 | 3.3152 | 2.9288 | 3.3324 | 2.9143 |  |  | 2015-03-31
CO_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
CO_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
CO_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
CO_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
CO_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | NO | NO | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
CO_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
CO_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES | YES | YES |  |  | 2015-03-31
CO_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 95.9596 | 86.0182 | 95.0108 | 84.4831 | 93.5435 | 83.5423 | 90.7208 | 80.496 |  |  | 2015-03-31
CO_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.7546 | 1.6476 | 1.7704 | 1.64 | 1.7109 | 1.591 | 1.7145 | 1.5178 |  |  | 2015-03-31
CO_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 4.6204 | 4.4907 | 4.3919 | 4.2562 | 4.2305 | 4.0762 | 4.2958 | 4.0959 |  |  | 2015-03-31
CO_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.4522 | 2.3322 | 2.3407 | 2.2201 | 2.2189 | 2.1068 | 2.0763 | 1.9216 |  |  | 2015-03-31
CO_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.0455 | 4.0022 | 4.0825 | 4.0339 | 4.0741 | 4.0344 | 4.2024 | 4.1829 |  |  | 2015-03-31
CO_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 783.9856 | 741.608 | 805.1744 | 741.608 | 762.7968 | 720.4192 | 762.7968 | 678.0416 |  |  | 2015-03-31
CO_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1928.1808 | 1864.6144 | 1928.1808 | 1864.6144 | 1906.992 | 1843.4256 | 1928.1808 | 1843.4256 |  |  | 2015-03-31
CO_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 932.3072 | 868.7408 | 932.3072 | 868.7408 | 911.1184 | 868.7408 | 932.3072 | 868.7408 |  |  | 2015-03-31
CO_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1822.2368 | 1801.048 | 1843.4256 | 1822.2368 | 1843.4256 | 1822.2368 | 1885.8032 | 1885.8032 |  |  | 2015-03-31
CO_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  | 2015-03-31
CO_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  | 2015-03-31
CO_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  | 2015-03-31
CO_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  | 2015-03-31
CO_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized | motorized | motorized |  |  | 2015-03-31
CO_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
CO_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | No | No | No | No | No | No | No |  |  | 2015-03-31
CO_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
CO_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | No | No | No | No |  |  | 2015-03-31
CO_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.3513 | 1.3066 | 1.3539 | 1.3056 | 1.3344 | 1.2858 | 1.355 | 1.292 |  |  | 2015-03-31
CO_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.2761 | 1.2624 | 1.2878 | 1.2724 | 1.2851 | 1.2726 | 1.3256 | 1.3194 |  |  | 2015-03-31
CO_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.52556 | 0.52132 | 0.50133 | 0.49033 | 0.44729 | 0.44192 | 0.40117 | 0.41497 |  |  | 2015-03-31
CO_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.51878 | 0.51487 | 0.4948 | 0.48421 | 0.44088 | 0.43598 | 0.39476 | 0.4079 |  |  | 2015-03-31
CO_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.64245 | 0.63647 | 0.61152 | 0.60142 | 0.53846 | 0.52875 | 0.46696 | 0.49778 |  |  | 2015-03-31
CO_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.92936 | 0.92635 | 0.89317 | 0.87296 | 0.82148 | 0.80364 | 0.73923 | 0.79028 |  |  | 2015-03-31
CO_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.52699 | 0.52271 | 0.53216 | 0.51927 | 0.47527 | 0.46602 | 0.40009 | 0.42907 |  |  | 2015-03-31
CO_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.54364 | 0.53997 | 0.54999 | 0.53746 | 0.49402 | 0.48506 | 0.42043 | 0.44996 |  |  | 2015-03-31
CO_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.93595 | 0.92801 | 0.91612 | 0.88838 | 0.84685 | 0.81863 | 0.75062 | 0.80356 |  |  | 2015-03-31
CO_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4856 | 1.4633 | 1.4677 | 1.4327 | 1.38 | 1.3496 | 1.3228 | 1.3475 |  |  | 2015-03-31
CO_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4742 | 1.4524 | 1.4564 | 1.422 | 1.3689 | 1.3393 | 1.3113 | 1.3348 |  |  | 2015-03-31
CO_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8486 | 1.8204 | 1.8179 | 1.7834 | 1.6808 | 1.6329 | 1.5623 | 1.6705 |  |  | 2015-03-31
CO_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4936 | 2.4587 | 2.4539 | 2.3838 | 2.3249 | 2.2533 | 2.1994 | 2.3158 |  |  | 2015-03-31
CO_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.5239 | 1.4971 | 1.5803 | 1.5338 | 1.492 | 1.4458 | 1.3661 | 1.4284 |  |  | 2015-03-31
CO_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.5305 | 1.5033 | 1.5869 | 1.5402 | 1.4991 | 1.4533 | 1.3739 | 1.4368 |  |  | 2015-03-31
CO_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.0869 | 2.0457 | 2.1336 | 2.0604 | 2.0148 | 1.9416 | 1.822 | 1.9315 |  |  | 2015-03-31
CO_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5313 | 2.4827 | 2.5353 | 2.4447 | 2.4153 | 2.3163 | 2.2525 | 2.3774 |  |  | 2015-03-31
CO_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.455 | 2.4561 | 2.4504 | 2.473 | 2.3214 | 2.3573 | 2.3629 | 2.4295 |  |  | 2015-03-31
CO_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0399 | 0.94053 | 1.0166 | 0.91185 | 0.94064 | 0.84872 | 0.86794 | 0.81217 |  |  | 2015-03-31
CO_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0387 | 0.92826 | 1.015 | 0.89974 | 0.93892 | 0.83676 | 0.86685 | 0.79759 |  |  | 2015-03-31
CO_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3086 | 1.1621 | 1.2777 | 1.1261 | 1.1821 | 1.0465 | 1.0737 | 0.98348 |  |  | 2015-03-31
CO_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6556 | 1.544 | 1.6197 | 1.4936 | 1.5252 | 1.4084 | 1.4194 | 1.4173 |  |  | 2015-03-31
CO_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.228 | 1.0824 | 1.2446 | 1.0926 | 1.1689 | 1.0267 | 1.0648 | 0.98227 |  |  | 2015-03-31
CO_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2319 | 1.0864 | 1.2487 | 1.0973 | 1.1737 | 1.0311 | 1.0696 | 0.98842 |  |  | 2015-03-31
CO_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5128 | 1.3617 | 1.5243 | 1.361 | 1.4306 | 1.28 | 1.288 | 1.2363 |  |  | 2015-03-31
CO_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7203 | 1.5834 | 1.7081 | 1.5517 | 1.6166 | 1.4666 | 1.4824 | 1.4641 |  |  | 2015-03-31
CO_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  | 2015-03-31
CO_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  | 2015-03-31
CO_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
CO_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
CO_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
CO_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
CO_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
CO_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
CO_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
CO_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  | 2015-03-31
CO_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  | 2015-03-31
CO_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  | 2015-03-31
CO_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 211.888 | 211.888 | 190.6992 | 190.6992 | 190.6992 |  |  | 2015-03-31
CO_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 211.888 | 190.6992 | 190.6992 | 169.5104 | 190.6992 |  |  | 2015-03-31
CO_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 296.6432 | 275.4544 | 275.4544 | 233.0768 | 233.0768 | 211.888 | 233.0768 |  |  | 2015-03-31
CO_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 423.776 | 402.5872 | 402.5872 | 360.2096 | 360.2096 | 339.0208 | 360.2096 |  |  | 2015-03-31
CO_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 233.0768 | 211.888 | 211.888 | 190.6992 | 190.6992 |  |  | 2015-03-31
CO_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 233.0768 | 254.2656 | 233.0768 | 211.888 | 211.888 | 190.6992 | 211.888 |  |  | 2015-03-31
CO_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 423.776 | 402.5872 | 402.5872 | 381.3984 | 360.2096 | 339.0208 | 360.2096 |  |  | 2015-03-31
CO_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 656.8528 | 635.664 | 614.4752 | 614.4752 | 593.2864 | 614.4752 |  |  | 2015-03-31
CO_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 656.8528 | 656.8528 | 635.664 | 614.4752 | 593.2864 | 593.2864 | 593.2864 |  |  | 2015-03-31
CO_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 826.3632 | 826.3632 | 805.1744 | 762.7968 | 741.608 | 699.2304 | 741.608 |  |  | 2015-03-31
CO_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1123.0064 | 1101.8176 | 1101.8176 | 1080.6288 | 1038.2512 | 1017.0624 | 995.8736 | 1038.2512 |  |  | 2015-03-31
CO_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 678.0416 | 720.4192 | 699.2304 | 678.0416 | 656.8528 | 614.4752 | 635.664 |  |  | 2015-03-31
CO_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 720.4192 | 699.2304 | 678.0416 | 656.8528 | 614.4752 | 656.8528 |  |  | 2015-03-31
CO_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | 953.496 | 932.3072 | 911.1184 | 868.7408 | 826.3632 | 868.7408 |  |  | 2015-03-31
CO_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1144.1952 | 1123.0064 | 1144.1952 | 1101.8176 | 1080.6288 | 1038.2512 | 1017.0624 | 1080.6288 |  |  | 2015-03-31
CO_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 1101.8176 | 1101.8176 | 1101.8176 | 1123.0064 | 1038.2512 | 1059.44 | 1059.44 | 1101.8176 |  |  | 2015-03-31
CO_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 423.776 | 466.1536 | 402.5872 | 423.776 | 381.3984 | 381.3984 | 360.2096 |  |  | 2015-03-31
CO_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 423.776 | 466.1536 | 402.5872 | 423.776 | 381.3984 | 381.3984 | 360.2096 |  |  | 2015-03-31
CO_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 572.0976 | 508.5312 | 529.72 | 466.1536 | 487.3424 | 444.9648 |  |  | 2015-03-31
CO_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 699.2304 | 720.4192 | 678.0416 | 678.0416 | 635.664 | 635.664 | 635.664 |  |  | 2015-03-31
CO_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 487.3424 | 550.9088 | 487.3424 | 529.72 | 466.1536 | 487.3424 | 444.9648 |  |  | 2015-03-31
CO_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 487.3424 | 572.0976 | 487.3424 | 529.72 | 466.1536 | 487.3424 | 444.9648 |  |  | 2015-03-31
CO_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 678.0416 | 614.4752 | 635.664 | 572.0976 | 572.0976 | 550.9088 |  |  | 2015-03-31
CO_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 762.7968 | 699.2304 | 720.4192 | 656.8528 | 656.8528 | 656.8528 |  |  | 2015-03-31
CO_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  | 2015-03-31
CO_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.16772 | 0.16637 | 0.15998 | 0.15647 | 0.14274 | 0.14102 | 0.12803 | 0.13243 |  |  | 2015-03-31
CO_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.16555 | 0.1643 | 0.15791 | 0.15453 | 0.1407 | 0.13913 | 0.12598 | 0.13017 |  |  | 2015-03-31
CO_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.20502 | 0.20311 | 0.19515 | 0.19193 | 0.17184 | 0.16874 | 0.14901 | 0.15886 |  |  | 2015-03-31
CO_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.29658 | 0.29561 | 0.28503 | 0.27858 | 0.26216 | 0.25646 | 0.2359 | 0.25219 |  |  | 2015-03-31
CO_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16818 | 0.16681 | 0.16983 | 0.16571 | 0.15167 | 0.14872 | 0.12768 | 0.13693 |  |  | 2015-03-31
CO_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.17349 | 0.17232 | 0.17551 | 0.17152 | 0.15765 | 0.15479 | 0.13417 | 0.1436 |  |  | 2015-03-31
CO_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.29869 | 0.29615 | 0.29236 | 0.28351 | 0.27026 | 0.26124 | 0.23955 | 0.25643 |  |  | 2015-03-31
CO_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.47409 | 0.46697 | 0.46838 | 0.45722 | 0.44041 | 0.43067 | 0.42215 | 0.43003 |  |  | 2015-03-31
CO_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.47044 | 0.46351 | 0.46478 | 0.4538 | 0.43685 | 0.42738 | 0.41847 | 0.42598 |  |  | 2015-03-31
CO_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.58994 | 0.58093 | 0.58014 | 0.56912 | 0.53638 | 0.52109 | 0.49855 | 0.53308 |  |  | 2015-03-31
CO_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.79575 | 0.78465 | 0.78309 | 0.76071 | 0.74193 | 0.71907 | 0.70188 | 0.73902 |  |  | 2015-03-31
CO_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.48632 | 0.47775 | 0.50432 | 0.48947 | 0.47613 | 0.46138 | 0.43595 | 0.45583 |  |  | 2015-03-31
CO_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.48841 | 0.47975 | 0.50642 | 0.49151 | 0.4784 | 0.46378 | 0.43843 | 0.45851 |  |  | 2015-03-31
CO_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.66598 | 0.65284 | 0.68088 | 0.65753 | 0.64298 | 0.61961 | 0.58143 | 0.61637 |  |  | 2015-03-31
CO_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.8078 | 0.7923 | 0.80908 | 0.78017 | 0.77078 | 0.73918 | 0.71883 | 0.75868 |  |  | 2015-03-31
CO_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.78347 | 0.78379 | 0.78198 | 0.78918 | 0.74082 | 0.75227 | 0.75404 | 0.7753 |  |  | 2015-03-31
CO_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.33186 | 0.30015 | 0.32442 | 0.29099 | 0.30017 | 0.27085 | 0.27697 | 0.25918 |  |  | 2015-03-31
CO_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.33147 | 0.29623 | 0.32391 | 0.28713 | 0.29964 | 0.26702 | 0.27664 | 0.25453 |  |  | 2015-03-31
CO_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.41761 | 0.37085 | 0.40775 | 0.35937 | 0.37723 | 0.33395 | 0.34264 | 0.31385 |  |  | 2015-03-31
CO_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.52835 | 0.49273 | 0.51688 | 0.47665 | 0.48674 | 0.44944 | 0.45297 | 0.45229 |  |  | 2015-03-31
CO_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.39187 | 0.34541 | 0.3972 | 0.34867 | 0.37303 | 0.32764 | 0.3398 | 0.31346 |  |  | 2015-03-31
CO_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.39313 | 0.34669 | 0.3985 | 0.35017 | 0.37456 | 0.32905 | 0.34134 | 0.31542 |  |  | 2015-03-31
CO_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.48277 | 0.43456 | 0.48643 | 0.43433 | 0.45654 | 0.40846 | 0.41104 | 0.39453 |  |  | 2015-03-31
CO_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.54899 | 0.5053 | 0.54509 | 0.49519 | 0.5159 | 0.46802 | 0.47306 | 0.46724 |  |  | 2015-03-31
OR_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.4241 | 1.345 | 1.4802 | 1.3631 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.2682 | 2.1048 | 1.8744 | 1.7408 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4007 | 1.338 | 1.4233 | 1.3743 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.3526 | 1.2705 | 1.4792 | 1.3671 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6111 | 1.506 | 1.7658 | 1.6662 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 656.8528 | 614.4752 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 1017.0624 | 953.496 | 847.552 | 783.9856 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 656.8528 | 614.4752 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 720.4192 | 678.0416 | 805.1744 | 741.608 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42581 | 0.39712 | 0.47236 | 0.43499 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.72384 | 0.67169 | 0.59816 | 0.55552 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.447 | 0.42699 | 0.45422 | 0.43857 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.42276 | 0.39151 | 0.47205 | 0.43629 | [6 empty] | 2015-03-31
OR_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.51415 | 0.48062 | 0.56351 | 0.53173 | [6 empty] | 2015-03-31
OR_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 9937.5472 | 9492.5824 | 10933.4208 | 10552.0224 | [6 empty] | 2015-03-31
OR_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24536.6304 | 24134.0432 | 26528.3776 | 26104.6016 | [6 empty] | 2015-03-31
OR_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 197966.9587 | 193241.8563 | 210150.5187 | 205955.1363 | [6 empty] | 2015-03-31
OR_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23392.4352 | 21760.8976 | 25405.3712 | 23498.3792 | [6 empty] | 2015-03-31
OR_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OR_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OR_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OR_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OR_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
OR_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
OR_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
OR_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
OR_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
OR_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
OR_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
OR_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
OR_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OR_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OR_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OR_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
OR_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
OR_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
OR_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OR_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OR_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OR_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 307.1266 | 300.2983 | 278.4284 | 272.7093 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 307.1266 | 300.2983 | 278.4284 | 272.7093 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
OR_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 291.5043 | 285.0208 | 264.2738 | 258.8356 | [6 empty] | 2015-03-31
OR_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 291.5043 | 285.0208 | 264.2738 | 258.8356 | [6 empty] | 2015-03-31
OR_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.9957 | 3.9183 | 4.5217 | 4.4172 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1446.239 | 707.0433 | 1311.1023 | 642.0855 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 707.0433 | 0 | 642.0855 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1446.239 | 1414.085 | 1311.1023 | 1284.171 | [6 empty] | 2015-03-31
OR_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 803.4846 | 787.9196 | 909.2459 | 888.2315 | [6 empty] | 2015-03-31
OR_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1687.4254 | 1643.6785 | 1551.4471 | 1511.1207 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
OR_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.661 | 10.1816 | 11.7379 | 11.3223 | [6 empty] | 2015-03-31
OR_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.2904 | 32.8412 | 38.1446 | 35.501 | [6 empty] | 2015-03-31
OR_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 278.3845 | 257.1492 | 295.538 | 289.6433 | [6 empty] | 2015-03-31
OR_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.6292 | 29.6113 | 36.5335 | 33.7726 | [6 empty] | 2015-03-31
OR_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.5094 | 42.3854 | 47.5683 | 47.486 | [6 empty] | 2015-03-31
OR_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.83283 | 0.81251 | 0.92206 | 0.90118 | [6 empty] | 2015-03-31
OR_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.5692 | 10.2505 | 11.6876 | 11.3574 | [6 empty] | 2015-03-31
OR_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.7216 | 0.6934 | 0.79873 | 0.76874 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 7.802 | 3.8142 | 7.0729 | 3.4638 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 3.8142 | 0 | 3.4638 | [6 empty] | 2015-03-31
OR_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 23.4059 | 22.8855 | 21.2188 | 20.7829 | [6 empty] | 2015-03-31
OR_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.3678 | 17.0313 | 19.6539 | 19.1996 | [6 empty] | 2015-03-31
OR_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 31.2534 | 30.4422 | 28.7351 | 27.9882 | [6 empty] | 2015-03-31
OR_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8198 | 3.7849 | 4.0645 | 4.0328 | [6 empty] | 2015-03-31
OR_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
OR_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | [6 empty] | 2015-03-31
OR_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
OR_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | YES | [6 empty] | 2015-03-31
OR_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4305.3855 | 4202.6328 | 4381.4557 | 4261.91 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 7.2235 | 7.2193 | 6.8745 | 6.8921 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 32.1608 | 28.3621 | 32.6418 | 27.5721 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4517 | 6.2254 | 6.2577 | 5.9901 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5491 | 5.2719 | 5.171 | 4.8124 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 2966.432 | 2966.432 | 3093.5648 | 3093.5648 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12670.9024 | 11441.952 | 13963.4192 | 12416.6368 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2902.8656 | 2796.9216 | 2818.1104 | 2690.9776 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2479.0896 | 2351.9568 | 2330.768 | 2161.2576 | [6 empty] | 2015-03-31
OR_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
OR_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | [6 empty] | 2015-03-31
OR_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.4062 | 1.5359 | 3.4971 | 2.3214 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.0823 | 2.0836 | 2.0958 | 2.1011 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.5945 | 12.2685 | 14.8821 | 13.3201 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 2.0351 | 1.9637 | 1.9739 | 1.8895 | [6 empty] | 2015-03-31
OR_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.7416 | 1.644 | 1.6311 | 1.518 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.0651 | 23.2627 | 22.9589 | 20.2476 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.8802 | 22.9714 | 22.7915 | 20.2026 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.2254 | 21.7098 | 20.3632 | 18.8219 | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 24.7658 | 22.5398 | 23.136 | 20.4145 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.0609 | 7.0399 | 7.1229 | 7.0845 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.1787 | 4.7604 | 5.1499 | 4.5039 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.2166 | 10.2166 | 8.8506 | 8.8506 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8136.4992 | 7161.8144 | 8581.464 | 7352.5136 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 8051.744 | 7077.0592 | 8496.7088 | 7331.3248 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7373.7024 | 6695.6608 | 7712.7232 | 6865.1712 | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9407.8272 | 8263.632 | 10424.8896 | 8920.4848 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2775.7328 | 2754.544 | 3093.5648 | 3072.376 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1779.8592 | 1567.9712 | 2034.1248 | 1716.2928 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
OR_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | [6 empty] | 2015-03-31
OR_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
OR_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
OR_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OR_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
OR_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | Yes | No | Yes | [6 empty] | 2015-03-31
OR_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | Yes | No | Yes | [6 empty] | 2015-03-31
OR_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | Yes | No | Yes | [6 empty] | 2015-03-31
OR_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7169.1669 | 7852.8447 | 7346.4748 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7079.39 | 7852.8447 | 7330.1594 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6690.5755 | 6777.6191 | 6777.6191 | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 825.0071 | 825.0071 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
OR_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | No | Yes | No | [6 empty] | 2015-03-31
OR_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | No | Yes | No | [6 empty] | 2015-03-31
OR_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | No | Yes | No | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
OR_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
OR_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
OR_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
OR_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.3587 | 1.2686 | 1.5 | 1.3411 | [6 empty] | 2015-03-31
OR_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 136.6071 | 127.5447 | 150.816 | 134.8422 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.9096 | 10.4965 | 12.5747 | 10.7562 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.7789 | 10.3651 | 12.4371 | 10.7323 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.7966 | 9.8706 | 11.305 | 10.0391 | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.7684 | 12.1133 | 15.1504 | 13.0472 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 1.9448 | 1.929 | 2.0967 | 2.0736 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2514 | 1.0959 | 1.4305 | 1.2081 | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
OR_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.9528 | 2.757 | 3.26 | 2.9147 | [6 empty] | 2015-03-31
OR_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OR_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OR_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OR_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OR_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
OR_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 102.9917 | 97.7487 | 99.5311 | 90.5101 | [6 empty] | 2015-03-31
OR_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.8925 | 1.7902 | 1.7064 | 1.6066 | [6 empty] | 2015-03-31
OR_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 4.6154 | 4.5033 | 4.3409 | 4.2278 | [6 empty] | 2015-03-31
OR_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.3915 | 2.3085 | 2.3111 | 2.2141 | [6 empty] | 2015-03-31
OR_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 3.9034 | 3.8731 | 3.8053 | 3.7661 | [6 empty] | 2015-03-31
OR_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 741.608 | 678.0416 | 741.608 | 699.2304 | [6 empty] | 2015-03-31
OR_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1546.7824 | 1504.4048 | 1737.4816 | 1652.7264 | [6 empty] | 2015-03-31
OR_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 741.608 | 699.2304 | 826.3632 | 783.9856 | [6 empty] | 2015-03-31
OR_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1652.7264 | 1631.5376 | [6 empty] | 2015-03-31
OR_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
OR_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
OR_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
OR_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
OR_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
OR_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OR_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | No | No | [6 empty] | 2015-03-31
OR_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OR_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
OR_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.0863 | 1.0532 | 1.2108 | 1.1636 | [6 empty] | 2015-03-31
OR_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0656 | 1.0557 | 1.1645 | 1.1507 | [6 empty] | 2015-03-31
OR_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.40435 | 0.40409 | 0.44759 | 0.43871 | [6 empty] | 2015-03-31
OR_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.39949 | 0.39534 | 0.44122 | 0.43274 | [6 empty] | 2015-03-31
OR_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.53424 | 0.54002 | 0.53614 | 0.52318 | [6 empty] | 2015-03-31
OR_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.73197 | 0.72927 | 0.81301 | 0.79592 | [6 empty] | 2015-03-31
OR_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.69164 | 0.69437 | 0.54304 | 0.53383 | [6 empty] | 2015-03-31
OR_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.705 | 0.70639 | 0.55943 | 0.55035 | [6 empty] | 2015-03-31
OR_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.92454 | 0.92621 | 0.86568 | 0.84156 | [6 empty] | 2015-03-31
OR_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.149 | 1.1264 | 1.303 | 1.2719 | [6 empty] | 2015-03-31
OR_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.1404 | 1.1184 | 1.292 | 1.2616 | [6 empty] | 2015-03-31
OR_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.5326 | 1.5108 | 1.59 | 1.5419 | [6 empty] | 2015-03-31
OR_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.959 | 1.9273 | 2.2202 | 2.1578 | [6 empty] | 2015-03-31
OR_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.879 | 1.8549 | 1.5828 | 1.5453 | [6 empty] | 2015-03-31
OR_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.88 | 1.8606 | 1.589 | 1.5517 | [6 empty] | 2015-03-31
OR_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3246 | 2.2975 | 2.0913 | 2.0287 | [6 empty] | 2015-03-31
OR_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4456 | 2.4108 | 2.3925 | 2.3102 | [6 empty] | 2015-03-31
OR_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1188 | 2.1308 | 2.175 | 2.1722 | [6 empty] | 2015-03-31
OR_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.84105 | 0.74186 | 0.89686 | 0.80037 | [6 empty] | 2015-03-31
OR_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.84324 | 0.74307 | 0.89497 | 0.78875 | [6 empty] | 2015-03-31
OR_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0574 | 0.93052 | 1.1312 | 0.99545 | [6 empty] | 2015-03-31
OR_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.2851 | 1.1973 | 1.461 | 1.3513 | [6 empty] | 2015-03-31
OR_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3118 | 1.2101 | 1.2118 | 1.0793 | [6 empty] | 2015-03-31
OR_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3156 | 1.214 | 1.2155 | 1.0838 | [6 empty] | 2015-03-31
OR_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5377 | 1.4315 | 1.4675 | 1.3258 | [6 empty] | 2015-03-31
OR_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6223 | 1.5189 | 1.6092 | 1.4651 | [6 empty] | 2015-03-31
OR_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
OR_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
OR_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OR_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OR_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OR_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OR_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OR_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OR_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OR_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
OR_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
OR_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
OR_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 169.5104 | 169.5104 | 211.888 | 190.6992 | [6 empty] | 2015-03-31
OR_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 169.5104 | 169.5104 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
OR_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
OR_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 317.832 | 360.2096 | 360.2096 | [6 empty] | 2015-03-31
OR_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 254.2656 | 233.0768 | [6 empty] | 2015-03-31
OR_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 296.6432 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
OR_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 402.5872 | 381.3984 | 381.3984 | [6 empty] | 2015-03-31
OR_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 487.3424 | 593.2864 | 572.0976 | [6 empty] | 2015-03-31
OR_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 487.3424 | 572.0976 | 572.0976 | [6 empty] | 2015-03-31
OR_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 678.0416 | 720.4192 | 699.2304 | [6 empty] | 2015-03-31
OR_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | 995.8736 | 974.6848 | [6 empty] | 2015-03-31
OR_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 783.9856 | 720.4192 | 699.2304 | [6 empty] | 2015-03-31
OR_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 783.9856 | 720.4192 | 699.2304 | [6 empty] | 2015-03-31
OR_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 995.8736 | 932.3072 | 911.1184 | [6 empty] | 2015-03-31
OR_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1080.6288 | 1059.44 | 1080.6288 | 1038.2512 | [6 empty] | 2015-03-31
OR_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 953.496 | 974.6848 | 974.6848 | [6 empty] | 2015-03-31
OR_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 296.6432 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
OR_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 296.6432 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
OR_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 402.5872 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
OR_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 656.8528 | 614.4752 | [6 empty] | 2015-03-31
OR_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 487.3424 | [6 empty] | 2015-03-31
OR_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 487.3424 | [6 empty] | 2015-03-31
OR_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
OR_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 678.0416 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
OR_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
OR_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.11946 | 0.11798 | 0.14283 | 0.14 | [6 empty] | 2015-03-31
OR_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.11784 | 0.11643 | 0.14081 | 0.1381 | [6 empty] | 2015-03-31
OR_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.16163 | 0.16366 | 0.17109 | 0.16696 | [6 empty] | 2015-03-31
OR_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.22398 | 0.22307 | 0.25945 | 0.25399 | [6 empty] | 2015-03-31
OR_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.19993 | 0.20084 | 0.1733 | 0.17036 | [6 empty] | 2015-03-31
OR_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.20439 | 0.2055 | 0.17853 | 0.17563 | [6 empty] | 2015-03-31
OR_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.27763 | 0.2782 | 0.27626 | 0.26857 | [6 empty] | 2015-03-31
OR_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.35038 | 0.34274 | 0.41582 | 0.4059 | [6 empty] | 2015-03-31
OR_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.34749 | 0.34002 | 0.41231 | 0.4026 | [6 empty] | 2015-03-31
OR_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.47817 | 0.47429 | 0.5074 | 0.49206 | [6 empty] | 2015-03-31
OR_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.61415 | 0.60341 | 0.70853 | 0.6886 | [6 empty] | 2015-03-31
OR_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.56192 | 0.55548 | 0.50511 | 0.49313 | [6 empty] | 2015-03-31
OR_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.56382 | 0.55738 | 0.50707 | 0.49519 | [6 empty] | 2015-03-31
OR_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.71128 | 0.70224 | 0.66739 | 0.64741 | [6 empty] | 2015-03-31
OR_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.75958 | 0.74793 | 0.76348 | 0.73724 | [6 empty] | 2015-03-31
OR_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67614 | 0.67999 | 0.69409 | 0.69319 | [6 empty] | 2015-03-31
OR_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.24876 | 0.21674 | 0.28621 | 0.25541 | [6 empty] | 2015-03-31
OR_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.24859 | 0.21631 | 0.28561 | 0.25171 | [6 empty] | 2015-03-31
OR_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.31825 | 0.29013 | 0.361 | 0.31767 | [6 empty] | 2015-03-31
OR_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.40531 | 0.37728 | 0.46623 | 0.43125 | [6 empty] | 2015-03-31
OR_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.40402 | 0.37024 | 0.3867 | 0.34444 | [6 empty] | 2015-03-31
OR_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.4053 | 0.37153 | 0.38789 | 0.34588 | [6 empty] | 2015-03-31
OR_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.4787 | 0.44437 | 0.46833 | 0.42311 | [6 empty] | 2015-03-31
OR_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.50839 | 0.47394 | 0.51354 | 0.46753 | [6 empty] | 2015-03-31
WA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.3197 | 1.236 | 1.4748 | 1.3564 | 1.4399 | 1.337 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.2848 | 2.1367 | 2.0549 | 1.8885 | 2.0191 | 1.8944 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3489 | 1.2903 | 1.5235 | 1.4683 | 1.4329 | 1.4054 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.2361 | 1.1558 | 1.4819 | 1.384 | 1.398 | 1.3213 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5641 | 1.4713 | 1.7703 | 1.6691 | 1.7067 | 1.6597 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 656.8528 | 614.4752 | 656.8528 | 593.2864 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 1038.2512 | 953.496 | 932.3072 | 847.552 | 911.1184 | 847.552 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 678.0416 | 656.8528 | 635.664 | 635.664 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 550.9088 | 529.72 | 656.8528 | 614.4752 | 635.664 | 593.2864 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 805.1744 | 741.608 | 762.7968 | 741.608 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42115 | 0.39443 | 0.47065 | 0.43286 | 0.4595 | 0.42666 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.72914 | 0.68188 | 0.65577 | 0.60268 | 0.64435 | 0.60455 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.43047 | 0.41176 | 0.48617 | 0.46857 | 0.45726 | 0.44848 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.39448 | 0.36885 | 0.4729 | 0.44167 | 0.44614 | 0.42166 |  |  |  |  | 2015-03-31
WA_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.49916 | 0.46953 | 0.56495 | 0.53265 | 0.54463 | 0.52964 |  |  |  |  | 2015-03-31
WA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10043.4912 | 9598.5264 | 10806.288 | 10424.8896 | 10806.288 | 10403.7008 |  |  |  |  | 2015-03-31
WA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24430.6864 | 24070.4768 | 26761.4544 | 26422.4336 | 26528.3776 | 26146.9792 |  |  |  |  | 2015-03-31
WA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 195636.1907 | 191292.4867 | 218265.8291 | 214409.4675 | 211167.5811 | 206463.6675 |  |  |  |  | 2015-03-31
WA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22820.3376 | 21337.1216 | 25723.2032 | 23795.0224 | 25384.1824 | 23540.7568 |  |  |  |  | 2015-03-31
WA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WA_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | 2015-03-31
WA_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | 2015-03-31
WA_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | Yes | Yes | No |  |  |  |  | 2015-03-31
WA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
WA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
WA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
WA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
WA_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
WA_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
WA_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
WA_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
WA_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WA_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WA_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes |  |  |  |  | 2015-03-31
WA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes |  |  |  |  | 2015-03-31
WA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | No | No | Yes |  |  |  |  | 2015-03-31
WA_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WA_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WA_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WA_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 278.5666 | 272.3197 | 298.1681 | 292.8707 | 284.5206 | 278.3868 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 278.5666 | 272.3197 | 298.1681 | 292.8707 | 284.5206 | 278.3868 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
WA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 264.4061 | 258.4651 | 283.0096 | 277.9817 | 270.056 | 264.2341 |  |  |  |  | 2015-03-31
WA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 264.4061 | 258.4651 | 283.0096 | 277.9817 | 270.056 | 264.2341 |  |  |  |  | 2015-03-31
WA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 3.9139 | 3.8384 | 4.7559 | 4.6448 | 5.2271 | 5.0775 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1311.7521 | 641.1678 | 1404.0549 | 689.554 | 1339.7898 | 655.4521 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 641.1678 | 0 | 689.554 | 0 | 655.4521 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1311.7521 | 1282.3355 | 1404.0549 | 1379.1097 | 1339.7898 | 1310.9057 |  |  |  |  | 2015-03-31
WA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 787.0367 | 771.841 | 956.3419 | 934.0025 | 1051.0967 | 1021.0144 |  |  |  |  | 2015-03-31
WA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1552.2174 | 1508.9619 | 1661.4309 | 1622.9146 | 1585.3493 | 1542.5804 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WA_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.7824 | 10.2978 | 11.5927 | 11.1807 | 11.5983 | 11.1593 |  |  |  |  | 2015-03-31
WA_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.1324 | 32.7418 | 38.4624 | 35.9517 | 38.1486 | 37.5756 |  |  |  |  | 2015-03-31
WA_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 275.1324 | 254.5405 | 306.9378 | 301.5085 | 296.9675 | 290.345 |  |  |  |  | 2015-03-31
WA_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.8063 | 29.1736 | 36.9832 | 34.2129 | 36.4945 | 33.8448 |  |  |  |  | 2015-03-31
WA_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.0918 | 42.9666 | 46.6945 | 46.6128 | 47.3916 | 47.2975 |  |  |  |  | 2015-03-31
WA_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.84486 | 0.82407 | 0.9094 | 0.88871 | 0.92206 | 0.90111 |  |  |  |  | 2015-03-31
WA_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.7184 | 10.3902 | 11.5504 | 11.2179 | 11.7093 | 11.3829 |  |  |  |  | 2015-03-31
WA_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.7285 | 0.70068 | 0.78978 | 0.75973 | 0.7976 | 0.76885 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 7.0764 | 3.4589 | 7.5744 | 3.7199 | 7.2277 | 3.5359 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 3.4589 | 0 | 3.7199 | 0 | 3.5359 |  |  |  |  | 2015-03-31
WA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.2293 | 20.7533 | 22.7231 | 22.3194 | 21.6831 | 21.2156 |  |  |  |  | 2015-03-31
WA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 17.0122 | 16.6838 | 20.6719 | 20.189 | 22.7201 | 22.0698 |  |  |  |  | 2015-03-31
WA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 28.7494 | 27.9482 | 30.7723 | 30.0574 | 29.3639 | 28.5709 |  |  |  |  | 2015-03-31
WA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8172 | 3.7819 | 4.0592 | 4.027 | 4.0678 | 4.0357 |  |  |  |  | 2015-03-31
WA_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | NO | NO | YES | YES |  |  |  |  | 2015-03-31
WA_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | NO | YES | YES | YES |  |  |  |  | 2015-03-31
WA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4211.9399 | 4114.5535 | 4587.1223 | 4454.7413 | 4758.1704 | 4591.0231 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 6.7727 | 6.7877 | 7.726 | 7.6119 | 6.9812 | 7.0403 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 28.8719 | 26.683 | 31.0606 | 28.898 | 31.4998 | 26.9089 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4224 | 6.2199 | 6.579 | 6.2945 | 6.5087 | 6.2483 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4572 | 5.17 | 5.5455 | 5.1692 | 5.4175 | 5.0683 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 2839.2992 | 2839.2992 | 3474.9632 | 3432.5856 | 3114.7536 | 3157.1312 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12522.5808 | 11293.6304 | 13984.608 | 12967.5456 | 13348.944 | 12119.9936 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2881.6768 | 2796.9216 | 2966.432 | 2839.2992 | 2924.0544 | 2818.1104 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2457.9008 | 2330.768 | 2500.2784 | 2330.768 | 2436.712 | 2288.3904 |  |  |  |  | 2015-03-31
WA_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
WA_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | Yes | Yes |  |  |  |  | 2015-03-31
WA_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 2.3765 | 1.5111 | 3.6513 | 2.4411 | 4.3766 | 2.9997 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 1.983 | 1.9902 | 2.3553 | 2.3206 | 2.1098 | 2.1314 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.448 | 12.1273 | 14.9085 | 13.9268 | 14.3191 | 12.9997 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 2.0258 | 1.962 | 2.0752 | 1.9855 | 2.0531 | 1.9709 |  |  |  |  | 2015-03-31
WA_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.7214 | 1.6308 | 1.7492 | 1.6305 | 1.7089 | 1.5987 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 21.0606 | 18.9692 | 25.1186 | 22.3681 | 23.9954 | 21.3666 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 20.8512 | 18.7197 | 24.9394 | 22.1535 | 23.8162 | 21.1242 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 18.8863 | 17.6905 | 22.2807 | 20.6169 | 21.3094 | 19.7647 |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 20.9954 | 19.0591 | 24.41 | 21.8349 | 23.3077 | 20.8319 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 6.4565 | 6.4447 | 7.3448 | 7.2976 | 9.6906 | 9.6906 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 4.2828 | 3.8936 | 5.4247 | 4.8292 | 5.1947 | 4.6149 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 8.4043 | 8.4043 | 9.4598 | 9.4598 | 9.121 | 9.121 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7903.4224 | 7098.248 | 8729.7856 | 7500.8352 | 8645.0304 | 7437.2688 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7818.6672 | 7013.4928 | 8645.0304 | 7437.2688 | 8539.0864 | 7352.5136 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7183.0032 | 6632.0944 | 7882.2336 | 6992.304 | 7797.4784 | 6928.7376 |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9068.8064 | 8051.744 | 10467.2672 | 9005.24 | 10297.7568 | 8856.9184 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 2775.7328 | 2754.544 | 3051.1872 | 3029.9984 | 3347.8304 | 3347.8304 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1716.2928 | 1504.4048 | 2034.1248 | 1737.4816 | 2012.936 | 1716.2928 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
WA_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | n/a | n/a |  |  |  |  | 2015-03-31
WA_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | VFD | VFD |  |  |  |  | 2015-03-31
WA_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | n/a | VFD | VFD | VFD | n/a | VFD |  |  |  |  | 2015-03-31
WA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WA_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | Yes | Yes | No | No |  |  |  |  | 2015-03-31
WA_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | Yes | No | Yes | No | No |  |  |  |  | 2015-03-31
WA_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | Yes | No | Yes | No | No |  |  |  |  | 2015-03-31
WA_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | Yes | No | Yes | No | No |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7108.8212 | 7852.8447 | 7510.1371 | 7852.8447 | 7428.0517 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7814.0904 | 7015.315 | 7852.8447 | 7438.074 | 7852.8447 | 7343.7838 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6629.6153 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 825.0071 | 825.0071 | 1434.9903 | 1434.9903 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | No | Yes | No | Yes | Yes |  |  |  |  | 2015-03-31
WA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | No | Yes | No | Yes | Yes |  |  |  |  | 2015-03-31
WA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | No | Yes | No | Yes | Yes |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2015-03-31
WA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2015-03-31
WA_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.308 | 1.2377 | 1.5757 | 1.4058 | 1.6766 | 1.4889 |  |  |  |  | 2015-03-31
WA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 131.5082 | 124.4409 | 158.4208 | 141.3391 | 168.5698 | 149.6998 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.5767 | 10.4082 | 12.7957 | 10.9958 | 12.656 | 10.8756 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.4408 | 10.2713 | 12.6512 | 10.8903 | 12.508 | 10.7522 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.5228 | 9.7807 | 11.5304 | 10.236 | 11.4215 | 10.1411 |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.289 | 11.7928 | 15.223 | 13.1712 | 14.9804 | 12.9568 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 1.9461 | 1.9326 | 2.0704 | 2.0451 | 2.2687 | 2.2687 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.1983 | 1.0557 | 1.4306 | 1.2248 | 1.4143 | 1.2092 |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
WA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 2.8426 | 2.6899 | 3.4244 | 3.0551 | 3.6437 | 3.2358 |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 99.8891 | 95.9617 | 102.7274 | 93.1062 | 102.4517 | 92.4597 |  |  |  |  | 2015-03-31
WA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.7165 | 1.6071 | 1.7697 | 1.6452 | 1.693 | 1.5661 |  |  |  |  | 2015-03-31
WA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 4.095 | 3.9894 | 4.4635 | 4.3449 | 4.2828 | 4.1424 |  |  |  |  | 2015-03-31
WA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.1464 | 2.0668 | 2.3498 | 2.2525 | 2.2619 | 2.1729 |  |  |  |  | 2015-03-31
WA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 3.635 | 3.6046 | 3.8603 | 3.8158 | 3.7629 | 3.724 |  |  |  |  | 2015-03-31
WA_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 720.4192 | 678.0416 | 762.7968 | 699.2304 | 741.608 | 678.0416 |  |  |  |  | 2015-03-31
WA_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1504.4048 | 1462.0272 | 1695.104 | 1631.5376 | 1673.9152 | 1610.3488 |  |  |  |  | 2015-03-31
WA_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 720.4192 | 699.2304 | 805.1744 | 762.7968 | 805.1744 | 762.7968 |  |  |  |  | 2015-03-31
WA_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1652.7264 | 1631.5376 | 1652.7264 | 1631.5376 |  |  |  |  | 2015-03-31
WA_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
WA_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
WA_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
WA_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
WA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WA_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.059 | 1.0381 | 1.194 | 1.1487 | 1.1785 | 1.1329 |  |  |  |  | 2015-03-31
WA_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0686 | 1.0581 | 1.1528 | 1.1374 | 1.1608 | 1.1463 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.33781 | 0.33489 | 0.47391 | 0.46482 | 0.42071 | 0.41631 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.33261 | 0.32993 | 0.46758 | 0.45891 | 0.41407 | 0.41005 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.44795 | 0.45544 | 0.5785 | 0.57709 | 0.51806 | 0.51624 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.64108 | 0.64253 | 0.8395 | 0.82124 | 0.78851 | 0.77358 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.62147 | 0.62566 | 0.59445 | 0.5801 | 0.56306 | 0.54823 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.63372 | 0.63963 | 0.61036 | 0.59676 | 0.57877 | 0.56453 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.82573 | 0.83216 | 0.89148 | 0.86245 | 0.87424 | 0.845 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.0199 | 1 | 1.3632 | 1.3314 | 1.2803 | 1.2512 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.0106 | 0.99117 | 1.3523 | 1.3213 | 1.2685 | 1.2401 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.3627 | 1.3512 | 1.7202 | 1.6916 | 1.6199 | 1.584 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.7885 | 1.7646 | 2.2856 | 2.2198 | 2.207 | 2.1411 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7338 | 1.7191 | 1.6991 | 1.6469 | 1.6711 | 1.6102 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7397 | 1.7248 | 1.7063 | 1.6537 | 1.6778 | 1.6163 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.1376 | 2.1134 | 2.2412 | 2.1647 | 2.1735 | 2.0798 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.2872 | 2.2604 | 2.4649 | 2.3684 | 2.4587 | 2.3544 |  |  |  |  | 2015-03-31
WA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1053 | 2.1171 | 2.3027 | 2.3029 | 2.142 | 2.144 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.70093 | 0.61235 | 0.90982 | 0.82967 | 0.87203 | 0.78186 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.70265 | 0.61874 | 0.90988 | 0.81797 | 0.86854 | 0.7697 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.87653 | 0.80984 | 1.1567 | 1.0281 | 1.0932 | 0.9646 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1594 | 1.0885 | 1.482 | 1.3731 | 1.4488 | 1.333 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2207 | 1.1279 | 1.2807 | 1.1372 | 1.2573 | 1.1123 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2246 | 1.1325 | 1.2855 | 1.1421 | 1.2621 | 1.1165 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.4181 | 1.3235 | 1.5485 | 1.3959 | 1.5067 | 1.3469 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.511 | 1.4187 | 1.6595 | 1.5044 | 1.6319 | 1.4779 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WA_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 148.3216 | 148.3216 | 211.888 | 211.888 | 190.6992 | 190.6992 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 148.3216 | 148.3216 | 211.888 | 211.888 | 190.6992 | 190.6992 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 254.2656 | 254.2656 | 233.0768 | 233.0768 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 296.6432 | 381.3984 | 360.2096 | 360.2096 | 339.0208 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 275.4544 | 254.2656 | 254.2656 | 254.2656 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 275.4544 | 275.4544 | 254.2656 | 254.2656 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 381.3984 | 402.5872 | 381.3984 | 402.5872 | 381.3984 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 614.4752 | 593.2864 | 572.0976 | 572.0976 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 444.9648 | 614.4752 | 593.2864 | 572.0976 | 550.9088 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | 783.9856 | 762.7968 | 720.4192 | 720.4192 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 783.9856 | 1038.2512 | 995.8736 | 995.8736 | 953.496 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 783.9856 | 762.7968 | 741.608 | 762.7968 | 720.4192 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 783.9856 | 762.7968 | 741.608 | 762.7968 | 720.4192 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 953.496 | 1017.0624 | 974.6848 | 974.6848 | 932.3072 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 1017.0624 | 1101.8176 | 1059.44 | 1101.8176 | 1059.44 |  |  |  |  | 2015-03-31
WA_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 953.496 | 1038.2512 | 1038.2512 | 974.6848 | 974.6848 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 275.4544 | 402.5872 | 381.3984 | 402.5872 | 360.2096 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 275.4544 | 402.5872 | 360.2096 | 381.3984 | 339.0208 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 529.72 | 466.1536 | 487.3424 | 423.776 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 487.3424 | 656.8528 | 614.4752 | 656.8528 | 593.2864 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 572.0976 | 508.5312 | 572.0976 | 508.5312 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 572.0976 | 508.5312 | 572.0976 | 508.5312 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 593.2864 | 699.2304 | 635.664 | 678.0416 | 614.4752 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 635.664 | 741.608 | 678.0416 | 741.608 | 656.8528 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.1078 | 0.10687 | 0.15124 | 0.14833 | 0.13426 | 0.13286 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.10614 | 0.10528 | 0.14922 | 0.14645 | 0.13214 | 0.13086 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.14295 | 0.14534 | 0.18462 | 0.18416 | 0.16532 | 0.16474 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.20459 | 0.20504 | 0.26791 | 0.26208 | 0.25163 | 0.24687 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.1945 | 0.19643 | 0.1897 | 0.18513 | 0.17968 | 0.17495 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.19924 | 0.20127 | 0.19478 | 0.19044 | 0.1847 | 0.18015 |  |  |  |  | 2015-03-31
WA_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.26351 | 0.26556 | 0.2845 | 0.27523 | 0.27899 | 0.26967 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.32548 | 0.31914 | 0.43503 | 0.42488 | 0.40858 | 0.39929 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.32252 | 0.31631 | 0.43157 | 0.42166 | 0.40483 | 0.39575 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.43485 | 0.43119 | 0.54897 | 0.53982 | 0.51694 | 0.50548 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.57075 | 0.56314 | 0.72938 | 0.70838 | 0.70432 | 0.68328 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.55328 | 0.54861 | 0.54222 | 0.52556 | 0.5333 | 0.51385 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.55517 | 0.55042 | 0.54452 | 0.52773 | 0.53542 | 0.51581 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.68216 | 0.67445 | 0.71523 | 0.69081 | 0.69362 | 0.66371 |  |  |  |  | 2015-03-31
WA_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.7299 | 0.72135 | 0.7866 | 0.75583 | 0.78463 | 0.75133 |  |  |  |  | 2015-03-31
WA_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67185 | 0.67561 | 0.73484 | 0.73489 | 0.68355 | 0.6842 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.2214 | 0.19541 | 0.29034 | 0.26477 | 0.27829 | 0.24951 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.22134 | 0.19309 | 0.29036 | 0.26103 | 0.27718 | 0.24564 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.27972 | 0.25844 | 0.36913 | 0.32809 | 0.34885 | 0.30783 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.36999 | 0.34736 | 0.47295 | 0.43821 | 0.46233 | 0.42537 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.38955 | 0.35996 | 0.40872 | 0.36289 | 0.40125 | 0.35494 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.39079 | 0.36141 | 0.41023 | 0.36448 | 0.40276 | 0.35631 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.45254 | 0.42235 | 0.49418 | 0.44547 | 0.48082 | 0.42982 |  |  |  |  | 2015-03-31
WA_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.4822 | 0.45273 | 0.5296 | 0.48007 | 0.52077 | 0.47165 |  |  |  |  | 2015-03-31
CT_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6508 | 1.5523 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8119 | 1.6903 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3066 | 1.2581 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5862 | 1.4798 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5091 | 1.4336 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 678.0416 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42667 | 0.39262 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.5206 | 0.47789 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.41695 | 0.40149 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.43953 | 0.40291 | [8 empty] | 2015-03-31
CT_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.47983 | 0.45141 | [8 empty] | 2015-03-31
CT_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 9958.736 | 9619.7152 | [8 empty] | 2015-03-31
CT_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24388.3088 | 24070.4768 | [8 empty] | 2015-03-31
CT_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 198030.5251 | 194386.0515 | [8 empty] | 2015-03-31
CT_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23159.3584 | 21400.688 | [8 empty] | 2015-03-31
CT_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
CT_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
CT_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
CT_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
CT_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
CT_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
CT_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
CT_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
CT_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
CT_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
CT_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
CT_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
CT_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
CT_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
CT_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
CT_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
CT_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
CT_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
CT_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
CT_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
CT_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
CT_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 375.9749 | 370.8924 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 375.9749 | 370.8924 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
CT_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 356.8549 | 352.0254 | [8 empty] | 2015-03-31
CT_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 356.8549 | 352.0254 | [8 empty] | 2015-03-31
CT_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.0161 | 4.9006 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1770.4811 | 873.2545 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 873.2545 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1770.4811 | 1746.5471 | [8 empty] | 2015-03-31
CT_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1008.6607 | 985.4495 | [8 empty] | 2015-03-31
CT_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2065.6141 | 2029.9509 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
CT_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.6915 | 10.3164 | [8 empty] | 2015-03-31
CT_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.06 | 34.6086 | [8 empty] | 2015-03-31
CT_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 278.4744 | 273.3725 | [8 empty] | 2015-03-31
CT_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.3066 | 30.7626 | [8 empty] | 2015-03-31
CT_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.7285 | 42.6542 | [8 empty] | 2015-03-31
CT_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.79309 | 0.77942 | [8 empty] | 2015-03-31
CT_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.965 | 9.821 | [8 empty] | 2015-03-31
CT_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.68381 | 0.66145 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.5509 | 4.7109 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.7109 | [8 empty] | 2015-03-31
CT_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 28.6527 | 28.2654 | [8 empty] | 2015-03-31
CT_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 21.8028 | 21.3011 | [8 empty] | 2015-03-31
CT_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.2594 | 37.5985 | [8 empty] | 2015-03-31
CT_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8306 | 3.8072 | [8 empty] | 2015-03-31
CT_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4747.3567 | 4602.3042 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.6962 | 8.607 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 36.7798 | 35.3577 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2659 | 6.0339 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4493 | 5.1339 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3220.6976 | 3178.32 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12734.4688 | 11632.6512 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2521.4672 | 2415.5232 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2097.6912 | 1949.3696 | [8 empty] | 2015-03-31
CT_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
CT_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
CT_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.6231 | 2.4231 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.1877 | 2.1484 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.6612 | 12.4846 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7734 | 1.6891 | [8 empty] | 2015-03-31
CT_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4746 | 1.3643 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.3509 | 21.8443 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.9352 | 21.4618 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.7567 | 20.0282 | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.1114 | 26.6422 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.211 | 5.2713 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7606.7792 | 6547.3392 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7479.6464 | 6441.3952 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6822.7936 | 6017.6192 | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9344.2608 | 7988.1776 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1864.6144 | 1589.16 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
CT_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | [8 empty] | 2015-03-31
CT_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
CT_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
CT_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
CT_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
CT_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
CT_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
CT_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
CT_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7607.3937 | 6555.1155 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7482.6552 | 6440.3146 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6010.1396 | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
CT_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
CT_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
CT_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | [8 empty] | 2015-03-31
CT_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
CT_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
CT_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5598 | 1.4299 | [8 empty] | 2015-03-31
CT_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 156.8301 | 143.7659 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.1382 | 9.6708 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.9555 | 9.5014 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.9984 | 8.8668 | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.6691 | 11.7055 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.306 | 1.1084 | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
CT_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.39 | 3.1076 | [8 empty] | 2015-03-31
CT_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
CT_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.0295 | 98.1527 | [8 empty] | 2015-03-31
CT_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9727 | 1.8234 | [8 empty] | 2015-03-31
CT_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2322 | 5.0442 | [8 empty] | 2015-03-31
CT_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.4996 | 2.347 | [8 empty] | 2015-03-31
CT_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.1868 | 4.1471 | [8 empty] | 2015-03-31
CT_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
CT_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1567.9712 | 1504.4048 | [8 empty] | 2015-03-31
CT_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 741.608 | 699.2304 | [8 empty] | 2015-03-31
CT_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1483.216 | 1462.0272 | [8 empty] | 2015-03-31
CT_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
CT_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
CT_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
CT_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
CT_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
CT_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
CT_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
CT_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
CT_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
CT_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1002 | 1.0607 | [8 empty] | 2015-03-31
CT_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0558 | 1.0425 | [8 empty] | 2015-03-31
CT_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.5557 | 0.55048 | [8 empty] | 2015-03-31
CT_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.55126 | 0.54618 | [8 empty] | 2015-03-31
CT_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.66794 | 0.66299 | [8 empty] | 2015-03-31
CT_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.86486 | 0.84846 | [8 empty] | 2015-03-31
CT_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.65442 | 0.64241 | [8 empty] | 2015-03-31
CT_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.66675 | 0.65654 | [8 empty] | 2015-03-31
CT_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.91607 | 0.89692 | [8 empty] | 2015-03-31
CT_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5036 | 1.4707 | [8 empty] | 2015-03-31
CT_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.496 | 1.4636 | [8 empty] | 2015-03-31
CT_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8458 | 1.8074 | [8 empty] | 2015-03-31
CT_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2751 | 2.2151 | [8 empty] | 2015-03-31
CT_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7569 | 1.7135 | [8 empty] | 2015-03-31
CT_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7622 | 1.7185 | [8 empty] | 2015-03-31
CT_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2473 | 2.1838 | [8 empty] | 2015-03-31
CT_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4106 | 2.333 | [8 empty] | 2015-03-31
CT_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0449 | 2.0469 | [8 empty] | 2015-03-31
CT_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0402 | 0.90816 | [8 empty] | 2015-03-31
CT_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.041 | 0.89982 | [8 empty] | 2015-03-31
CT_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2834 | 1.1148 | [8 empty] | 2015-03-31
CT_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4867 | 1.3687 | [8 empty] | 2015-03-31
CT_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2639 | 1.1368 | [8 empty] | 2015-03-31
CT_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2672 | 1.1385 | [8 empty] | 2015-03-31
CT_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5167 | 1.3797 | [8 empty] | 2015-03-31
CT_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6197 | 1.4846 | [8 empty] | 2015-03-31
CT_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
CT_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
CT_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
CT_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
CT_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
CT_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
CT_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
CT_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
CT_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
CT_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
CT_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
CT_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
CT_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
CT_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
CT_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | [8 empty] | 2015-03-31
CT_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 317.832 | [8 empty] | 2015-03-31
CT_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
CT_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | [8 empty] | 2015-03-31
CT_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | [8 empty] | 2015-03-31
CT_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | [8 empty] | 2015-03-31
CT_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | [8 empty] | 2015-03-31
CT_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 699.2304 | [8 empty] | 2015-03-31
CT_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | [8 empty] | 2015-03-31
CT_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
CT_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
CT_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 826.3632 | [8 empty] | 2015-03-31
CT_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 911.1184 | [8 empty] | 2015-03-31
CT_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | [8 empty] | 2015-03-31
CT_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | [8 empty] | 2015-03-31
CT_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | [8 empty] | 2015-03-31
CT_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
CT_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2015-03-31
CT_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
CT_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
CT_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | [8 empty] | 2015-03-31
CT_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
CT_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
CT_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.13381 | 0.13086 | [8 empty] | 2015-03-31
CT_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.13236 | 0.12948 | [8 empty] | 2015-03-31
CT_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.16937 | 0.16894 | [8 empty] | 2015-03-31
CT_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.22915 | 0.22371 | [8 empty] | 2015-03-31
CT_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15422 | 0.1508 | [8 empty] | 2015-03-31
CT_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15872 | 0.15545 | [8 empty] | 2015-03-31
CT_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24126 | 0.23387 | [8 empty] | 2015-03-31
CT_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.39065 | 0.37968 | [8 empty] | 2015-03-31
CT_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.38811 | 0.37734 | [8 empty] | 2015-03-31
CT_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.50052 | 0.49077 | [8 empty] | 2015-03-31
CT_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.63228 | 0.61222 | [8 empty] | 2015-03-31
CT_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.44983 | 0.4357 | [8 empty] | 2015-03-31
CT_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.45156 | 0.43733 | [8 empty] | 2015-03-31
CT_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.60149 | 0.58069 | [8 empty] | 2015-03-31
CT_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67011 | 0.64423 | [8 empty] | 2015-03-31
CT_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64738 | 0.64809 | [8 empty] | 2015-03-31
CT_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.27393 | 0.24228 | [8 empty] | 2015-03-31
CT_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27415 | 0.23952 | [8 empty] | 2015-03-31
CT_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.34631 | 0.30658 | [8 empty] | 2015-03-31
CT_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.42167 | 0.3849 | [8 empty] | 2015-03-31
CT_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34818 | 0.30632 | [8 empty] | 2015-03-31
CT_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34928 | 0.3076 | [8 empty] | 2015-03-31
CT_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.42482 | 0.38047 | [8 empty] | 2015-03-31
CT_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.45926 | 0.41459 | [8 empty] | 2015-03-31
IA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.809 | 1.7067 | 1.703 | 1.6137 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9704 | 1.8475 | 1.8892 | 1.8011 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4364 | 1.3816 | 1.3859 | 1.357 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.737 | 1.6342 | 1.6101 | 1.536 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6491 | 1.5683 | 1.5642 | 1.5055 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 614.4752 | 614.4752 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 720.4192 | 678.0416 | 699.2304 | 678.0416 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44254 | 0.40723 | 0.43252 | 0.40131 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.54102 | 0.49673 | 0.53754 | 0.50441 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.45372 | 0.43239 | 0.44227 | 0.43306 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.46057 | 0.42391 | 0.43766 | 0.41104 | [6 empty] | 2015-03-31
IA_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.51523 | 0.48442 | 0.49918 | 0.48014 | [6 empty] | 2015-03-31
IA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10276.568 | 9916.3584 | 10213.0016 | 9831.6032 | [6 empty] | 2015-03-31
IA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25341.8048 | 24960.4064 | 25214.672 | 24854.4624 | [6 empty] | 2015-03-31
IA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 206506.0451 | 201992.8307 | 204450.7315 | 200424.8595 | [6 empty] | 2015-03-31
IA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 24197.6096 | 22248.24 | 23964.5328 | 22099.9184 | [6 empty] | 2015-03-31
IA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IA_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
IA_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
IA_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
IA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
IA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
IA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
IA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
IA_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
IA_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
IA_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
IA_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
IA_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IA_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IA_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
IA_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IA_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IA_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IA_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 420.8115 | 414.7925 | 398.5489 | 393.3367 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 420.8115 | 414.7925 | 398.5489 | 393.3367 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
IA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 399.4076 | 393.7048 | 378.2768 | 373.3282 | [6 empty] | 2015-03-31
IA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 399.4076 | 393.7048 | 378.2768 | 373.3282 | [6 empty] | 2015-03-31
IA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.4909 | 5.3693 | 5.8133 | 5.6756 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1981.6074 | 976.6161 | 1876.6783 | 926.0995 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 976.6161 | 0 | 926.0995 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1981.6074 | 1953.2353 | 1876.6783 | 1852.2688 | [6 empty] | 2015-03-31
IA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1104.1351 | 1079.6844 | 1168.9788 | 1141.2819 | [6 empty] | 2015-03-31
IA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2312.0866 | 2270.2418 | 2189.7221 | 2152.7909 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
IA_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0252 | 10.6369 | 10.9706 | 10.5485 | [6 empty] | 2015-03-31
IA_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.4454 | 35.8786 | 36.2443 | 35.7295 | [6 empty] | 2015-03-31
IA_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 290.4055 | 284.0575 | 287.5209 | 281.856 | [6 empty] | 2015-03-31
IA_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.7764 | 31.9873 | 34.4414 | 31.7642 | [6 empty] | 2015-03-31
IA_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.9935 | 43.916 | 44.3221 | 44.2296 | [6 empty] | 2015-03-31
IA_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.83231 | 0.81588 | 0.84232 | 0.82516 | [6 empty] | 2015-03-31
IA_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.5045 | 10.2431 | 10.6358 | 10.3638 | [6 empty] | 2015-03-31
IA_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.7208 | 0.69512 | 0.72831 | 0.70229 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.6899 | 5.2685 | 10.1244 | 4.996 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.2685 | 0 | 4.996 | [6 empty] | 2015-03-31
IA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 32.0697 | 31.611 | 30.3731 | 29.9759 | [6 empty] | 2015-03-31
IA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 23.8665 | 23.338 | 25.2682 | 24.6695 | [6 empty] | 2015-03-31
IA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 42.822 | 42.0488 | 40.5565 | 39.8738 | [6 empty] | 2015-03-31
IA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.917 | 3.8904 | 3.9117 | 3.8835 | [6 empty] | 2015-03-31
IA_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 5062.8779 | 4900.1385 | 5228.929 | 5049.3595 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.4032 | 9.2849 | 8.9188 | 8.8819 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 41.31 | 39.7848 | 38.3687 | 37.7862 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.8257 | 6.5806 | 6.5542 | 6.3352 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.9857 | 5.6574 | 5.7228 | 5.4171 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3411.3968 | 3347.8304 | 3263.0752 | 3220.6976 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13179.4336 | 12183.56 | 12734.4688 | 11992.8608 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2627.4112 | 2500.2784 | 2627.4112 | 2500.2784 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2182.4464 | 2034.1248 | 2182.4464 | 2012.936 | [6 empty] | 2015-03-31
IA_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | n/a | VFD | [6 empty] | 2015-03-31
IA_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IA_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.2603 | 2.9129 | 4.7048 | 3.2552 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3079 | 2.2665 | 2.2071 | 2.1865 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.1477 | 13.0668 | 13.6649 | 12.8679 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8421 | 1.7528 | 1.834 | 1.7525 | [6 empty] | 2015-03-31
IA_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5343 | 1.4191 | 1.5225 | 1.4133 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.5849 | 22.7499 | 26.2119 | 22.5345 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 26.2336 | 22.5781 | 25.8714 | 22.3301 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.8596 | 21.0809 | 23.5647 | 20.9083 | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.6445 | 27.9022 | 32.0156 | 27.5841 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.6747 | 5.6448 | 6.53 | 5.5591 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7988.1776 | 6822.7936 | 7861.0448 | 6759.2272 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7882.2336 | 6780.416 | 7755.1008 | 6695.6608 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7161.8144 | 6335.4512 | 7077.0592 | 6271.8848 | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9789.2256 | 8369.576 | 9598.5264 | 8284.8208 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2012.936 | 1695.104 | 1949.3696 | 1673.9152 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
IA_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
IA_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IA_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
IA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IA_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
IA_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
IA_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
IA_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
IA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 6826.8619 | 7852.8447 | 6762.2572 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 6775.3307 | 7763.5763 | 6700.8944 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6326.0434 | 6777.6191 | 6274.2368 | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
IA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
IA_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
IA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.6908 | 1.5252 | 1.7447 | 1.5774 | [6 empty] | 2015-03-31
IA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 169.9931 | 153.3473 | 175.4124 | 158.5999 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.6803 | 9.9954 | 11.5164 | 9.9008 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.526 | 9.9199 | 11.3668 | 9.8858 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.4829 | 9.3328 | 10.3534 | 9.2564 | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.3427 | 12.2591 | 14.0664 | 12.1193 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4035 | 1.187 | 1.3731 | 1.1689 | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
IA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.6745 | 3.3147 | 3.7916 | 3.4282 | [6 empty] | 2015-03-31
IA_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
IA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 105.6832 | 97.868 | 105.6843 | 98.1383 | [6 empty] | 2015-03-31
IA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1908 | 2.0735 | 2.1087 | 1.9854 | [6 empty] | 2015-03-31
IA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.4845 | 5.2838 | 5.4586 | 5.2567 | [6 empty] | 2015-03-31
IA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6028 | 2.4463 | 2.5889 | 2.4381 | [6 empty] | 2015-03-31
IA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5136 | 4.473 | 4.3574 | 4.321 | [6 empty] | 2015-03-31
IA_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
IA_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1652.7264 | 1589.16 | 1631.5376 | 1567.9712 | [6 empty] | 2015-03-31
IA_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 741.608 | [6 empty] | 2015-03-31
IA_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1546.7824 | 1525.5936 | 1546.7824 | 1525.5936 | [6 empty] | 2015-03-31
IA_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
IA_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
IA_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
IA_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
IA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
IA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
IA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
IA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | No | No | No | [6 empty] | 2015-03-31
IA_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1532 | 1.111 | 1.1478 | 1.1053 | [6 empty] | 2015-03-31
IA_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0812 | 1.0682 | 1.0801 | 1.0677 | [6 empty] | 2015-03-31
IA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.66095 | 0.65062 | 0.60332 | 0.59248 | [6 empty] | 2015-03-31
IA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.65555 | 0.64555 | 0.59801 | 0.58759 | [6 empty] | 2015-03-31
IA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.80644 | 0.79334 | 0.73999 | 0.72965 | [6 empty] | 2015-03-31
IA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0197 | 1.0006 | 0.95118 | 0.92661 | [6 empty] | 2015-03-31
IA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.74264 | 0.72856 | 0.70591 | 0.68735 | [6 empty] | 2015-03-31
IA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.75618 | 0.74161 | 0.71994 | 0.70201 | [6 empty] | 2015-03-31
IA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0625 | 1.036 | 1.0005 | 0.96639 | [6 empty] | 2015-03-31
IA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7338 | 1.6966 | 1.6296 | 1.5894 | [6 empty] | 2015-03-31
IA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7248 | 1.6882 | 1.6208 | 1.5813 | [6 empty] | 2015-03-31
IA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1799 | 2.1225 | 2.0578 | 1.9988 | [6 empty] | 2015-03-31
IA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6343 | 2.5659 | 2.5072 | 2.4253 | [6 empty] | 2015-03-31
IA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.9675 | 1.9128 | 1.9135 | 1.8497 | [6 empty] | 2015-03-31
IA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.9726 | 1.9181 | 1.9158 | 1.8555 | [6 empty] | 2015-03-31
IA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.5248 | 2.4459 | 2.4637 | 2.3714 | [6 empty] | 2015-03-31
IA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.7481 | 2.6598 | 2.6422 | 2.535 | [6 empty] | 2015-03-31
IA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2138 | 2.2088 | 2.177 | 2.1217 | [6 empty] | 2015-03-31
IA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1735 | 1.0392 | 1.1032 | 0.9705 | [6 empty] | 2015-03-31
IA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1758 | 1.0296 | 1.1059 | 0.96118 | [6 empty] | 2015-03-31
IA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4547 | 1.3031 | 1.3826 | 1.2245 | [6 empty] | 2015-03-31
IA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6834 | 1.5667 | 1.5995 | 1.4819 | [6 empty] | 2015-03-31
IA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.4024 | 1.2632 | 1.3527 | 1.2165 | [6 empty] | 2015-03-31
IA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.4061 | 1.2669 | 1.3569 | 1.2204 | [6 empty] | 2015-03-31
IA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6918 | 1.5386 | 1.642 | 1.4916 | [6 empty] | 2015-03-31
IA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7898 | 1.6469 | 1.7283 | 1.576 | [6 empty] | 2015-03-31
IA_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
IA_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
IA_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IA_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IA_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IA_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IA_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IA_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IA_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IA_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
IA_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
IA_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
IA_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
IA_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
IA_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
IA_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | 339.0208 | 339.0208 | [6 empty] | 2015-03-31
IA_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 211.888 | [6 empty] | 2015-03-31
IA_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 233.0768 | 233.0768 | [6 empty] | 2015-03-31
IA_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | 360.2096 | 360.2096 | [6 empty] | 2015-03-31
IA_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 593.2864 | 593.2864 | 572.0976 | [6 empty] | 2015-03-31
IA_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 572.0976 | [6 empty] | 2015-03-31
IA_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 762.7968 | 762.7968 | 741.608 | [6 empty] | 2015-03-31
IA_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 953.496 | 974.6848 | 932.3072 | [6 empty] | 2015-03-31
IA_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 635.664 | [6 empty] | 2015-03-31
IA_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
IA_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 868.7408 | 911.1184 | 868.7408 | [6 empty] | 2015-03-31
IA_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 995.8736 | 1017.0624 | 974.6848 | [6 empty] | 2015-03-31
IA_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 953.496 | 953.496 | 932.3072 | [6 empty] | 2015-03-31
IA_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
IA_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
IA_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 487.3424 | 508.5312 | 466.1536 | [6 empty] | 2015-03-31
IA_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
IA_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
IA_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 508.5312 | 444.9648 | [6 empty] | 2015-03-31
IA_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
IA_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 635.664 | 678.0416 | 614.4752 | [6 empty] | 2015-03-31
IA_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
IA_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14903 | 0.14563 | 0.14003 | 0.1364 | [6 empty] | 2015-03-31
IA_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14728 | 0.144 | 0.1383 | 0.1348 | [6 empty] | 2015-03-31
IA_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.19135 | 0.18813 | 0.17917 | 0.17605 | [6 empty] | 2015-03-31
IA_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.25855 | 0.25218 | 0.24722 | 0.23889 | [6 empty] | 2015-03-31
IA_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16338 | 0.15892 | 0.16063 | 0.15502 | [6 empty] | 2015-03-31
IA_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16778 | 0.16355 | 0.16531 | 0.15993 | [6 empty] | 2015-03-31
IA_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.26845 | 0.25966 | 0.25978 | 0.24825 | [6 empty] | 2015-03-31
IA_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.42717 | 0.41474 | 0.41472 | 0.40105 | [6 empty] | 2015-03-31
IA_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.42419 | 0.41195 | 0.41177 | 0.39834 | [6 empty] | 2015-03-31
IA_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.55626 | 0.5403 | 0.53835 | 0.52175 | [6 empty] | 2015-03-31
IA_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.70241 | 0.6794 | 0.68552 | 0.6575 | [6 empty] | 2015-03-31
IA_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.47402 | 0.4574 | 0.4774 | 0.45749 | [6 empty] | 2015-03-31
IA_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.47571 | 0.45915 | 0.47938 | 0.45943 | [6 empty] | 2015-03-31
IA_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.64098 | 0.61521 | 0.64397 | 0.61325 | [6 empty] | 2015-03-31
IA_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.73562 | 0.70602 | 0.72643 | 0.68982 | [6 empty] | 2015-03-31
IA_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67394 | 0.67216 | 0.68093 | 0.66638 | [6 empty] | 2015-03-31
IA_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.29547 | 0.26448 | 0.28355 | 0.25317 | [6 empty] | 2015-03-31
IA_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29533 | 0.26131 | 0.28352 | 0.25003 | [6 empty] | 2015-03-31
IA_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.37449 | 0.33814 | 0.36249 | 0.32375 | [6 empty] | 2015-03-31
IA_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.46391 | 0.42594 | 0.44983 | 0.41093 | [6 empty] | 2015-03-31
IA_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.36993 | 0.32398 | 0.36611 | 0.32037 | [6 empty] | 2015-03-31
IA_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.37109 | 0.3252 | 0.36755 | 0.32172 | [6 empty] | 2015-03-31
IA_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.45336 | 0.40367 | 0.45017 | 0.39972 | [6 empty] | 2015-03-31
IA_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.49245 | 0.44471 | 0.4847 | 0.43453 | [6 empty] | 2015-03-31
MA_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6327 | 1.5372 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8139 | 1.6943 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3302 | 1.2757 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5718 | 1.4634 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5024 | 1.4267 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 678.0416 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 550.9088 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42122 | 0.388 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52374 | 0.48056 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.42451 | 0.40711 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.43418 | 0.39713 | [8 empty] | 2015-03-31
MA_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.47396 | 0.44559 | [8 empty] | 2015-03-31
MA_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 9937.5472 | 9577.3376 | [8 empty] | 2015-03-31
MA_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24579.008 | 24218.7984 | [8 empty] | 2015-03-31
MA_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 200785.0691 | 196653.2531 | [8 empty] | 2015-03-31
MA_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23074.6032 | 21294.744 | [8 empty] | 2015-03-31
MA_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
MA_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
MA_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
MA_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
MA_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
MA_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
MA_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
MA_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
MA_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
MA_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
MA_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
MA_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
MA_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
MA_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
MA_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
MA_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
MA_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
MA_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
MA_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
MA_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
MA_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
MA_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 378.7466 | 373.3416 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 378.7466 | 373.3416 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
MA_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 359.488 | 354.3542 | [8 empty] | 2015-03-31
MA_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 359.488 | 354.3542 | [8 empty] | 2015-03-31
MA_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.9041 | 4.7967 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1783.4784 | 879.0209 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 879.0209 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1783.4784 | 1758.1178 | [8 empty] | 2015-03-31
MA_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 986.1532 | 964.5476 | [8 empty] | 2015-03-31
MA_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2080.8304 | 2043.4237 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
MA_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.658 | 10.2824 | [8 empty] | 2015-03-31
MA_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.3346 | 34.8257 | [8 empty] | 2015-03-31
MA_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 282.3505 | 276.5467 | [8 empty] | 2015-03-31
MA_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.1589 | 30.6056 | [8 empty] | 2015-03-31
MA_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.5155 | 42.441 | [8 empty] | 2015-03-31
MA_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.78915 | 0.77529 | [8 empty] | 2015-03-31
MA_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.9173 | 9.7686 | [8 empty] | 2015-03-31
MA_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.67994 | 0.65769 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.6213 | 4.742 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.742 | [8 empty] | 2015-03-31
MA_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 28.864 | 28.452 | [8 empty] | 2015-03-31
MA_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 21.3163 | 20.8492 | [8 empty] | 2015-03-31
MA_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.5415 | 37.8468 | [8 empty] | 2015-03-31
MA_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.825 | 3.8016 | [8 empty] | 2015-03-31
MA_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4832.1016 | 4689.7727 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.8721 | 8.7127 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 38.0668 | 36.021 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.2799 | 6.0479 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4595 | 5.1552 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3326.6416 | 3241.8864 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12988.7344 | 11717.4064 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2542.656 | 2415.5232 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2118.88 | 1970.5584 | [8 empty] | 2015-03-31
MA_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
MA_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
MA_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.3628 | 2.2232 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.248 | 2.1903 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.9387 | 12.5846 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7834 | 1.6992 | [8 empty] | 2015-03-31
MA_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4865 | 1.3771 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.114 | 21.5409 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.7044 | 21.1607 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.5412 | 19.7396 | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 30.7716 | 26.2139 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.1929 | 5.2629 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7543.2128 | 6462.584 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7416.08 | 6356.64 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6759.2272 | 5932.864 | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9238.3168 | 7861.0448 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1864.6144 | 1589.16 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
MA_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | [8 empty] | 2015-03-31
MA_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
MA_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
MA_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
MA_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
MA_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
MA_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
MA_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
MA_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7536.2841 | 6464.0672 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7413.389 | 6349.9655 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6764.249 | 5923.5409 | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MA_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MA_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MA_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | [8 empty] | 2015-03-31
MA_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MA_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MA_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5149 | 1.3936 | [8 empty] | 2015-03-31
MA_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 152.3149 | 140.1189 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.0341 | 9.5365 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.8541 | 9.3681 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.9037 | 8.739 | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.5198 | 11.5173 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3022 | 1.1066 | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
MA_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.2924 | 3.0288 | [8 empty] | 2015-03-31
MA_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MA_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.1446 | 98.7101 | [8 empty] | 2015-03-31
MA_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9997 | 1.8453 | [8 empty] | 2015-03-31
MA_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2738 | 5.0706 | [8 empty] | 2015-03-31
MA_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5083 | 2.3534 | [8 empty] | 2015-03-31
MA_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.1684 | 4.1272 | [8 empty] | 2015-03-31
MA_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2015-03-31
MA_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1589.16 | 1525.5936 | [8 empty] | 2015-03-31
MA_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 699.2304 | [8 empty] | 2015-03-31
MA_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1483.216 | 1462.0272 | [8 empty] | 2015-03-31
MA_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
MA_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
MA_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
MA_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
MA_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MA_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
MA_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MA_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
MA_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
MA_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1089 | 1.0662 | [8 empty] | 2015-03-31
MA_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.051 | 1.0375 | [8 empty] | 2015-03-31
MA_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.57799 | 0.56645 | [8 empty] | 2015-03-31
MA_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.57339 | 0.56219 | [8 empty] | 2015-03-31
MA_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.71021 | 0.70242 | [8 empty] | 2015-03-31
MA_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.88537 | 0.86529 | [8 empty] | 2015-03-31
MA_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.67007 | 0.6577 | [8 empty] | 2015-03-31
MA_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.68371 | 0.67118 | [8 empty] | 2015-03-31
MA_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.94173 | 0.91769 | [8 empty] | 2015-03-31
MA_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5551 | 1.5151 | [8 empty] | 2015-03-31
MA_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5475 | 1.508 | [8 empty] | 2015-03-31
MA_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.9427 | 1.9046 | [8 empty] | 2015-03-31
MA_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3391 | 2.275 | [8 empty] | 2015-03-31
MA_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8039 | 1.7546 | [8 empty] | 2015-03-31
MA_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8068 | 1.7597 | [8 empty] | 2015-03-31
MA_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3221 | 2.2534 | [8 empty] | 2015-03-31
MA_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4857 | 2.4037 | [8 empty] | 2015-03-31
MA_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.067 | 2.0617 | [8 empty] | 2015-03-31
MA_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.05 | 0.92494 | [8 empty] | 2015-03-31
MA_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0509 | 0.9166 | [8 empty] | 2015-03-31
MA_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3083 | 1.1656 | [8 empty] | 2015-03-31
MA_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5107 | 1.3966 | [8 empty] | 2015-03-31
MA_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2813 | 1.1555 | [8 empty] | 2015-03-31
MA_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2849 | 1.1591 | [8 empty] | 2015-03-31
MA_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5517 | 1.4154 | [8 empty] | 2015-03-31
MA_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6446 | 1.5106 | [8 empty] | 2015-03-31
MA_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MA_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
MA_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MA_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MA_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MA_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MA_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MA_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MA_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MA_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MA_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
MA_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MA_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
MA_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
MA_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | [8 empty] | 2015-03-31
MA_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 317.832 | [8 empty] | 2015-03-31
MA_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | [8 empty] | 2015-03-31
MA_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | [8 empty] | 2015-03-31
MA_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | [8 empty] | 2015-03-31
MA_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 550.9088 | [8 empty] | 2015-03-31
MA_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | [8 empty] | 2015-03-31
MA_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 720.4192 | [8 empty] | 2015-03-31
MA_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | [8 empty] | 2015-03-31
MA_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | [8 empty] | 2015-03-31
MA_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | [8 empty] | 2015-03-31
MA_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | [8 empty] | 2015-03-31
MA_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 911.1184 | [8 empty] | 2015-03-31
MA_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | [8 empty] | 2015-03-31
MA_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | [8 empty] | 2015-03-31
MA_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | [8 empty] | 2015-03-31
MA_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | [8 empty] | 2015-03-31
MA_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2015-03-31
MA_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | [8 empty] | 2015-03-31
MA_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | [8 empty] | 2015-03-31
MA_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | [8 empty] | 2015-03-31
MA_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
MA_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MA_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.13606 | 0.13232 | [8 empty] | 2015-03-31
MA_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.13458 | 0.13096 | [8 empty] | 2015-03-31
MA_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.17858 | 0.17676 | [8 empty] | 2015-03-31
MA_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23058 | 0.224 | [8 empty] | 2015-03-31
MA_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15875 | 0.15481 | [8 empty] | 2015-03-31
MA_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16322 | 0.1595 | [8 empty] | 2015-03-31
MA_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24374 | 0.2359 | [8 empty] | 2015-03-31
MA_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.39677 | 0.38359 | [8 empty] | 2015-03-31
MA_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.39426 | 0.38128 | [8 empty] | 2015-03-31
MA_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.52128 | 0.50866 | [8 empty] | 2015-03-31
MA_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.638 | 0.61499 | [8 empty] | 2015-03-31
MA_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.46112 | 0.44593 | [8 empty] | 2015-03-31
MA_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.46289 | 0.44762 | [8 empty] | 2015-03-31
MA_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.61814 | 0.59572 | [8 empty] | 2015-03-31
MA_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67797 | 0.651 | [8 empty] | 2015-03-31
MA_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64159 | 0.63972 | [8 empty] | 2015-03-31
MA_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.27433 | 0.24183 | [8 empty] | 2015-03-31
MA_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27461 | 0.2391 | [8 empty] | 2015-03-31
MA_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.3496 | 0.31557 | [8 empty] | 2015-03-31
MA_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.42128 | 0.3836 | [8 empty] | 2015-03-31
MA_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.35117 | 0.30987 | [8 empty] | 2015-03-31
MA_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.35237 | 0.31104 | [8 empty] | 2015-03-31
MA_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.43054 | 0.38639 | [8 empty] | 2015-03-31
MA_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46075 | 0.41667 | [8 empty] | 2015-03-31
MI_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6408 | 1.545 | 1.5405 | 1.4552 | 1.419 | 1.3243 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8361 | 1.7265 | 1.7898 | 1.6954 | 1.684 | 1.6286 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3716 | 1.32 | 1.3154 | 1.2927 | 1.2778 | 1.3255 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5588 | 1.4557 | 1.4379 | 1.3646 | 1.2925 | 1.2103 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5471 | 1.4595 | 1.4903 | 1.4383 | 1.4394 | 1.4548 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 593.2864 | 550.9088 | 572.0976 | 529.72 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 762.7968 | 720.4192 | 741.608 | 720.4192 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 593.2864 | 572.0976 | 572.0976 | 593.2864 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 593.2864 | 550.9088 | 550.9088 | 508.5312 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 678.0416 | 656.8528 | 656.8528 | 656.8528 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.43369 | 0.39981 | 0.42034 | 0.39033 | 0.40797 | 0.37361 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.53476 | 0.49355 | 0.53955 | 0.50384 | 0.53205 | 0.51065 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.4377 | 0.42124 | 0.41978 | 0.41253 | 0.40776 | 0.423 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.43743 | 0.40294 | 0.41369 | 0.38898 | 0.38832 | 0.35803 |  |  |  |  | 2015-03-31
MI_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.49371 | 0.46576 | 0.47558 | 0.45899 | 0.45935 | 0.46425 |  |  |  |  | 2015-03-31
MI_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10191.8128 | 9831.6032 | 10001.1136 | 9619.7152 | 9768.0368 | 9407.8272 |  |  |  |  | 2015-03-31
MI_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24451.8752 | 24134.0432 | 24176.4208 | 23879.7776 | 23922.1552 | 23985.7216 |  |  |  |  | 2015-03-31
MI_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 196250.6659 | 192563.8147 | 193962.2755 | 190487.3123 | 191440.8083 | 192309.5491 |  |  |  |  | 2015-03-31
MI_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23286.4912 | 21506.632 | 23011.0368 | 21294.744 | 22460.128 | 21252.3664 |  |  |  |  | 2015-03-31
MI_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
MI_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
MI_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | Yes | No |  |  |  |  | 2015-03-31
MI_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
MI_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
MI_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
MI_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
MI_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
MI_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
MI_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
MI_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
MI_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
MI_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
MI_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | No | Yes |  |  |  |  | 2015-03-31
MI_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
MI_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
MI_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
MI_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 374.0212 | 369.0476 | 351.8658 | 347.0547 | 326.6244 | 325.677 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 374.0212 | 369.0476 | 351.8658 | 347.0547 | 326.6244 | 325.677 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal | Centrifugal |  |  |  |  | 2015-03-31
MI_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 355.0025 | 350.2789 | 333.9776 | 329.3995 | 310.0152 | 309.1155 |  |  |  |  | 2015-03-31
MI_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 355.0025 | 350.2789 | 333.9776 | 329.3995 | 310.0152 | 309.1155 |  |  |  |  | 2015-03-31
MI_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.2277 | 5.1082 | 5.3615 | 5.2243 | 5.5732 | 5.448 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1761.2879 | 868.9115 | 1656.8343 | 817.1285 | 1538.0535 | 766.7958 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 868.9115 | 0 | 817.1285 | 0 | 766.7958 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1761.2879 | 1737.8294 | 1656.8343 | 1634.3268 | 1538.0535 | 1533.5917 |  |  |  |  | 2015-03-31
MI_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1051.222 | 1027.1834 | 1078.1279 | 1050.5261 | 1120.6828 | 1095.5189 |  |  |  |  | 2015-03-31
MI_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2054.9944 | 2019.9652 | 1933.2639 | 1899.5027 | 1794.5736 | 1782.5273 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
MI_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.9279 | 10.5453 | 10.7383 | 10.3262 | 10.4912 | 10.0931 |  |  |  |  | 2015-03-31
MI_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.1637 | 34.6942 | 34.7686 | 34.3183 | 34.393 | 34.4974 |  |  |  |  | 2015-03-31
MI_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 275.9972 | 270.7948 | 272.7568 | 267.8855 | 269.2333 | 270.4313 |  |  |  |  | 2015-03-31
MI_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.4782 | 30.9109 | 33.0939 | 30.6244 | 32.2773 | 30.5512 |  |  |  |  | 2015-03-31
MI_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.796 | 43.7196 | 43.51 | 43.4197 | 43.4703 | 43.381 |  |  |  |  | 2015-03-31
MI_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.82449 | 0.80837 | 0.82325 | 0.80668 | 0.82474 | 0.83029 |  |  |  |  | 2015-03-31
MI_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.39 | 10.1336 | 10.3848 | 10.123 | 10.4049 | 10.5105 |  |  |  |  | 2015-03-31
MI_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.71069 | 0.6864 | 0.70907 | 0.68475 | 0.70845 | 0.70738 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.5013 | 4.6875 | 8.9385 | 4.4081 | 8.2973 | 4.1366 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.6875 | 0 | 4.4081 | 0 | 4.1366 |  |  |  |  | 2015-03-31
MI_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 28.5038 | 28.1248 | 26.8154 | 26.4488 | 24.8918 | 24.8196 |  |  |  |  | 2015-03-31
MI_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.7228 | 22.2032 | 23.3043 | 22.7077 | 24.2242 | 23.6803 |  |  |  |  | 2015-03-31
MI_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.0606 | 37.4115 | 35.8061 | 35.182 | 33.2375 | 33.0149 |  |  |  |  | 2015-03-31
MI_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8753 | 3.8497 | 3.8526 | 3.8251 | 3.8313 | 3.8327 |  |  |  |  | 2015-03-31
MI_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4843.6459 | 4689.5279 | 4835.9499 | 4676.1262 | 4876.5442 | 4746.6616 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.4206 | 8.3973 | 7.986 | 7.9767 | 7.5797 | 7.6078 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 36.1477 | 35.6862 | 33.4906 | 33.0465 | 31.4443 | 31.0712 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3087 | 6.0777 | 6.0937 | 5.8914 | 5.7225 | 5.6699 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.4825 | 5.1856 | 5.2732 | 4.989 | 4.9064 | 4.7798 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3072.376 | 3072.376 | 2966.432 | 2987.6208 | 2860.488 | 2881.6768 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12268.3152 | 11632.6512 | 11950.4832 | 11357.1968 | 11611.4624 | 11145.3088 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2563.8448 | 2436.712 | 2563.8448 | 2457.9008 | 2521.4672 | 2500.2784 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2118.88 | 1970.5584 | 2118.88 | 1970.5584 | 2076.5024 | 2012.936 |  |  |  |  | 2015-03-31
MI_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
MI_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.973 | 2.6916 | 4.1737 | 2.8474 | 4.5307 | 3.1223 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.0823 | 2.0841 | 2.0831 | 2.0883 | 1.9978 | 2.0184 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.1573 | 12.486 | 12.8188 | 12.1798 | 12.4527 | 11.9668 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7923 | 1.71 | 1.7975 | 1.7218 | 1.7706 | 1.7505 |  |  |  |  | 2015-03-31
MI_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4868 | 1.3779 | 1.4883 | 1.3864 | 1.457 | 1.4091 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.6306 | 22.1068 | 25.3837 | 21.9133 | 24.5477 | 21.8135 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.2524 | 21.8373 | 25.0243 | 21.6055 | 24.1902 | 21.4222 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.0392 | 20.496 | 22.8708 | 20.3548 | 22.1471 | 20.2061 |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.4313 | 27.1178 | 29.9672 | 26.636 | 26.7161 | 24.0906 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 14.9958 | 14.9958 | 14.9958 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.4325 | 5.4961 | 6.2436 | 5.3441 | 6.2217 | 5.276 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 | 10.5074 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7691.5344 | 6632.0944 | 7606.7792 | 6568.528 | 7373.7024 | 6547.3392 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7585.5904 | 6547.3392 | 7500.8352 | 6483.7728 | 7267.7584 | 6420.2064 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6907.5488 | 6144.752 | 6865.1712 | 6102.3744 | 6653.2832 | 6059.9968 |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9429.016 | 8136.4992 | 9238.3168 | 7988.1776 | 8920.4848 | 7564.4016 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 4492.0256 | 4492.0256 | 4492.0256 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1928.1808 | 1652.7264 | 1864.6144 | 1610.3488 | 1949.3696 | 1589.16 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
MI_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | n/a | n/a |  |  |  |  | 2015-03-31
MI_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
MI_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
MI_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7691.3225 | 6633.8955 | 7617.2465 | 6575.817 | 7366.3499 | 6545.8772 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7577.8141 | 6553.0178 | 7509.3743 | 6483.455 | 7259.0922 | 6428.4489 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6150.5154 | 6777.6191 | 6108.1378 | 6645.9943 | 6063.5141 |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | 2584.9912 | 2584.9912 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
MI_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
MI_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.6013 | 1.4625 | 1.6312 | 1.4908 | 1.6661 | 1.5223 |  |  |  |  | 2015-03-31
MI_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 160.9981 | 147.0469 | 164.0096 | 149.8898 | 167.5189 | 153.0605 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.261 | 9.787 | 11.1526 | 9.7013 | 10.7853 | 9.6571 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.0949 | 9.6677 | 10.9946 | 9.565 | 10.6282 | 9.4839 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.1225 | 9.0739 | 10.0485 | 9.0113 | 9.8048 | 8.9455 |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.8096 | 11.9145 | 13.5385 | 11.7028 | 13.0616 | 11.0826 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 3.0475 | 3.0475 | 3.0475 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3526 | 1.1557 | 1.3129 | 1.1237 | 1.3649 | 1.1094 |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
MI_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.4801 | 3.1785 | 3.5452 | 3.2399 | 3.621 | 3.3085 |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
MI_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 103.2799 | 96.8865 | 103.4331 | 97.2178 | 103.6488 | 96.7751 |  |  |  |  | 2015-03-31
MI_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.003 | 1.8829 | 1.8947 | 1.7698 | 1.776 | 1.5906 |  |  |  |  | 2015-03-31
MI_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3414 | 5.1456 | 5.1465 | 5.0101 | 4.7377 | 4.5369 |  |  |  |  | 2015-03-31
MI_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5409 | 2.3879 | 2.4842 | 2.3365 | 2.4443 | 2.2576 |  |  |  |  | 2015-03-31
MI_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.205 | 4.1661 | 4.0445 | 4.0089 | 3.8251 | 3.802 |  |  |  |  | 2015-03-31
MI_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 635.664 | 678.0416 | 614.4752 | 678.0416 | 593.2864 |  |  |  |  | 2015-03-31
MI_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1610.3488 | 1546.7824 | 1567.9712 | 1504.4048 | 1525.5936 | 1440.8384 |  |  |  |  | 2015-03-31
MI_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 741.608 | 699.2304 | 741.608 | 678.0416 |  |  |  |  | 2015-03-31
MI_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1504.4048 | 1483.216 | 1504.4048 | 1504.4048 |  |  |  |  | 2015-03-31
MI_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
MI_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
MI_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
MI_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
MI_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
MI_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
MI_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
MI_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1232 | 1.082 | 1.0946 | 1.0544 | 1.0724 | 1.0284 |  |  |  |  | 2015-03-31
MI_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0674 | 1.0545 | 1.0572 | 1.0572 | 1.0548 | 1.0468 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.55311 | 0.5465 | 0.49475 | 0.48748 | 0.41587 | 0.4245 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.54804 | 0.54179 | 0.48974 | 0.48285 | 0.41117 | 0.41936 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.69815 | 0.69516 | 0.62299 | 0.61546 | 0.52153 | 0.55012 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.882 | 0.86918 | 0.80697 | 0.78945 | 0.68578 | 0.71712 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.66455 | 0.65399 | 0.62683 | 0.61303 | 0.53929 | 0.56753 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.67765 | 0.66714 | 0.64 | 0.62677 | 0.55308 | 0.58137 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.94367 | 0.92358 | 0.87713 | 0.84947 | 0.75128 | 0.78837 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.493 | 1.4653 | 1.3783 | 1.3472 | 1.2253 | 1.2379 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4846 | 1.4576 | 1.3699 | 1.3395 | 1.2172 | 1.2291 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.9303 | 1.8898 | 1.7639 | 1.7293 | 1.559 | 1.6225 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3126 | 2.2598 | 2.1594 | 2.0951 | 1.9063 | 1.9758 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7875 | 1.7454 | 1.725 | 1.6725 | 1.5547 | 1.6143 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7933 | 1.7509 | 1.7308 | 1.6778 | 1.5601 | 1.62 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2993 | 2.2359 | 2.197 | 2.1186 | 1.9493 | 2.039 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4729 | 2.3998 | 2.3475 | 2.2558 | 2.0949 | 2.1823 |  |  |  |  | 2015-03-31
MI_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0439 | 2.0385 | 2.0249 | 2.0133 | 1.9457 | 1.9998 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0179 | 0.90106 | 0.94031 | 0.82681 | 0.82531 | 0.73921 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0287 | 0.89644 | 0.95103 | 0.81797 | 0.83206 | 0.72905 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2833 | 1.1569 | 1.1838 | 1.0513 | 0.99698 | 0.96523 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4948 | 1.396 | 1.3963 | 1.2948 | 1.2362 | 1.2065 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2738 | 1.1506 | 1.2279 | 1.1026 | 1.1081 | 1.0431 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2776 | 1.1546 | 1.2316 | 1.1069 | 1.1117 | 1.0478 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5405 | 1.4083 | 1.472 | 1.3359 | 1.3094 | 1.262 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6185 | 1.4886 | 1.5438 | 1.4108 | 1.375 | 1.3393 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
MI_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | 148.3216 | 169.5104 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | 148.3216 | 148.3216 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 233.0768 | 233.0768 | 233.0768 | 190.6992 | 211.888 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | 317.832 | 317.832 | 275.4544 | 296.6432 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | 190.6992 | 211.888 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 233.0768 | 211.888 | 211.888 | 211.888 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 339.0208 | 339.0208 | 339.0208 | 296.6432 | 317.832 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 529.72 | 487.3424 | 508.5312 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 508.5312 | 487.3424 | 508.5312 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 720.4192 | 699.2304 | 678.0416 | 635.664 | 678.0416 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | 889.9296 | 868.7408 | 805.1744 | 847.552 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 635.664 | 656.8528 | 635.664 | 614.4752 | 635.664 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 656.8528 | 635.664 | 614.4752 | 656.8528 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 868.7408 | 826.3632 | 805.1744 | 847.552 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 953.496 | 974.6848 | 932.3072 | 889.9296 | 932.3072 |  |  |  |  | 2015-03-31
MI_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | 911.1184 | 911.1184 | 868.7408 | 889.9296 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 360.2096 | 317.832 | 339.0208 | 296.6432 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 360.2096 | 317.832 | 339.0208 | 296.6432 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 466.1536 | 423.776 | 423.776 | 402.5872 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 593.2864 | 529.72 | 529.72 | 529.72 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | 487.3424 | 444.9648 | 466.1536 | 423.776 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 508.5312 | 444.9648 | 466.1536 | 444.9648 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 593.2864 | 529.72 | 550.9088 | 529.72 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 656.8528 | 593.2864 | 593.2864 | 572.0976 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.13375 | 0.13151 | 0.1256 | 0.12319 | 0.10999 | 0.1129 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.13208 | 0.12997 | 0.12394 | 0.12166 | 0.10842 | 0.11117 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.17331 | 0.17244 | 0.16096 | 0.15949 | 0.13937 | 0.14954 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23697 | 0.2326 | 0.22537 | 0.21935 | 0.19705 | 0.20803 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15583 | 0.15241 | 0.15435 | 0.14968 | 0.1383 | 0.14785 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16023 | 0.15681 | 0.15882 | 0.15435 | 0.14299 | 0.15269 |  |  |  |  | 2015-03-31
MI_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.25357 | 0.24673 | 0.24533 | 0.23583 | 0.21672 | 0.22972 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.39237 | 0.38288 | 0.37974 | 0.36928 | 0.35273 | 0.35707 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.38955 | 0.38027 | 0.37689 | 0.36666 | 0.34993 | 0.354 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.51431 | 0.50412 | 0.4926 | 0.48076 | 0.45238 | 0.47471 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.65021 | 0.63205 | 0.63063 | 0.60837 | 0.57761 | 0.60212 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.45719 | 0.44322 | 0.46208 | 0.44444 | 0.43645 | 0.45702 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.45915 | 0.44507 | 0.46405 | 0.44625 | 0.43834 | 0.45901 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.61294 | 0.59178 | 0.61159 | 0.58511 | 0.56477 | 0.5958 |  |  |  |  | 2015-03-31
MI_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.69901 | 0.67392 | 0.68946 | 0.65774 | 0.63631 | 0.6671 |  |  |  |  | 2015-03-31
MI_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64951 | 0.64804 | 0.64617 | 0.64248 | 0.62091 | 0.63819 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.27213 | 0.2433 | 0.26039 | 0.23269 | 0.23731 | 0.21738 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27177 | 0.24035 | 0.25998 | 0.22968 | 0.23637 | 0.21385 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.34482 | 0.31338 | 0.32915 | 0.29659 | 0.2946 | 0.28576 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.43151 | 0.3974 | 0.41676 | 0.38152 | 0.38043 | 0.36987 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.35235 | 0.31084 | 0.3519 | 0.3094 | 0.3304 | 0.30786 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.35364 | 0.31211 | 0.35318 | 0.31078 | 0.33166 | 0.30944 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.43114 | 0.38671 | 0.42665 | 0.38046 | 0.39366 | 0.37723 |  |  |  |  | 2015-03-31
MI_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46519 | 0.42234 | 0.4589 | 0.41324 | 0.42258 | 0.41007 |  |  |  |  | 2015-03-31
NE_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.8112 | 1.7069 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9939 | 1.869 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4481 | 1.3911 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.7616 | 1.6502 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6629 | 1.5792 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 572.0976 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 762.7968 | 699.2304 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 741.608 | 699.2304 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44444 | 0.40877 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.54625 | 0.5007 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.45729 | 0.43518 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.46756 | 0.42964 | [8 empty] | 2015-03-31
NE_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.5204 | 0.4886 | [8 empty] | 2015-03-31
NE_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10276.568 | 9916.3584 | [8 empty] | 2015-03-31
NE_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25341.8048 | 24939.2176 | [8 empty] | 2015-03-31
NE_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 206378.9123 | 201759.7539 | [8 empty] | 2015-03-31
NE_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 24345.9312 | 22375.3728 | [8 empty] | 2015-03-31
NE_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
NE_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
NE_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
NE_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
NE_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
NE_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
NE_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
NE_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
NE_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
NE_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
NE_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
NE_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
NE_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
NE_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
NE_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
NE_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
NE_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
NE_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
NE_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
NE_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
NE_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
NE_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 417.5502 | 411.5596 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 417.5502 | 411.5596 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
NE_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 396.3114 | 390.6351 | [8 empty] | 2015-03-31
NE_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 396.3114 | 390.6351 | [8 empty] | 2015-03-31
NE_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.4579 | 5.338 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1966.2326 | 969.0048 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 969.0048 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1966.2326 | 1938.019 | [8 empty] | 2015-03-31
NE_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1097.5097 | 1073.3966 | [8 empty] | 2015-03-31
NE_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2294.1758 | 2252.6479 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
NE_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0337 | 10.6452 | [8 empty] | 2015-03-31
NE_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.4482 | 35.867 | [8 empty] | 2015-03-31
NE_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 290.2161 | 283.7233 | [8 empty] | 2015-03-31
NE_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 35.0135 | 32.1703 | [8 empty] | 2015-03-31
NE_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 44.032 | 43.9544 | [8 empty] | 2015-03-31
NE_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.83454 | 0.81766 | [8 empty] | 2015-03-31
NE_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.5402 | 10.2714 | [8 empty] | 2015-03-31
NE_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.72366 | 0.69759 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.6071 | 5.2274 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.2274 | [8 empty] | 2015-03-31
NE_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 31.8212 | 31.3646 | [8 empty] | 2015-03-31
NE_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 23.7233 | 23.2021 | [8 empty] | 2015-03-31
NE_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 42.4901 | 41.7211 | [8 empty] | 2015-03-31
NE_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.9168 | 3.8902 | [8 empty] | 2015-03-31
NE_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 5043.8571 | 4881.8115 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.2837 | 9.1784 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 40.5295 | 39.1829 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.89 | 6.6359 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 6.0439 | 5.7046 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3411.3968 | 3347.8304 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13073.4896 | 12162.3712 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2648.6 | 2521.4672 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2203.6352 | 2034.1248 | [8 empty] | 2015-03-31
NE_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
NE_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
NE_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.2257 | 2.8862 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.3045 | 2.268 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.0331 | 13.0472 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8525 | 1.7608 | [8 empty] | 2015-03-31
NE_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5448 | 1.4271 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.8601 | 22.9612 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 26.5232 | 22.8357 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 24.097 | 21.2837 | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.9568 | 28.1426 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.7366 | 5.6914 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8051.744 | 6886.36 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7966.9888 | 6843.9824 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7225.3808 | 6377.8288 | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9895.1696 | 8454.3312 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2012.936 | 1716.2928 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
NE_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
NE_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
NE_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
NE_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
NE_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
NE_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
NE_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
NE_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
NE_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 6890.2799 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 6852.6063 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6386.8764 | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
NE_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
NE_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
NE_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | [8 empty] | 2015-03-31
NE_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
NE_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
NE_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.695 | 1.5251 | [8 empty] | 2015-03-31
NE_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 170.4211 | 153.3386 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.8012 | 10.0882 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.6532 | 10.0331 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.5872 | 9.4226 | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.4799 | 12.3647 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4165 | 1.1968 | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
NE_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.6838 | 3.3145 | [8 empty] | 2015-03-31
NE_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
NE_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 106.0762 | 97.8577 | [8 empty] | 2015-03-31
NE_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.2377 | 2.1247 | [8 empty] | 2015-03-31
NE_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.5678 | 5.3647 | [8 empty] | 2015-03-31
NE_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6321 | 2.475 | [8 empty] | 2015-03-31
NE_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.5649 | 4.5234 | [8 empty] | 2015-03-31
NE_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 720.4192 | 656.8528 | [8 empty] | 2015-03-31
NE_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1673.9152 | 1610.3488 | [8 empty] | 2015-03-31
NE_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | [8 empty] | 2015-03-31
NE_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1546.7824 | 1525.5936 | [8 empty] | 2015-03-31
NE_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
NE_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
NE_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
NE_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
NE_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
NE_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
NE_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
NE_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
NE_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1708 | 1.128 | [8 empty] | 2015-03-31
NE_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0869 | 1.0737 | [8 empty] | 2015-03-31
NE_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.6708 | 0.65993 | [8 empty] | 2015-03-31
NE_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.66529 | 0.65476 | [8 empty] | 2015-03-31
NE_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.82661 | 0.81114 | [8 empty] | 2015-03-31
NE_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 1.0437 | 1.0233 | [8 empty] | 2015-03-31
NE_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.75817 | 0.74155 | [8 empty] | 2015-03-31
NE_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.77034 | 0.75545 | [8 empty] | 2015-03-31
NE_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.087 | 1.0587 | [8 empty] | 2015-03-31
NE_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.7588 | 1.7202 | [8 empty] | 2015-03-31
NE_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.7497 | 1.7117 | [8 empty] | 2015-03-31
NE_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.2267 | 2.1754 | [8 empty] | 2015-03-31
NE_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.6934 | 2.6216 | [8 empty] | 2015-03-31
NE_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 2.0061 | 1.9515 | [8 empty] | 2015-03-31
NE_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 2.0117 | 1.9566 | [8 empty] | 2015-03-31
NE_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.5955 | 2.5067 | [8 empty] | 2015-03-31
NE_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.8074 | 2.7144 | [8 empty] | 2015-03-31
NE_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2154 | 2.2096 | [8 empty] | 2015-03-31
NE_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.2045 | 1.061 | [8 empty] | 2015-03-31
NE_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.207 | 1.0515 | [8 empty] | 2015-03-31
NE_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.5056 | 1.3398 | [8 empty] | 2015-03-31
NE_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.7259 | 1.609 | [8 empty] | 2015-03-31
NE_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.4331 | 1.2894 | [8 empty] | 2015-03-31
NE_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.4366 | 1.2932 | [8 empty] | 2015-03-31
NE_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.742 | 1.5837 | [8 empty] | 2015-03-31
NE_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.8392 | 1.6865 | [8 empty] | 2015-03-31
NE_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
NE_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
NE_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
NE_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
NE_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
NE_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
NE_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
NE_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
NE_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
NE_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
NE_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
NE_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
NE_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
NE_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
NE_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | [8 empty] | 2015-03-31
NE_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | [8 empty] | 2015-03-31
NE_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | [8 empty] | 2015-03-31
NE_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | [8 empty] | 2015-03-31
NE_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 381.3984 | [8 empty] | 2015-03-31
NE_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | [8 empty] | 2015-03-31
NE_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | [8 empty] | 2015-03-31
NE_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 783.9856 | [8 empty] | 2015-03-31
NE_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 974.6848 | [8 empty] | 2015-03-31
NE_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 656.8528 | [8 empty] | 2015-03-31
NE_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 656.8528 | [8 empty] | 2015-03-31
NE_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 889.9296 | [8 empty] | 2015-03-31
NE_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 1017.0624 | [8 empty] | 2015-03-31
NE_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 953.496 | [8 empty] | 2015-03-31
NE_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | [8 empty] | 2015-03-31
NE_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | [8 empty] | 2015-03-31
NE_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 487.3424 | [8 empty] | 2015-03-31
NE_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 614.4752 | [8 empty] | 2015-03-31
NE_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | [8 empty] | 2015-03-31
NE_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | [8 empty] | 2015-03-31
NE_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
NE_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 635.664 | [8 empty] | 2015-03-31
NE_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
NE_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15309 | 0.14951 | [8 empty] | 2015-03-31
NE_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15131 | 0.14785 | [8 empty] | 2015-03-31
NE_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.19673 | 0.19305 | [8 empty] | 2015-03-31
NE_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.26599 | 0.25918 | [8 empty] | 2015-03-31
NE_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16685 | 0.16208 | [8 empty] | 2015-03-31
NE_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.17124 | 0.16655 | [8 empty] | 2015-03-31
NE_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.27689 | 0.26752 | [8 empty] | 2015-03-31
NE_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.4363 | 0.42341 | [8 empty] | 2015-03-31
NE_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.4333 | 0.42061 | [8 empty] | 2015-03-31
NE_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.57011 | 0.55312 | [8 empty] | 2015-03-31
NE_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.71939 | 0.69535 | [8 empty] | 2015-03-31
NE_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.48253 | 0.465 | [8 empty] | 2015-03-31
NE_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.48435 | 0.46668 | [8 empty] | 2015-03-31
NE_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.6563 | 0.62913 | [8 empty] | 2015-03-31
NE_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.75446 | 0.72339 | [8 empty] | 2015-03-31
NE_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67465 | 0.67258 | [8 empty] | 2015-03-31
NE_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.30392 | 0.27132 | [8 empty] | 2015-03-31
NE_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.30374 | 0.26818 | [8 empty] | 2015-03-31
NE_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.38694 | 0.3468 | [8 empty] | 2015-03-31
NE_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.47689 | 0.43755 | [8 empty] | 2015-03-31
NE_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.37647 | 0.3295 | [8 empty] | 2015-03-31
NE_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.37763 | 0.33068 | [8 empty] | 2015-03-31
NE_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.46399 | 0.41325 | [8 empty] | 2015-03-31
NE_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.50456 | 0.45555 | [8 empty] | 2015-03-31
NH_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6013 | 1.5044 | 1.5264 | 1.4401 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7976 | 1.6758 | 1.7028 | 1.6085 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3286 | 1.2789 | 1.261 | 1.2405 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5346 | 1.4258 | 1.4492 | 1.3658 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5187 | 1.4302 | 1.4684 | 1.4141 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 593.2864 | 550.9088 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 699.2304 | 720.4192 | 678.0416 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 593.2864 | 550.9088 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 635.664 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42603 | 0.3923 | 0.41664 | 0.38646 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.53272 | 0.48954 | 0.51265 | 0.47852 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.42399 | 0.40813 | 0.40241 | 0.39586 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.43538 | 0.39858 | 0.41778 | 0.39033 | [6 empty] | 2015-03-31
NH_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.48463 | 0.45642 | 0.46861 | 0.45128 | [6 empty] | 2015-03-31
NH_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10001.1136 | 9640.904 | 9895.1696 | 9513.7712 | [6 empty] | 2015-03-31
NH_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24536.6304 | 24218.7984 | 24261.176 | 23964.5328 | [6 empty] | 2015-03-31
NH_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 199768.0067 | 195996.4003 | 196377.7987 | 192987.5907 | [6 empty] | 2015-03-31
NH_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23265.3024 | 21485.4432 | 22989.848 | 21273.5552 | [6 empty] | 2015-03-31
NH_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NH_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
NH_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
NH_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
NH_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
NH_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
NH_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
NH_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
NH_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
NH_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
NH_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
NH_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
NH_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NH_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NH_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NH_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
NH_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
NH_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
NH_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NH_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NH_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NH_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 362.7695 | 357.5039 | 347.6593 | 342.7773 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 362.7695 | 357.5039 | 347.6593 | 342.7773 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
NH_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 344.3247 | 339.3231 | 329.9817 | 325.3506 | [6 empty] | 2015-03-31
NH_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 344.3247 | 339.3231 | 329.9817 | 325.3506 | [6 empty] | 2015-03-31
NH_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.1292 | 5.0103 | 5.36 | 5.2239 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1708.1893 | 841.7314 | 1637.1799 | 807.0588 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 841.7314 | 0 | 807.0588 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1708.1893 | 1683.4628 | 1637.1799 | 1614.0384 | [6 empty] | 2015-03-31
NH_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1031.4186 | 1007.4941 | 1077.8156 | 1050.4548 | [6 empty] | 2015-03-31
NH_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1993.1781 | 1956.7224 | 1910.1224 | 1876.0442 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
NH_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.7264 | 10.3493 | 10.6254 | 10.2175 | [6 empty] | 2015-03-31
NH_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.2888 | 34.8251 | 34.8834 | 34.4574 | [6 empty] | 2015-03-31
NH_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 280.9219 | 275.6334 | 276.1767 | 271.3891 | [6 empty] | 2015-03-31
NH_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.4512 | 30.8887 | 33.0591 | 30.5834 | [6 empty] | 2015-03-31
NH_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.8315 | 42.7569 | 42.9701 | 42.8813 | [6 empty] | 2015-03-31
NH_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.79971 | 0.7853 | 0.80311 | 0.78849 | [6 empty] | 2015-03-31
NH_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.0622 | 9.9078 | 10.104 | 9.8722 | [6 empty] | 2015-03-31
NH_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.68982 | 0.6669 | 0.69203 | 0.66909 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.2155 | 4.5408 | 8.8316 | 4.3538 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.5408 | 0 | 4.3538 | [6 empty] | 2015-03-31
NH_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 27.6464 | 27.2451 | 26.4948 | 26.1228 | [6 empty] | 2015-03-31
NH_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.2947 | 21.7776 | 23.2976 | 22.7062 | [6 empty] | 2015-03-31
NH_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 36.9156 | 36.2413 | 35.378 | 34.7484 | [6 empty] | 2015-03-31
NH_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8272 | 3.803 | 3.8194 | 3.7941 | [6 empty] | 2015-03-31
NH_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4815.0418 | 4666.919 | 4855.1043 | 4698.4882 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.5544 | 8.4597 | 8.0704 | 8.0123 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 35.8328 | 34.4272 | 33.352 | 32.6133 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.1883 | 5.9468 | 5.9362 | 5.7237 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.3682 | 5.0659 | 5.1055 | 4.8331 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3263.0752 | 3199.5088 | 3093.5648 | 3072.376 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12903.9792 | 11759.784 | 12395.448 | 11611.4624 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2563.8448 | 2457.9008 | 2521.4672 | 2415.5232 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2140.0688 | 1991.7472 | 2076.5024 | 1928.1808 | [6 empty] | 2015-03-31
NH_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
NH_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NH_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.7568 | 2.5261 | 4.1149 | 2.8027 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2052 | 2.161 | 2.1002 | 2.0775 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.8383 | 12.6134 | 13.2945 | 12.4702 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8023 | 1.7192 | 1.7642 | 1.6914 | [6 empty] | 2015-03-31
NH_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5035 | 1.394 | 1.458 | 1.3583 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.5158 | 22.0029 | 25.0489 | 21.5824 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.109 | 21.6484 | 24.6404 | 21.2347 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.9261 | 20.359 | 22.5232 | 19.9986 | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 30.5422 | 26.8254 | 28.9688 | 26.3156 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 11.1636 | 14.9958 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.2254 | 5.2976 | 6.0753 | 5.1605 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7649.1568 | 6610.9056 | 7522.024 | 6483.7728 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7543.2128 | 6504.9616 | 7394.8912 | 6377.8288 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6886.36 | 6102.3744 | 6759.2272 | 5996.4304 | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9365.4496 | 8051.744 | 9174.7504 | 7903.4224 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 3347.8304 | 4492.0256 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1864.6144 | 1589.16 | 1822.2368 | 1546.7824 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
NH_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | [6 empty] | 2015-03-31
NH_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
NH_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
NH_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NH_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
NH_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
NH_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
NH_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
NH_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7656.8695 | 6602.7055 | 7516.748 | 6476.5262 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7534.822 | 6496.3166 | 7394.1708 | 6372.1926 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6109.4091 | 6758.8458 | 6001.2615 | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NH_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NH_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NH_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
NH_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
NH_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
NH_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5882 | 1.4544 | 1.6296 | 1.4902 | [6 empty] | 2015-03-31
NH_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 159.6857 | 146.2318 | 163.8448 | 149.8258 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.2106 | 9.741 | 11.0054 | 9.5548 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.0319 | 9.584 | 10.826 | 9.4009 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.0728 | 9.0132 | 9.8958 | 8.8537 | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.712 | 11.786 | 13.4435 | 11.562 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 2.2687 | 3.0475 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.309 | 1.1139 | 1.2775 | 1.0851 | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
NH_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.4517 | 3.1609 | 3.5416 | 3.2386 | [6 empty] | 2015-03-31
NH_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
NH_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.4959 | 98.3779 | 104.1689 | 98.0892 | [6 empty] | 2015-03-31
NH_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9263 | 1.778 | 1.8492 | 1.6987 | [6 empty] | 2015-03-31
NH_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2248 | 5.0246 | 5.0884 | 4.9467 | [6 empty] | 2015-03-31
NH_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.494 | 2.3393 | 2.4727 | 2.3234 | [6 empty] | 2015-03-31
NH_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.1097 | 4.0699 | 4.0018 | 3.965 | [6 empty] | 2015-03-31
NH_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 656.8528 | 593.2864 | [6 empty] | 2015-03-31
NH_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1567.9712 | 1504.4048 | 1546.7824 | 1504.4048 | [6 empty] | 2015-03-31
NH_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 741.608 | 699.2304 | 741.608 | 699.2304 | [6 empty] | 2015-03-31
NH_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | 1483.216 | 1462.0272 | [6 empty] | 2015-03-31
NH_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
NH_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
NH_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
NH_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
NH_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
NH_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NH_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
NH_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NH_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
NH_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.0986 | 1.0565 | 1.0883 | 1.0472 | [6 empty] | 2015-03-31
NH_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0469 | 1.0458 | 1.0537 | 1.0414 | [6 empty] | 2015-03-31
NH_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.53283 | 0.52256 | 0.4881 | 0.48289 | [6 empty] | 2015-03-31
NH_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.52828 | 0.51833 | 0.48362 | 0.47862 | [6 empty] | 2015-03-31
NH_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.64246 | 0.63623 | 0.57615 | 0.57313 | [6 empty] | 2015-03-31
NH_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.83892 | 0.82144 | 0.78664 | 0.76542 | [6 empty] | 2015-03-31
NH_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.63979 | 0.62934 | 0.59964 | 0.58514 | [6 empty] | 2015-03-31
NH_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.65372 | 0.64207 | 0.61236 | 0.59938 | [6 empty] | 2015-03-31
NH_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.89625 | 0.87702 | 0.84022 | 0.81059 | [6 empty] | 2015-03-31
NH_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4504 | 1.4146 | 1.372 | 1.3368 | [6 empty] | 2015-03-31
NH_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4425 | 1.4073 | 1.3642 | 1.3296 | [6 empty] | 2015-03-31
NH_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7749 | 1.7453 | 1.6639 | 1.6143 | [6 empty] | 2015-03-31
NH_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2165 | 2.1533 | 2.1184 | 2.0465 | [6 empty] | 2015-03-31
NH_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.729 | 1.6823 | 1.6575 | 1.6024 | [6 empty] | 2015-03-31
NH_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7342 | 1.6878 | 1.6627 | 1.6078 | [6 empty] | 2015-03-31
NH_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2062 | 2.1437 | 2.1137 | 2.0323 | [6 empty] | 2015-03-31
NH_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.3643 | 2.2862 | 2.2656 | 2.1707 | [6 empty] | 2015-03-31
NH_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0512 | 2.0526 | 2.0487 | 2.0707 | [6 empty] | 2015-03-31
NH_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0029 | 0.8719 | 0.95405 | 0.8261 | [6 empty] | 2015-03-31
NH_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0035 | 0.86334 | 0.95442 | 0.81764 | [6 empty] | 2015-03-31
NH_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2347 | 1.0727 | 1.1766 | 1.0531 | [6 empty] | 2015-03-31
NH_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4466 | 1.3288 | 1.3855 | 1.2671 | [6 empty] | 2015-03-31
NH_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2473 | 1.1194 | 1.1951 | 1.067 | [6 empty] | 2015-03-31
NH_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2489 | 1.1232 | 1.1984 | 1.0708 | [6 empty] | 2015-03-31
NH_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.4908 | 1.3571 | 1.4287 | 1.2895 | [6 empty] | 2015-03-31
NH_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.5913 | 1.4571 | 1.5314 | 1.3926 | [6 empty] | 2015-03-31
NH_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
NH_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
NH_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NH_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NH_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NH_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NH_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NH_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NH_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NH_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
NH_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
NH_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
NH_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | [6 empty] | 2015-03-31
NH_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | [6 empty] | 2015-03-31
NH_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 211.888 | 211.888 | [6 empty] | 2015-03-31
NH_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 317.832 | 317.832 | 296.6432 | [6 empty] | 2015-03-31
NH_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
NH_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 211.888 | 211.888 | [6 empty] | 2015-03-31
NH_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
NH_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 508.5312 | [6 empty] | 2015-03-31
NH_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 508.5312 | [6 empty] | 2015-03-31
NH_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 699.2304 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
NH_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 868.7408 | 847.552 | [6 empty] | 2015-03-31
NH_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
NH_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
NH_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 847.552 | 805.1744 | [6 empty] | 2015-03-31
NH_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 911.1184 | 932.3072 | 889.9296 | [6 empty] | 2015-03-31
NH_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 932.3072 | 932.3072 | 932.3072 | [6 empty] | 2015-03-31
NH_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 360.2096 | 317.832 | [6 empty] | 2015-03-31
NH_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 381.3984 | 317.832 | [6 empty] | 2015-03-31
NH_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 466.1536 | 402.5872 | [6 empty] | 2015-03-31
NH_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 572.0976 | 529.72 | [6 empty] | 2015-03-31
NH_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
NH_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 487.3424 | 423.776 | [6 empty] | 2015-03-31
NH_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 593.2864 | 529.72 | [6 empty] | 2015-03-31
NH_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 635.664 | 572.0976 | [6 empty] | 2015-03-31
NH_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
NH_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.13336 | 0.12996 | 0.12592 | 0.12274 | [6 empty] | 2015-03-31
NH_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.13186 | 0.12856 | 0.12443 | 0.12134 | [6 empty] | 2015-03-31
NH_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.17035 | 0.16942 | 0.15552 | 0.15473 | [6 empty] | 2015-03-31
NH_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.22937 | 0.22352 | 0.22014 | 0.21295 | [6 empty] | 2015-03-31
NH_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15772 | 0.15434 | 0.15001 | 0.14573 | [6 empty] | 2015-03-31
NH_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16234 | 0.159 | 0.15478 | 0.15054 | [6 empty] | 2015-03-31
NH_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24294 | 0.23558 | 0.23349 | 0.22349 | [6 empty] | 2015-03-31
NH_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.38929 | 0.37728 | 0.3795 | 0.36751 | [6 empty] | 2015-03-31
NH_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.38664 | 0.37484 | 0.37685 | 0.36508 | [6 empty] | 2015-03-31
NH_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.50236 | 0.49241 | 0.47688 | 0.46641 | [6 empty] | 2015-03-31
NH_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.63328 | 0.61203 | 0.61953 | 0.59502 | [6 empty] | 2015-03-31
NH_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.45867 | 0.44445 | 0.44895 | 0.43192 | [6 empty] | 2015-03-31
NH_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.46039 | 0.44627 | 0.45072 | 0.43374 | [6 empty] | 2015-03-31
NH_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.6107 | 0.59002 | 0.59477 | 0.56905 | [6 empty] | 2015-03-31
NH_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.67588 | 0.64968 | 0.66165 | 0.62945 | [6 empty] | 2015-03-31
NH_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65459 | 0.65504 | 0.65378 | 0.66079 | [6 empty] | 2015-03-31
NH_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.2716 | 0.23939 | 0.26279 | 0.23256 | [6 empty] | 2015-03-31
NH_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.2718 | 0.23653 | 0.26289 | 0.22969 | [6 empty] | 2015-03-31
NH_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.3431 | 0.30553 | 0.33142 | 0.29037 | [6 empty] | 2015-03-31
NH_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.42052 | 0.38345 | 0.41026 | 0.37286 | [6 empty] | 2015-03-31
NH_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.35324 | 0.31152 | 0.34423 | 0.30208 | [6 empty] | 2015-03-31
NH_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.35453 | 0.31278 | 0.34534 | 0.30338 | [6 empty] | 2015-03-31
NH_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.42968 | 0.38528 | 0.41763 | 0.37185 | [6 empty] | 2015-03-31
NH_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46263 | 0.41798 | 0.45259 | 0.40593 | [6 empty] | 2015-03-31
RI_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6315 | 1.5367 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7761 | 1.6582 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.291 | 1.2405 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5627 | 1.4601 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4778 | 1.4044 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 720.4192 | 656.8528 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 550.9088 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42028 | 0.38727 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.50976 | 0.4679 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.412 | 0.39588 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.43104 | 0.39372 | [8 empty] | 2015-03-31
RI_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.46662 | 0.43901 | [8 empty] | 2015-03-31
RI_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 9916.3584 | 9577.3376 | [8 empty] | 2015-03-31
RI_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24345.9312 | 24006.9104 | [8 empty] | 2015-03-31
RI_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 197755.0707 | 193898.7091 | [8 empty] | 2015-03-31
RI_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22883.904 | 21125.2336 | [8 empty] | 2015-03-31
RI_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
RI_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
RI_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
RI_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
RI_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
RI_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
RI_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
RI_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
RI_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
RI_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
RI_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
RI_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
RI_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
RI_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
RI_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
RI_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
RI_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
RI_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
RI_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
RI_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
RI_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
RI_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 376.9985 | 371.7058 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 376.9985 | 371.7058 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
RI_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 357.8208 | 352.8061 | [8 empty] | 2015-03-31
RI_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 357.8208 | 352.8061 | [8 empty] | 2015-03-31
RI_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.8593 | 4.7424 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1775.2362 | 875.1693 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 875.1693 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1775.2362 | 1750.3512 | [8 empty] | 2015-03-31
RI_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 977.1407 | 953.6204 | [8 empty] | 2015-03-31
RI_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2071.3202 | 2034.389 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
RI_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.6508 | 10.2764 | [8 empty] | 2015-03-31
RI_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 34.9882 | 34.5136 | [8 empty] | 2015-03-31
RI_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 278.0899 | 272.6716 | [8 empty] | 2015-03-31
RI_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.8879 | 30.3721 | [8 empty] | 2015-03-31
RI_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.561 | 42.4869 | [8 empty] | 2015-03-31
RI_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.78471 | 0.77189 | [8 empty] | 2015-03-31
RI_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.921 | 9.709 | [8 empty] | 2015-03-31
RI_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.67554 | 0.65406 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.5769 | 4.7212 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.7212 | [8 empty] | 2015-03-31
RI_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 28.7307 | 28.3274 | [8 empty] | 2015-03-31
RI_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 21.1214 | 20.6131 | [8 empty] | 2015-03-31
RI_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.3636 | 37.681 | [8 empty] | 2015-03-31
RI_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8212 | 3.7984 | [8 empty] | 2015-03-31
RI_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4719.9568 | 4580.0034 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.7807 | 8.6802 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 37.444 | 35.9787 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.1846 | 5.9564 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.3765 | 5.0724 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3220.6976 | 3157.1312 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12734.4688 | 11611.4624 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2500.2784 | 2373.1456 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2076.5024 | 1928.1808 | [8 empty] | 2015-03-31
RI_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
RI_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
RI_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.3828 | 2.2378 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.1882 | 2.1436 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.6601 | 12.4595 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7515 | 1.6686 | [8 empty] | 2015-03-31
RI_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4539 | 1.3446 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 24.8667 | 21.2716 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.4369 | 20.8782 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.312 | 19.6339 | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 30.5608 | 26.0839 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.1243 | 5.2114 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7458.4576 | 6377.8288 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7331.3248 | 6271.8848 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6695.6608 | 5890.4864 | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9174.7504 | 7818.6672 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1843.4256 | 1567.9712 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
RI_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | [8 empty] | 2015-03-31
RI_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
RI_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
RI_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
RI_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
RI_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
RI_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
RI_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
RI_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7462.1021 | 6383.2531 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7333.1259 | 6265.1891 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6695.4489 | 5891.8213 | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
RI_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
RI_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
RI_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | [8 empty] | 2015-03-31
RI_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
RI_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
RI_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5062 | 1.3868 | [8 empty] | 2015-03-31
RI_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 151.4389 | 139.432 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.9254 | 9.4172 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.7366 | 9.243 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.8778 | 8.6922 | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.4272 | 11.4602 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2878 | 1.0958 | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
RI_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.2734 | 3.0139 | [8 empty] | 2015-03-31
RI_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
RI_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 103.41 | 98.129 | [8 empty] | 2015-03-31
RI_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9625 | 1.813 | [8 empty] | 2015-03-31
RI_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2025 | 4.9861 | [8 empty] | 2015-03-31
RI_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.4899 | 2.3358 | [8 empty] | 2015-03-31
RI_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.1444 | 4.1033 | [8 empty] | 2015-03-31
RI_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
RI_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1567.9712 | 1504.4048 | [8 empty] | 2015-03-31
RI_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 741.608 | 699.2304 | [8 empty] | 2015-03-31
RI_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1483.216 | 1462.0272 | [8 empty] | 2015-03-31
RI_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
RI_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
RI_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
RI_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
RI_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
RI_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
RI_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
RI_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
RI_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
RI_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.0939 | 1.0484 | [8 empty] | 2015-03-31
RI_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0477 | 1.0343 | [8 empty] | 2015-03-31
RI_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.55975 | 0.54906 | [8 empty] | 2015-03-31
RI_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.55534 | 0.54498 | [8 empty] | 2015-03-31
RI_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.6762 | 0.6724 | [8 empty] | 2015-03-31
RI_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.85793 | 0.84016 | [8 empty] | 2015-03-31
RI_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.64911 | 0.6384 | [8 empty] | 2015-03-31
RI_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.66287 | 0.65141 | [8 empty] | 2015-03-31
RI_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.91365 | 0.89168 | [8 empty] | 2015-03-31
RI_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5092 | 1.4716 | [8 empty] | 2015-03-31
RI_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5019 | 1.4649 | [8 empty] | 2015-03-31
RI_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8637 | 1.8237 | [8 empty] | 2015-03-31
RI_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.2678 | 2.2043 | [8 empty] | 2015-03-31
RI_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7507 | 1.7046 | [8 empty] | 2015-03-31
RI_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7556 | 1.7097 | [8 empty] | 2015-03-31
RI_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2411 | 2.1787 | [8 empty] | 2015-03-31
RI_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.4097 | 2.3336 | [8 empty] | 2015-03-31
RI_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0695 | 2.0702 | [8 empty] | 2015-03-31
RI_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0289 | 0.90164 | [8 empty] | 2015-03-31
RI_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0294 | 0.89355 | [8 empty] | 2015-03-31
RI_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2743 | 1.1235 | [8 empty] | 2015-03-31
RI_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4752 | 1.36 | [8 empty] | 2015-03-31
RI_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2487 | 1.1246 | [8 empty] | 2015-03-31
RI_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2504 | 1.1282 | [8 empty] | 2015-03-31
RI_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5037 | 1.3736 | [8 empty] | 2015-03-31
RI_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6031 | 1.4728 | [8 empty] | 2015-03-31
RI_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
RI_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
RI_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
RI_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
RI_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
RI_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
RI_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
RI_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
RI_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
RI_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
RI_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
RI_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
RI_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | [8 empty] | 2015-03-31
RI_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 169.5104 | [8 empty] | 2015-03-31
RI_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | [8 empty] | 2015-03-31
RI_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 296.6432 | [8 empty] | 2015-03-31
RI_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
RI_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
RI_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | [8 empty] | 2015-03-31
RI_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | [8 empty] | 2015-03-31
RI_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 529.72 | [8 empty] | 2015-03-31
RI_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 678.0416 | [8 empty] | 2015-03-31
RI_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | [8 empty] | 2015-03-31
RI_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
RI_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 614.4752 | [8 empty] | 2015-03-31
RI_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 805.1744 | [8 empty] | 2015-03-31
RI_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 889.9296 | [8 empty] | 2015-03-31
RI_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | [8 empty] | 2015-03-31
RI_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | [8 empty] | 2015-03-31
RI_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | [8 empty] | 2015-03-31
RI_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
RI_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2015-03-31
RI_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
RI_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
RI_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | [8 empty] | 2015-03-31
RI_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | [8 empty] | 2015-03-31
RI_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
RI_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.13129 | 0.12781 | [8 empty] | 2015-03-31
RI_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.12988 | 0.1265 | [8 empty] | 2015-03-31
RI_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.16904 | 0.16788 | [8 empty] | 2015-03-31
RI_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.22252 | 0.21667 | [8 empty] | 2015-03-31
RI_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15221 | 0.1488 | [8 empty] | 2015-03-31
RI_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15675 | 0.1534 | [8 empty] | 2015-03-31
RI_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.23595 | 0.22875 | [8 empty] | 2015-03-31
RI_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.3853 | 0.37287 | [8 empty] | 2015-03-31
RI_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.38289 | 0.37065 | [8 empty] | 2015-03-31
RI_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.49816 | 0.48742 | [8 empty] | 2015-03-31
RI_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.61801 | 0.5969 | [8 empty] | 2015-03-31
RI_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.44538 | 0.43126 | [8 empty] | 2015-03-31
RI_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.44699 | 0.43296 | [8 empty] | 2015-03-31
RI_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.59521 | 0.57478 | [8 empty] | 2015-03-31
RI_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.6577 | 0.63252 | [8 empty] | 2015-03-31
RI_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.64749 | 0.64773 | [8 empty] | 2015-03-31
RI_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.26861 | 0.23623 | [8 empty] | 2015-03-31
RI_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.26875 | 0.23358 | [8 empty] | 2015-03-31
RI_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.34069 | 0.30334 | [8 empty] | 2015-03-31
RI_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.41171 | 0.3746 | [8 empty] | 2015-03-31
RI_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34153 | 0.30119 | [8 empty] | 2015-03-31
RI_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.3427 | 0.30239 | [8 empty] | 2015-03-31
RI_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.41758 | 0.37464 | [8 empty] | 2015-03-31
RI_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.45003 | 0.40696 | [8 empty] | 2015-03-31
SD_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.7581 | 1.6565 | 1.6459 | 1.5468 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9678 | 1.8474 | 1.9762 | 1.859 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.4264 | 1.3601 | 1.4127 | 1.3721 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6982 | 1.5918 | 1.6384 | 1.5541 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6271 | 1.5453 | 1.6735 | 1.6027 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 635.664 | 572.0976 | 635.664 | 593.2864 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 847.552 | 805.1744 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 678.0416 | 635.664 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 741.608 | 699.2304 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44337 | 0.40817 | 0.45225 | 0.41844 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.55395 | 0.50936 | 0.60687 | 0.56363 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.4552 | 0.43402 | 0.45081 | 0.43787 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.46031 | 0.42366 | 0.48207 | 0.45123 | [6 empty] | 2015-03-31
SD_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.51923 | 0.48823 | 0.53406 | 0.51145 | [6 empty] | 2015-03-31
SD_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10318.9456 | 9958.736 | 10467.2672 | 10064.68 | [6 empty] | 2015-03-31
SD_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25257.0496 | 24875.6512 | 26358.8672 | 25956.28 | [6 empty] | 2015-03-31
SD_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 204916.8851 | 200424.8595 | 216295.2707 | 211570.1683 | [6 empty] | 2015-03-31
SD_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 24218.7984 | 22290.6176 | 25829.1472 | 23752.6448 | [6 empty] | 2015-03-31
SD_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
SD_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
SD_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
SD_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
SD_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
SD_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
SD_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
SD_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
SD_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
SD_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
SD_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
SD_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
SD_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
SD_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
SD_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
SD_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
SD_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
SD_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
SD_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
SD_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
SD_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
SD_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 403.5699 | 397.731 | 353.5942 | 347.4241 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 403.5699 | 397.731 | 353.5942 | 347.4241 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
SD_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 383.0534 | 377.5094 | 335.6183 | 329.7567 | [6 empty] | 2015-03-31
SD_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 383.0534 | 377.5094 | 335.6183 | 329.7567 | [6 empty] | 2015-03-31
SD_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.6112 | 5.4657 | 5.6312 | 5.4775 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1900.4537 | 936.445 | 1665.0764 | 817.9987 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 936.445 | 0 | 817.9987 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1900.4537 | 1872.8742 | 1665.0764 | 1636.0704 | [6 empty] | 2015-03-31
SD_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1128.3385 | 1099.0836 | 1132.3614 | 1101.4532 | [6 empty] | 2015-03-31
SD_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2217.3017 | 2176.8834 | 1942.7741 | 1901.5633 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
SD_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.0678 | 10.6785 | 11.2418 | 10.8064 | [6 empty] | 2015-03-31
SD_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.3238 | 35.7602 | 37.8881 | 37.3044 | [6 empty] | 2015-03-31
SD_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 288.1708 | 281.8559 | 304.1859 | 297.53 | [6 empty] | 2015-03-31
SD_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.8217 | 32.0323 | 37.1311 | 34.1353 | [6 empty] | 2015-03-31
SD_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 44.2087 | 44.1309 | 45.2077 | 45.1129 | [6 empty] | 2015-03-31
SD_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.84042 | 0.82313 | 0.85844 | 0.8412 | [6 empty] | 2015-03-31
SD_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.6169 | 10.3418 | 10.8494 | 10.575 | [6 empty] | 2015-03-31
SD_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.72753 | 0.70118 | 0.74604 | 0.71881 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 10.2519 | 5.0518 | 8.9824 | 4.4128 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 5.0518 | 0 | 4.4128 | [6 empty] | 2015-03-31
SD_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 30.7557 | 30.3107 | 26.9471 | 26.4769 | [6 empty] | 2015-03-31
SD_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 24.3897 | 23.7573 | 24.4766 | 23.8085 | [6 empty] | 2015-03-31
SD_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 41.0675 | 40.3192 | 35.9819 | 35.2195 | [6 empty] | 2015-03-31
SD_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.9149 | 3.8873 | 3.8904 | 3.8621 | [6 empty] | 2015-03-31
SD_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 5147.4649 | 4980.7327 | 5127.2168 | 4956.1416 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 9.0571 | 9.0132 | 8.2623 | 8.171 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 39.1691 | 38.4676 | 33.6061 | 32.7567 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.7572 | 6.5028 | 6.6615 | 6.4078 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.9091 | 5.5878 | 5.805 | 5.4546 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3305.4528 | 3580.9072 | 3496.152 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12946.3568 | 12162.3712 | 13666.776 | 12713.28 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2648.6 | 2521.4672 | 2881.6768 | 2733.3552 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2224.824 | 2055.3136 | 2415.5232 | 2246.0128 | [6 empty] | 2015-03-31
SD_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
SD_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | No | Yes | [6 empty] | 2015-03-31
SD_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.3894 | 3.0117 | 4.5754 | 3.1547 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.261 | 2.2351 | 2.4207 | 2.3717 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.9006 | 13.0559 | 14.6779 | 13.6517 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8608 | 1.7713 | 2.0133 | 1.9205 | [6 empty] | 2015-03-31
SD_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5516 | 1.4355 | 1.6929 | 1.5732 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.7598 | 23.0212 | 28.7519 | 24.6291 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 26.4329 | 22.868 | 28.335 | 24.2938 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 24.0298 | 21.3498 | 25.8626 | 22.7888 | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 32.729 | 28.1407 | 31.096 | 28.1373 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 11.1636 | 11.1636 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.6726 | 5.6545 | 6.7817 | 5.6794 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8030.5552 | 6907.5488 | 8623.8416 | 7394.8912 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7924.6112 | 6865.1712 | 8496.7088 | 7288.9472 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7204.192 | 6399.0176 | 7755.1008 | 6843.9824 | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9831.6032 | 8454.3312 | 10403.7008 | 8899.296 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2012.936 | 1695.104 | 2034.1248 | 1695.104 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
SD_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
SD_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
SD_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
SD_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
SD_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
SD_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
SD_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
SD_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
SD_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 6908.2904 | 7852.8447 | 7390.7806 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 6862.3107 | 7852.8447 | 7290.155 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6406.7303 | 6777.6191 | 6777.6191 | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
SD_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
SD_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
SD_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
SD_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
SD_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
SD_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.7172 | 1.5487 | 1.7975 | 1.5919 | [6 empty] | 2015-03-31
SD_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 172.6528 | 155.7063 | 180.7238 | 160.0566 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.7572 | 10.1146 | 12.6324 | 10.821 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.6135 | 10.0473 | 12.4493 | 10.6737 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.5577 | 9.4519 | 11.363 | 10.0125 | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.3798 | 12.3639 | 15.1204 | 13.0295 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.4031 | 1.189 | 1.426 | 1.1942 | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
SD_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.732 | 3.3657 | 3.9064 | 3.4597 | [6 empty] | 2015-03-31
SD_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
SD_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 106.23 | 98.087 | 108.1995 | 97.537 | [6 empty] | 2015-03-31
SD_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.1828 | 2.0638 | 2.1334 | 1.9811 | [6 empty] | 2015-03-31
SD_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.5412 | 5.3393 | 5.6864 | 5.5266 | [6 empty] | 2015-03-31
SD_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.624 | 2.4715 | 2.7325 | 2.568 | [6 empty] | 2015-03-31
SD_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.4659 | 4.4248 | 4.3978 | 4.3512 | [6 empty] | 2015-03-31
SD_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 762.7968 | 699.2304 | [6 empty] | 2015-03-31
SD_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1652.7264 | 1610.3488 | 1737.4816 | 1673.9152 | [6 empty] | 2015-03-31
SD_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 783.9856 | 741.608 | 826.3632 | 762.7968 | [6 empty] | 2015-03-31
SD_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1546.7824 | 1525.5936 | 1610.3488 | 1589.16 | [6 empty] | 2015-03-31
SD_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
SD_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
SD_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
SD_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
SD_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
SD_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
SD_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
SD_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
SD_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
SD_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1652 | 1.1227 | 1.2199 | 1.1739 | [6 empty] | 2015-03-31
SD_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0884 | 1.0751 | 1.1276 | 1.1127 | [6 empty] | 2015-03-31
SD_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.63782 | 0.62836 | 0.57488 | 0.56372 | [6 empty] | 2015-03-31
SD_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.63227 | 0.62316 | 0.56979 | 0.55882 | [6 empty] | 2015-03-31
SD_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.78578 | 0.77219 | 0.71717 | 0.68971 | [6 empty] | 2015-03-31
SD_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.99785 | 0.97933 | 0.94259 | 0.90712 | [6 empty] | 2015-03-31
SD_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.73844 | 0.72296 | 0.7211 | 0.69674 | [6 empty] | 2015-03-31
SD_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.75044 | 0.73694 | 0.73552 | 0.70881 | [6 empty] | 2015-03-31
SD_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 1.0519 | 1.0256 | 1.0181 | 0.97094 | [6 empty] | 2015-03-31
SD_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.6863 | 1.6511 | 1.5835 | 1.5294 | [6 empty] | 2015-03-31
SD_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.6771 | 1.6425 | 1.5745 | 1.5211 | [6 empty] | 2015-03-31
SD_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 2.1447 | 2.0862 | 1.988 | 1.8334 | [6 empty] | 2015-03-31
SD_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.5888 | 2.5337 | 2.5026 | 2.3947 | [6 empty] | 2015-03-31
SD_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.9628 | 1.9113 | 1.9693 | 1.8831 | [6 empty] | 2015-03-31
SD_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.9687 | 1.9166 | 1.9744 | 1.8883 | [6 empty] | 2015-03-31
SD_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.5326 | 2.4524 | 2.5437 | 2.423 | [6 empty] | 2015-03-31
SD_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.7317 | 2.643 | 2.6862 | 2.5717 | [6 empty] | 2015-03-31
SD_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1577 | 2.1542 | 2.2337 | 2.2194 | [6 empty] | 2015-03-31
SD_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.1541 | 1.0118 | 1.147 | 0.96905 | [6 empty] | 2015-03-31
SD_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.1567 | 1.0068 | 1.1461 | 0.95952 | [6 empty] | 2015-03-31
SD_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.4436 | 1.2829 | 1.432 | 1.272 | [6 empty] | 2015-03-31
SD_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6667 | 1.5551 | 1.6614 | 1.4924 | [6 empty] | 2015-03-31
SD_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3984 | 1.2606 | 1.4288 | 1.2649 | [6 empty] | 2015-03-31
SD_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.4021 | 1.2642 | 1.428 | 1.2683 | [6 empty] | 2015-03-31
SD_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6969 | 1.5446 | 1.7227 | 1.5404 | [6 empty] | 2015-03-31
SD_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7885 | 1.6411 | 1.8458 | 1.6645 | [6 empty] | 2015-03-31
SD_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
SD_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
SD_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
SD_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
SD_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
SD_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
SD_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
SD_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
SD_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
SD_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
SD_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
SD_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
SD_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 233.0768 | 211.888 | [6 empty] | 2015-03-31
SD_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
SD_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | 275.4544 | 275.4544 | [6 empty] | 2015-03-31
SD_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | 381.3984 | 381.3984 | [6 empty] | 2015-03-31
SD_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 275.4544 | 254.2656 | [6 empty] | 2015-03-31
SD_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 275.4544 | 254.2656 | [6 empty] | 2015-03-31
SD_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 381.3984 | 402.5872 | 381.3984 | [6 empty] | 2015-03-31
SD_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 593.2864 | 656.8528 | 614.4752 | [6 empty] | 2015-03-31
SD_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
SD_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 762.7968 | 826.3632 | 783.9856 | [6 empty] | 2015-03-31
SD_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 974.6848 | 1059.44 | 1017.0624 | [6 empty] | 2015-03-31
SD_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 783.9856 | 741.608 | [6 empty] | 2015-03-31
SD_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 783.9856 | 741.608 | [6 empty] | 2015-03-31
SD_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 889.9296 | 1038.2512 | 974.6848 | [6 empty] | 2015-03-31
SD_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 1017.0624 | 1144.1952 | 1080.6288 | [6 empty] | 2015-03-31
SD_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 953.496 | 995.8736 | 995.8736 | [6 empty] | 2015-03-31
SD_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | 466.1536 | 402.5872 | [6 empty] | 2015-03-31
SD_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 360.2096 | 466.1536 | 402.5872 | [6 empty] | 2015-03-31
SD_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 593.2864 | 508.5312 | [6 empty] | 2015-03-31
SD_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 720.4192 | 635.664 | [6 empty] | 2015-03-31
SD_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 593.2864 | 508.5312 | [6 empty] | 2015-03-31
SD_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 593.2864 | 508.5312 | [6 empty] | 2015-03-31
SD_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 572.0976 | 720.4192 | 635.664 | [6 empty] | 2015-03-31
SD_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 635.664 | 783.9856 | 699.2304 | [6 empty] | 2015-03-31
SD_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
SD_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14876 | 0.14559 | 0.15905 | 0.15337 | [6 empty] | 2015-03-31
SD_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14695 | 0.14392 | 0.15732 | 0.15172 | [6 empty] | 2015-03-31
SD_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.19045 | 0.1873 | 0.20162 | 0.19233 | [6 empty] | 2015-03-31
SD_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.26072 | 0.25447 | 0.27616 | 0.26409 | [6 empty] | 2015-03-31
SD_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16712 | 0.16263 | 0.18979 | 0.18184 | [6 empty] | 2015-03-31
SD_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.17152 | 0.1672 | 0.19456 | 0.18663 | [6 empty] | 2015-03-31
SD_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.27384 | 0.26503 | 0.29126 | 0.2755 | [6 empty] | 2015-03-31
SD_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.42721 | 0.41533 | 0.4598 | 0.44128 | [6 empty] | 2015-03-31
SD_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.42417 | 0.41247 | 0.45674 | 0.43843 | [6 empty] | 2015-03-31
SD_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.5563 | 0.54043 | 0.58738 | 0.55843 | [6 empty] | 2015-03-31
SD_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.70772 | 0.68494 | 0.75815 | 0.7213 | [6 empty] | 2015-03-31
SD_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.48444 | 0.46752 | 0.54838 | 0.52207 | [6 empty] | 2015-03-31
SD_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.48623 | 0.46926 | 0.55007 | 0.5238 | [6 empty] | 2015-03-31
SD_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.65442 | 0.62808 | 0.73425 | 0.69434 | [6 empty] | 2015-03-31
SD_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.74901 | 0.71902 | 0.80709 | 0.76028 | [6 empty] | 2015-03-31
SD_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.67014 | 0.66885 | 0.71282 | 0.70826 | [6 empty] | 2015-03-31
SD_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.29627 | 0.26484 | 0.32375 | 0.28439 | [6 empty] | 2015-03-31
SD_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29615 | 0.26162 | 0.32345 | 0.28115 | [6 empty] | 2015-03-31
SD_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.37697 | 0.33754 | 0.41328 | 0.3608 | [6 empty] | 2015-03-31
SD_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.46831 | 0.43032 | 0.50369 | 0.45403 | [6 empty] | 2015-03-31
SD_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.375 | 0.32938 | 0.4179 | 0.36509 | [6 empty] | 2015-03-31
SD_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.37625 | 0.33058 | 0.41904 | 0.36626 | [6 empty] | 2015-03-31
SD_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.46052 | 0.4111 | 0.51223 | 0.45345 | [6 empty] | 2015-03-31
SD_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.49956 | 0.45168 | 0.55372 | 0.49363 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.492 | 1.3666 | 1.5419 | 1.426 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9747 | 1.8105 | 1.9408 | 1.8055 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5265 | 1.4639 | 1.5026 | 1.476 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5708 | 1.4346 | 1.5816 | 1.4711 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7616 | 1.6538 | 1.7826 | 1.7131 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 699.2304 | 635.664 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 889.9296 | 805.1744 | 868.7408 | 805.1744 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 678.0416 | 656.8528 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 699.2304 | 635.664 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 783.9856 | 741.608 | 805.1744 | 762.7968 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.47613 | 0.43613 | 0.49207 | 0.45506 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.63019 | 0.57778 | 0.61936 | 0.57617 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.48713 | 0.46717 | 0.47951 | 0.47105 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.50127 | 0.45781 | 0.50473 | 0.46948 | [6 empty] | 2015-03-31
ID_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.56216 | 0.52777 | 0.56889 | 0.54668 | [6 empty] | 2015-03-31
ID_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10679.1552 | 10297.7568 | 11399.5744 | 10975.7984 | [6 empty] | 2015-03-31
ID_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 26549.5664 | 26083.4128 | 28202.2928 | 27714.9504 | [6 empty] | 2015-03-31
ID_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 213074.5731 | 208179.9603 | 224495.3363 | 218922.6819 | [6 empty] | 2015-03-31
ID_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 26104.6016 | 24049.288 | 27354.7408 | 25235.8608 | [6 empty] | 2015-03-31
ID_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ID_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | No | [6 empty] | 2015-03-31
ID_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | No | [6 empty] | 2015-03-31
ID_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | No | [6 empty] | 2015-03-31
ID_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
ID_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
ID_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
ID_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
ID_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
ID_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
ID_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
ID_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
ID_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ID_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ID_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ID_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | Yes | [6 empty] | 2015-03-31
ID_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | Yes | [6 empty] | 2015-03-31
ID_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | Yes | [6 empty] | 2015-03-31
ID_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ID_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ID_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ID_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 305.0327 | 298.4599 | 288.3886 | 281.57 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 305.0327 | 298.4599 | 288.3886 | 281.57 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
ID_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 289.5196 | 283.2875 | 273.7211 | 267.2509 | [6 empty] | 2015-03-31
ID_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 289.5196 | 283.2875 | 273.7211 | 267.2509 | [6 empty] | 2015-03-31
ID_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 4.7715 | 4.6475 | 4.87 | 4.7252 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1436.3801 | 702.7146 | 1358.0034 | 662.9477 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 702.7146 | 0 | 662.9477 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1436.3801 | 1405.4291 | 1358.0034 | 1325.8954 | [6 empty] | 2015-03-31
ID_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 959.4803 | 934.5493 | 979.2869 | 950.1603 | [6 empty] | 2015-03-31
ID_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1675.8547 | 1653.8227 | 1606.9058 | 1560.2186 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ID_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.4558 | 11.0509 | 12.2348 | 11.7738 | [6 empty] | 2015-03-31
ID_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 38.176 | 35.494 | 40.3743 | 39.6881 | [6 empty] | 2015-03-31
ID_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 299.6382 | 292.7735 | 315.6932 | 307.8544 | [6 empty] | 2015-03-31
ID_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 37.5405 | 34.5634 | 39.1582 | 36.2672 | [6 empty] | 2015-03-31
ID_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 46.2737 | 46.1925 | 49.7716 | 49.6729 | [6 empty] | 2015-03-31
ID_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.88182 | 0.86415 | 0.94403 | 0.9261 | [6 empty] | 2015-03-31
ID_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 11.1518 | 10.871 | 11.9081 | 11.6229 | [6 empty] | 2015-03-31
ID_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.76605 | 0.73845 | 0.81639 | 0.78843 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 7.7488 | 3.7909 | 7.326 | 3.5764 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 3.7909 | 0 | 3.5764 | [6 empty] | 2015-03-31
ID_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 23.2463 | 22.7454 | 21.9779 | 21.4582 | [6 empty] | 2015-03-31
ID_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 20.7397 | 20.2008 | 21.1678 | 20.5383 | [6 empty] | 2015-03-31
ID_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 31.0403 | 30.631 | 29.763 | 28.8976 | [6 empty] | 2015-03-31
ID_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.0303 | 4.0019 | 4.1048 | 4.0764 | [6 empty] | 2015-03-31
ID_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | [6 empty] | 2015-03-31
ID_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | YES | YES | YES | [6 empty] | 2015-03-31
ID_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4564.5615 | 4427.5425 | 4570.5582 | 4414.3709 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 7.4786 | 7.464 | 7.4162 | 7.4835 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 36.1378 | 28.0529 | 29.8983 | 28.4507 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.5597 | 6.2932 | 6.6301 | 6.3292 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6639 | 5.3157 | 5.4983 | 5.1022 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 3347.8304 | 3369.0192 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14048.1744 | 12353.0704 | 13454.888 | 12798.0352 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2924.0544 | 2775.7328 | 2987.6208 | 2839.2992 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2457.9008 | 2288.3904 | 2479.0896 | 2288.3904 | [6 empty] | 2015-03-31
ID_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
ID_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | Yes | [6 empty] | 2015-03-31
ID_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.6618 | 2.4494 | 4.1386 | 2.8139 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2677 | 2.264 | 2.2609 | 2.2814 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.9883 | 13.254 | 14.4438 | 13.7445 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 2.0419 | 1.9466 | 2.0914 | 1.9964 | [6 empty] | 2015-03-31
ID_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.7223 | 1.5985 | 1.7343 | 1.6094 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 27.7831 | 24.9764 | 24.7142 | 22.4865 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 27.5382 | 24.6744 | 24.4608 | 22.1227 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 24.6509 | 22.7782 | 21.8923 | 20.2741 | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 26.8853 | 24.1414 | 24.7048 | 21.6443 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 7.8695 | 7.8144 | 9.8089 | 9.8089 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.1359 | 5.4587 | 5.6167 | 4.9995 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.4262 | 10.4262 | 9.2323 | 9.2323 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8899.296 | 7670.3456 | 9132.3728 | 7839.856 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 8772.1632 | 7564.4016 | 8984.0512 | 7712.7232 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 8009.3664 | 7098.248 | 8221.2544 | 7267.7584 | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 10763.9104 | 9238.3168 | 11124.12 | 9513.7712 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3114.7536 | 3072.376 | 3347.8304 | 3347.8304 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2161.2576 | 1843.4256 | 2224.824 | 1885.8032 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
ID_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | [6 empty] | 2015-03-31
ID_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | VFD | VFD | [6 empty] | 2015-03-31
ID_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
ID_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ID_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | No | No | [6 empty] | 2015-03-31
ID_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | Yes | No | No | [6 empty] | 2015-03-31
ID_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | Yes | No | No | [6 empty] | 2015-03-31
ID_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | Yes | No | No | [6 empty] | 2015-03-31
ID_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7660.853 | 7852.8447 | 7846.6576 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7568.2368 | 7852.8447 | 7719.7155 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 1434.9903 | 1434.9903 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | No | Yes | Yes | [6 empty] | 2015-03-31
ID_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | No | Yes | Yes | [6 empty] | 2015-03-31
ID_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | No | Yes | Yes | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
ID_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | [6 empty] | 2015-03-31
ID_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
ID_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ID_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.6107 | 1.433 | 1.619 | 1.425 | [6 empty] | 2015-03-31
ID_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 161.9396 | 144.0815 | 162.7749 | 143.2777 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 13.0196 | 11.2164 | 13.3811 | 11.4885 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 12.8473 | 11.0808 | 13.1636 | 11.3026 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 11.7136 | 10.3853 | 12.0339 | 10.6407 | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 15.6638 | 13.5382 | 16.1777 | 13.9341 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.1074 | 2.0807 | 2.2687 | 2.2687 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.5129 | 1.2872 | 1.5537 | 1.3185 | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
ID_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.5004 | 3.1144 | 3.5185 | 3.097 | [6 empty] | 2015-03-31
ID_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ID_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.4106 | 94.2365 | 100.2236 | 89.273 | [6 empty] | 2015-03-31
ID_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.8872 | 1.7573 | 1.7749 | 1.6178 | [6 empty] | 2015-03-31
ID_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 4.7952 | 4.6699 | 4.6524 | 4.5075 | [6 empty] | 2015-03-31
ID_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5158 | 2.39 | 2.4488 | 2.3295 | [6 empty] | 2015-03-31
ID_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.0523 | 4.0236 | 3.9618 | 3.9203 | [6 empty] | 2015-03-31
ID_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 762.7968 | 699.2304 | 783.9856 | 699.2304 | [6 empty] | 2015-03-31
ID_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1737.4816 | 1673.9152 | 1843.4256 | 1758.6704 | [6 empty] | 2015-03-31
ID_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 826.3632 | 762.7968 | 868.7408 | 826.3632 | [6 empty] | 2015-03-31
ID_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1652.7264 | 1631.5376 | 1758.6704 | 1716.2928 | [6 empty] | 2015-03-31
ID_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
ID_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
ID_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
ID_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
ID_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ID_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ID_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ID_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ID_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ID_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.2192 | 1.172 | 1.2861 | 1.2381 | [6 empty] | 2015-03-31
ID_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.1566 | 1.1416 | 1.225 | 1.2094 | [6 empty] | 2015-03-31
ID_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.48902 | 0.47565 | 0.47553 | 0.46499 | [6 empty] | 2015-03-31
ID_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.48307 | 0.47011 | 0.46947 | 0.45941 | [6 empty] | 2015-03-31
ID_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.6374 | 0.62727 | 0.59086 | 0.58534 | [6 empty] | 2015-03-31
ID_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.87554 | 0.85202 | 0.85817 | 0.83178 | [6 empty] | 2015-03-31
ID_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.61565 | 0.601 | 0.56837 | 0.54948 | [6 empty] | 2015-03-31
ID_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.62855 | 0.6147 | 0.58441 | 0.5663 | [6 empty] | 2015-03-31
ID_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.948 | 0.91771 | 0.9237 | 0.88485 | [6 empty] | 2015-03-31
ID_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3871 | 1.3446 | 1.417 | 1.3736 | [6 empty] | 2015-03-31
ID_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3772 | 1.3354 | 1.4067 | 1.3641 | [6 empty] | 2015-03-31
ID_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8443 | 1.7986 | 1.8036 | 1.7593 | [6 empty] | 2015-03-31
ID_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3423 | 2.2649 | 2.3766 | 2.2849 | [6 empty] | 2015-03-31
ID_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6951 | 1.6468 | 1.6891 | 1.62 | [6 empty] | 2015-03-31
ID_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.701 | 1.6524 | 1.6959 | 1.6262 | [6 empty] | 2015-03-31
ID_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2678 | 2.1881 | 2.2674 | 2.1633 | [6 empty] | 2015-03-31
ID_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5549 | 2.4589 | 2.5705 | 2.445 | [6 empty] | 2015-03-31
ID_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1944 | 2.1728 | 2.2567 | 2.2714 | [6 empty] | 2015-03-31
ID_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.005 | 0.87873 | 1.0109 | 0.88822 | [6 empty] | 2015-03-31
ID_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0013 | 0.86983 | 1.0105 | 0.8782 | [6 empty] | 2015-03-31
ID_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2763 | 1.1304 | 1.2842 | 1.1246 | [6 empty] | 2015-03-31
ID_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5824 | 1.4447 | 1.5987 | 1.4562 | [6 empty] | 2015-03-31
ID_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3122 | 1.1574 | 1.3107 | 1.1462 | [6 empty] | 2015-03-31
ID_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3161 | 1.162 | 1.315 | 1.151 | [6 empty] | 2015-03-31
ID_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6078 | 1.4423 | 1.6074 | 1.427 | [6 empty] | 2015-03-31
ID_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7319 | 1.5673 | 1.7462 | 1.5656 | [6 empty] | 2015-03-31
ID_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ID_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
ID_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ID_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ID_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ID_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ID_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ID_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ID_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ID_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ID_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
ID_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ID_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
ID_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
ID_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 275.4544 | 275.4544 | 254.2656 | [6 empty] | 2015-03-31
ID_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 381.3984 | 381.3984 | 381.3984 | [6 empty] | 2015-03-31
ID_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
ID_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
ID_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 402.5872 | 423.776 | 402.5872 | [6 empty] | 2015-03-31
ID_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
ID_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
ID_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 805.1744 | 805.1744 | 783.9856 | [6 empty] | 2015-03-31
ID_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 1017.0624 | 1059.44 | 1038.2512 | [6 empty] | 2015-03-31
ID_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 741.608 | 762.7968 | 720.4192 | [6 empty] | 2015-03-31
ID_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 741.608 | 762.7968 | 741.608 | [6 empty] | 2015-03-31
ID_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 974.6848 | 1017.0624 | 974.6848 | [6 empty] | 2015-03-31
ID_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1144.1952 | 1101.8176 | 1165.384 | 1101.8176 | [6 empty] | 2015-03-31
ID_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 974.6848 | 1017.0624 | 1017.0624 | [6 empty] | 2015-03-31
ID_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 402.5872 | 444.9648 | 402.5872 | [6 empty] | 2015-03-31
ID_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 381.3984 | 444.9648 | 402.5872 | [6 empty] | 2015-03-31
ID_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 508.5312 | 572.0976 | 508.5312 | [6 empty] | 2015-03-31
ID_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
ID_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 593.2864 | 508.5312 | [6 empty] | 2015-03-31
ID_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 593.2864 | 508.5312 | [6 empty] | 2015-03-31
ID_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 720.4192 | 635.664 | [6 empty] | 2015-03-31
ID_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 699.2304 | 783.9856 | 699.2304 | [6 empty] | 2015-03-31
ID_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ID_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.15605 | 0.15179 | 0.15175 | 0.14838 | [6 empty] | 2015-03-31
ID_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15416 | 0.15002 | 0.14982 | 0.14661 | [6 empty] | 2015-03-31
ID_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.20341 | 0.20017 | 0.18856 | 0.18679 | [6 empty] | 2015-03-31
ID_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.2794 | 0.27191 | 0.27386 | 0.26544 | [6 empty] | 2015-03-31
ID_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.18933 | 0.18436 | 0.18137 | 0.17535 | [6 empty] | 2015-03-31
ID_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.1937 | 0.189 | 0.1865 | 0.18072 | [6 empty] | 2015-03-31
ID_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.30253 | 0.29287 | 0.29477 | 0.28238 | [6 empty] | 2015-03-31
ID_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.44264 | 0.4291 | 0.45219 | 0.43835 | [6 empty] | 2015-03-31
ID_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.43949 | 0.42618 | 0.44892 | 0.43534 | [6 empty] | 2015-03-31
ID_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.58857 | 0.57398 | 0.57558 | 0.56143 | [6 empty] | 2015-03-31
ID_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.74747 | 0.7228 | 0.75843 | 0.72915 | [6 empty] | 2015-03-31
ID_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.53743 | 0.52104 | 0.53904 | 0.51696 | [6 empty] | 2015-03-31
ID_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.53944 | 0.52293 | 0.54121 | 0.51898 | [6 empty] | 2015-03-31
ID_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.7237 | 0.69828 | 0.72359 | 0.69034 | [6 empty] | 2015-03-31
ID_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.81534 | 0.78469 | 0.8203 | 0.78027 | [6 empty] | 2015-03-31
ID_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.70028 | 0.69338 | 0.72016 | 0.72486 | [6 empty] | 2015-03-31
ID_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.32072 | 0.28042 | 0.3226 | 0.28345 | [6 empty] | 2015-03-31
ID_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.31953 | 0.27758 | 0.32246 | 0.28026 | [6 empty] | 2015-03-31
ID_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.40728 | 0.36075 | 0.40983 | 0.3589 | [6 empty] | 2015-03-31
ID_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.50498 | 0.46104 | 0.51017 | 0.46469 | [6 empty] | 2015-03-31
ID_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.41876 | 0.36936 | 0.41828 | 0.36578 | [6 empty] | 2015-03-31
ID_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.41998 | 0.37082 | 0.41965 | 0.36729 | [6 empty] | 2015-03-31
ID_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.51309 | 0.46028 | 0.51297 | 0.45538 | [6 empty] | 2015-03-31
ID_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.55268 | 0.50015 | 0.55725 | 0.49962 | [6 empty] | 2015-03-31
WY_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.5711 | 1.4395 | 1.6085 | 1.4922 | 1.5714 | 1.4405 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9565 | 1.7975 | 1.8622 | 1.744 | 1.8471 | 1.7572 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5325 | 1.474 | 1.5542 | 1.5186 | 1.519 | 1.6031 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.6502 | 1.4992 | 1.6037 | 1.4982 | 1.4785 | 1.3649 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.8317 | 1.7163 | 1.8579 | 1.7879 | 1.8234 | 1.8541 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 720.4192 | 678.0416 | 699.2304 | 656.8528 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 889.9296 | 805.1744 | 847.552 | 783.9856 | 826.3632 | 783.9856 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 699.2304 | 678.0416 | 678.0416 | 720.4192 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 741.608 | 678.0416 | 720.4192 | 678.0416 | 656.8528 | 614.4752 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 826.3632 | 762.7968 | 826.3632 | 805.1744 | 826.3632 | 826.3632 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 | 136.9178 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 | 103.7925 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 | 61.5711 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.50135 | 0.45938 | 0.51332 | 0.4762 | 0.50146 | 0.4597 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.62438 | 0.57364 | 0.59427 | 0.55655 | 0.58945 | 0.56076 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.48907 | 0.47039 | 0.49599 | 0.48462 | 0.48474 | 0.5116 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.52661 | 0.47844 | 0.51179 | 0.4781 | 0.47184 | 0.43556 |  |  |  |  | 2015-03-31
WY_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.58454 | 0.54771 | 0.59288 | 0.57056 | 0.58188 | 0.5917 |  |  |  |  | 2015-03-31
WY_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11336.008 | 10933.4208 | 12141.1824 | 11696.2176 | 12098.8048 | 11653.84 |  |  |  |  | 2015-03-31
WY_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 28096.3488 | 27630.1952 | 29664.32 | 29282.9216 | 29113.4112 | 29282.9216 |  |  |  |  | 2015-03-31
WY_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 227249.8803 | 223160.4419 | 238501.1332 | 234009.1076 | 228288.1315 | 231085.0531 |  |  |  |  | 2015-03-31
WY_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 27418.3072 | 25278.2384 | 28244.6704 | 26083.4128 | 27142.8528 | 25765.5808 |  |  |  |  | 2015-03-31
WY_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WY_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | Yes | Yes | No | Yes | No |  |  |  |  | 2015-03-31
WY_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | Yes | Yes | No | Yes | No |  |  |  |  | 2015-03-31
WY_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | Yes | Yes | No | Yes | No |  |  |  |  | 2015-03-31
WY_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 |  |  |  |  | 2015-03-31
WY_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
WY_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 |  |  |  |  | 2015-03-31
WY_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 | 5377.805 |  |  |  |  | 2015-03-31
WY_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 | 716.9654 |  |  |  |  | 2015-03-31
WY_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
WY_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 | 331.2021 |  |  |  |  | 2015-03-31
WY_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 | 33.1211 |  |  |  |  | 2015-03-31
WY_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WY_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WY_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WY_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | No | No | Yes | No | Yes |  |  |  |  | 2015-03-31
WY_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | No | No | Yes | No | Yes |  |  |  |  | 2015-03-31
WY_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | No | No | Yes | No | Yes |  |  |  |  | 2015-03-31
WY_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WY_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WY_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WY_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 327.4849 | 322.1686 | 268.9914 | 263.5834 | 237.382 | 238.2522 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 327.4849 | 322.1686 | 268.9914 | 263.5834 | 237.382 | 238.2522 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Screw | Screw | Screw | Screw |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Screw | Screw | Screw | Screw |  |  |  |  | 2015-03-31
WY_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 310.8356 | 305.7811 | 255.316 | 250.1822 | 225.3069 | 226.1404 |  |  |  |  | 2015-03-31
WY_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 310.8356 | 305.7811 | 255.316 | 250.1822 | 225.3069 | 226.1404 |  |  |  |  | 2015-03-31
WY_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.1849 | 5.0709 | 4.8166 | 4.6661 | 5.038 | 4.8766 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1542.1049 | 758.5362 | 1266.6627 | 620.5988 | 1117.8171 | 560.9572 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 758.5362 | 0 | 620.5988 | 0 | 560.9572 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1542.1049 | 1517.0709 | 1266.6627 | 1241.1976 | 1117.8171 | 1121.9144 |  |  |  |  | 2015-03-31
WY_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1042.6026 | 1019.683 | 968.5403 | 938.2773 | 1013.0686 | 980.6215 |  |  |  |  | 2015-03-31
WY_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1799.3287 | 1763.3484 | 1515.6824 | 1477.984 | 1337.5723 | 1335.9445 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | yes | yes |  |  |  |  | 2015-03-31
WY_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 12.1749 | 11.7439 | 13.0357 | 12.543 | 12.9887 | 12.5018 |  |  |  |  | 2015-03-31
WY_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 40.2164 | 37.5987 | 42.4695 | 41.9215 | 41.6675 | 41.9204 |  |  |  |  | 2015-03-31
WY_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 319.567 | 313.8283 | 335.4153 | 329.0709 | 321.0425 | 324.9601 |  |  |  |  | 2015-03-31
WY_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 39.2636 | 34.3895 | 40.4295 | 37.5048 | 38.8565 | 37.0274 |  |  |  |  | 2015-03-31
WY_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 48.8992 | 48.8142 | 53.0147 | 52.9098 | 53.7878 | 53.6789 |  |  |  |  | 2015-03-31
WY_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.9252 | 0.90831 | 1.0071 | 0.98773 | 1.0401 | 1.0486 |  |  |  |  | 2015-03-31
WY_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 11.6649 | 11.3949 | 12.7033 | 12.3957 | 13.1522 | 13.3104 |  |  |  |  | 2015-03-31
WY_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.80288 | 0.77512 | 0.86905 | 0.83971 | 0.89413 | 0.89521 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 8.3191 | 4.092 | 6.8332 | 3.3479 | 6.0302 | 3.0262 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.092 | 0 | 3.3479 | 0 | 3.0262 |  |  |  |  | 2015-03-31
WY_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 24.9573 | 24.5522 | 20.4996 | 20.0875 | 18.0907 | 18.157 |  |  |  |  | 2015-03-31
WY_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.5365 | 22.0411 | 20.9356 | 20.2814 | 21.8981 | 21.1967 |  |  |  |  | 2015-03-31
WY_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 33.325 | 32.6592 | 28.0727 | 27.3745 | 24.7738 | 24.7437 |  |  |  |  | 2015-03-31
WY_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.1146 | 4.0878 | 4.1758 | 4.1468 | 4.0137 | 4.0171 |  |  |  |  | 2015-03-31
WY_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | NO | NO | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4850.6587 | 4688.3125 | 4616.8551 | 4464.9737 | 4582.824 | 4453.2588 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.0624 | 7.9807 | 8.0881 | 8.0762 | 6.8165 | 7.1057 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 32.4821 | 31.2282 | 32.9842 | 31.0759 | 31.8052 | 29.0165 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.6623 | 6.3472 | 6.7111 | 6.418 | 6.5546 | 6.4713 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6875 | 5.329 | 5.4888 | 5.0936 | 5.2834 | 5.0977 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3623.2848 | 3580.9072 | 3644.4736 | 3644.4736 | 3072.376 | 3199.5088 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 14535.5168 | 13285.3776 | 14853.3488 | 13984.608 | 14323.6288 | 13052.3008 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 3008.8096 | 2860.488 | 3029.9984 | 2881.6768 | 2945.2432 | 2902.8656 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2500.2784 | 2330.768 | 2479.0896 | 2288.3904 | 2373.1456 | 2288.3904 |  |  |  |  | 2015-03-31
WY_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
WY_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | VFD | VFD |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 | 490.669 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 | 377.3937 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | No | No | No | No | Yes |  |  |  |  | 2015-03-31
WY_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.4199 | 3.0306 | 4.2391 | 2.8879 | 4.8115 | 3.3277 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.4579 | 2.4261 | 2.4658 | 2.4621 | 2.0781 | 2.1662 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 15.5074 | 14.2534 | 15.8318 | 14.9159 | 15.2659 | 14.0178 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 2.0311 | 2.0021 | 2.0459 | 2.0245 | 2.0675 | 2.0413 |  |  |  |  | 2015-03-31
WY_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.7575 | 1.6282 | 1.7314 | 1.6067 | 1.6666 | 1.608 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 30.5138 | 26.2442 | 20.373 | 17.5018 | 19.6738 | 16.8618 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 30.0195 | 25.8605 | 20.0276 | 17.2842 | 19.4082 | 16.5845 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 27.4028 | 24.0918 | 18.3023 | 16.1521 | 17.6128 | 15.7969 |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 29.2941 | 26.5284 | 25.0892 | 21.519 | 24.0592 | 20.3953 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 8.33 | 8.2694 | 8.133 | 8.0384 | 9.9964 | 9.9964 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.6649 | 5.9849 | 5.0683 | 4.2816 | 5.3377 | 4.2457 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 7.404 | 7.404 | 7.0043 | 7.0043 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 9153.5616 | 7882.2336 | 9174.7504 | 7882.2336 | 8856.9184 | 7585.5904 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 9005.24 | 7755.1008 | 9005.24 | 7776.2896 | 8729.7856 | 7458.4576 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 8221.2544 | 7225.3808 | 8242.4432 | 7267.7584 | 7924.6112 | 7119.4368 |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 11187.6864 | 9556.1488 | 11293.6304 | 9683.2816 | 10827.4768 | 9174.7504 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3241.8864 | 3199.5088 | 3453.7744 | 3432.5856 | 4492.0256 | 4492.0256 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2224.824 | 1864.6144 | 2288.3904 | 1928.1808 | 2394.3344 | 1906.992 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 |  |  |  |  | 2015-03-31
WY_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | n/a | n/a |  |  |  |  | 2015-03-31
WY_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | n/a | VFD | n/a | VFD | VFD | VFD |  |  |  |  | 2015-03-31
WY_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | n/a | VFD | n/a | VFD |  |  |  |  | 2015-03-31
WY_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WY_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | Yes | Yes | No | No | No | No |  |  |  |  | 2015-03-31
WY_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | Yes | No | No | No | No |  |  |  |  | 2015-03-31
WY_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | Yes | No | No | No | No |  |  |  |  | 2015-03-31
WY_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | Yes | No | No | No | No |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7852.8447 | 7852.8447 | 7852.8447 | 7852.8447 | 7590.5698 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7760.3133 | 7852.8447 | 7780.6969 | 7852.8447 | 7465.7042 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 | 6777.6191 |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 825.0071 | 825.0071 | 1434.9903 | 1434.9903 | 2584.9912 | 2584.9912 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | No | DifferentialDryBulb | No |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb |  |  |  |  | 2015-03-31
WY_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WY_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WY_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | No | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WY_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | No | No | Yes | Yes |  |  |  |  | 2015-03-31
WY_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | No | No | Yes | Yes | Yes | Yes |  |  |  |  | 2015-03-31
WY_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | no | no |  |  |  |  | 2015-03-31
WY_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.7095 | 1.5016 | 1.5587 | 1.3715 | 1.5889 | 1.3947 |  |  |  |  | 2015-03-31
WY_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 171.8761 | 150.9707 | 156.7194 | 137.8915 | 159.7554 | 140.2254 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 13.4065 | 11.5307 | 13.4277 | 11.5353 | 12.9669 | 11.1135 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 13.1893 | 11.362 | 13.2 | 11.3919 | 12.7918 | 10.9307 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 12.0397 | 10.5849 | 12.0629 | 10.6458 | 11.6085 | 10.4117 |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 16.2618 | 13.9763 | 16.4294 | 14.1831 | 15.755 | 13.4424 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.1985 | 2.1673 | 2.3456 | 2.3183 | 3.0475 | 3.0475 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.5553 | 1.3056 | 1.5987 | 1.3506 | 1.6837 | 1.3392 |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 | 2.1353 |  |  |  |  | 2015-03-31
WY_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.7152 | 3.2633 | 3.3876 | 2.9806 | 3.4532 | 3.0311 |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | YES | YES |  |  |  |  | 2015-03-31
WY_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 103.3925 | 91.8869 | 96.1905 | 85.5506 | 94.2593 | 83.7451 |  |  |  |  | 2015-03-31
WY_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9535 | 1.7971 | 1.764 | 1.6135 | 1.7655 | 1.5597 |  |  |  |  | 2015-03-31
WY_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2074 | 5.0515 | 4.2937 | 4.16 | 4.1847 | 3.9726 |  |  |  |  | 2015-03-31
WY_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.7084 | 2.5782 | 2.2903 | 2.1741 | 2.0268 | 1.913 |  |  |  |  | 2015-03-31
WY_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.2153 | 4.1713 | 4.0655 | 4.0202 | 4.1025 | 4.0793 |  |  |  |  | 2015-03-31
WY_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 783.9856 | 720.4192 | 805.1744 | 699.2304 |  |  |  |  | 2015-03-31
WY_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1843.4256 | 1758.6704 | 1906.992 | 1843.4256 | 1885.8032 | 1779.8592 |  |  |  |  | 2015-03-31
WY_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 911.1184 | 847.552 | 911.1184 | 847.552 |  |  |  |  | 2015-03-31
WY_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1737.4816 | 1716.2928 | 1822.2368 | 1801.048 | 1843.4256 | 1843.4256 |  |  |  |  | 2015-03-31
WY_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 | 119.2938 |  |  |  |  | 2015-03-31
WY_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 | 500.0133 |  |  |  |  | 2015-03-31
WY_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 | 267.7629 |  |  |  |  | 2015-03-31
WY_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 | 199.9928 |  |  |  |  | 2015-03-31
WY_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | motorized | motorized |  |  |  |  | 2015-03-31
WY_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WY_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | No | No | No | No |  |  |  |  | 2015-03-31
WY_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WY_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | No | No |  |  |  |  | 2015-03-31
WY_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.2859 | 1.2369 | 1.3351 | 1.2873 | 1.32 | 1.2531 |  |  |  |  | 2015-03-31
WY_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.2151 | 1.1992 | 1.2824 | 1.2681 | 1.2941 | 1.2868 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.50455 | 0.48918 | 0.47795 | 0.46852 | 0.39924 | 0.41306 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.49879 | 0.48384 | 0.47138 | 0.46243 | 0.39267 | 0.40583 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.6301 | 0.61077 | 0.58126 | 0.57122 | 0.46449 | 0.50553 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.88235 | 0.85557 | 0.86316 | 0.83847 | 0.74002 | 0.79008 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.61912 | 0.60664 | 0.54036 | 0.52626 | 0.47027 | 0.50681 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.63364 | 0.62123 | 0.55872 | 0.54472 | 0.48973 | 0.52711 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.93519 | 0.90326 | 0.90065 | 0.86503 | 0.79219 | 0.84703 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4446 | 1.3983 | 1.4507 | 1.4092 | 1.3033 | 1.328 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4347 | 1.3891 | 1.4392 | 1.3985 | 1.2917 | 1.3152 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.829 | 1.7798 | 1.7875 | 1.7454 | 1.577 | 1.6806 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3974 | 2.3127 | 2.4264 | 2.3369 | 2.1883 | 2.3033 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7067 | 1.6557 | 1.6452 | 1.5846 | 1.5342 | 1.6144 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7121 | 1.6615 | 1.6519 | 1.5915 | 1.5418 | 1.6229 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.2788 | 2.2037 | 2.1917 | 2.0966 | 2.0133 | 2.1396 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5604 | 2.4613 | 2.5509 | 2.432 | 2.3523 | 2.4838 |  |  |  |  | 2015-03-31
WY_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.3643 | 2.3637 | 2.4504 | 2.4443 | 2.2931 | 2.3685 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0326 | 0.90624 | 0.99521 | 0.88917 | 0.86156 | 0.79778 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0317 | 0.89558 | 0.99318 | 0.8771 | 0.86123 | 0.783 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.3114 | 1.1516 | 1.2501 | 1.0957 | 1.0716 | 0.98645 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.6117 | 1.4673 | 1.5924 | 1.4581 | 1.4174 | 1.412 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.321 | 1.1662 | 1.2741 | 1.1169 | 1.1599 | 1.0922 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3245 | 1.1706 | 1.2783 | 1.1218 | 1.1652 | 1.0983 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6176 | 1.4524 | 1.5491 | 1.3767 | 1.3936 | 1.3546 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.763 | 1.593 | 1.7145 | 1.5415 | 1.5394 | 1.5182 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 | 56.9945 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 | 109.9824 |  |  |  |  | 2015-03-31
WY_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 | 80.7372 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 | 54.9913 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 211.888 | 169.5104 | 190.6992 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 211.888 | 169.5104 | 190.6992 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 254.2656 | 254.2656 | 211.888 | 233.0768 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 381.3984 | 381.3984 | 381.3984 | 339.0208 | 360.2096 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | 233.0768 | 233.0768 | 211.888 | 233.0768 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | 254.2656 | 254.2656 | 211.888 | 233.0768 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 402.5872 | 402.5872 | 381.3984 | 360.2096 | 381.3984 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 656.8528 | 635.664 | 593.2864 | 593.2864 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 635.664 | 656.8528 | 635.664 | 572.0976 | 593.2864 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 805.1744 | 805.1744 | 783.9856 | 720.4192 | 762.7968 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1080.6288 | 1038.2512 | 1101.8176 | 1059.44 | 974.6848 | 1038.2512 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 741.608 | 741.608 | 720.4192 | 699.2304 | 720.4192 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 741.608 | 741.608 | 720.4192 | 699.2304 | 720.4192 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 995.8736 | 995.8736 | 953.496 | 911.1184 | 953.496 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1144.1952 | 1101.8176 | 1144.1952 | 1101.8176 | 1059.44 | 1123.0064 |  |  |  |  | 2015-03-31
WY_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 1059.44 | 1101.8176 | 1101.8176 | 1038.2512 | 1059.44 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 402.5872 | 444.9648 | 402.5872 | 381.3984 | 360.2096 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 402.5872 | 444.9648 | 402.5872 | 381.3984 | 360.2096 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 508.5312 | 572.0976 | 487.3424 | 487.3424 | 444.9648 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 720.4192 | 656.8528 | 635.664 | 635.664 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 572.0976 | 508.5312 | 529.72 | 487.3424 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | 572.0976 | 508.5312 | 529.72 | 487.3424 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 656.8528 | 699.2304 | 614.4752 | 635.664 | 614.4752 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 720.4192 | 762.7968 | 699.2304 | 699.2304 | 678.0416 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.16102 | 0.15611 | 0.15253 | 0.14951 | 0.12741 | 0.13182 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.15918 | 0.15441 | 0.15044 | 0.14757 | 0.12532 | 0.1295 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.20107 | 0.19492 | 0.18549 | 0.18229 | 0.14822 | 0.16132 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.28157 | 0.27303 | 0.27546 | 0.26757 | 0.23615 | 0.25214 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.18837 | 0.18393 | 0.17244 | 0.16794 | 0.15007 | 0.16174 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.19359 | 0.18916 | 0.1783 | 0.17384 | 0.15628 | 0.16822 |  |  |  |  | 2015-03-31
WY_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.29844 | 0.28825 | 0.28742 | 0.27605 | 0.25281 | 0.27031 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.46102 | 0.44624 | 0.46295 | 0.44973 | 0.41593 | 0.4238 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.45785 | 0.4433 | 0.45929 | 0.44631 | 0.4122 | 0.41973 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.58367 | 0.56798 | 0.57044 | 0.55699 | 0.50326 | 0.53631 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.76507 | 0.73802 | 0.77433 | 0.74576 | 0.69832 | 0.73505 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.54129 | 0.52552 | 0.52501 | 0.50569 | 0.48961 | 0.51518 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.54323 | 0.5276 | 0.52716 | 0.50789 | 0.49203 | 0.5179 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.72721 | 0.70326 | 0.69941 | 0.66908 | 0.6425 | 0.68278 |  |  |  |  | 2015-03-31
WY_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.8171 | 0.78548 | 0.81404 | 0.77613 | 0.75069 | 0.79265 |  |  |  |  | 2015-03-31
WY_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.75449 | 0.75432 | 0.78196 | 0.78003 | 0.73177 | 0.75585 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.32952 | 0.2892 | 0.31759 | 0.28376 | 0.27494 | 0.25459 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.32923 | 0.2858 | 0.31695 | 0.2799 | 0.27484 | 0.24987 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.41851 | 0.36749 | 0.39895 | 0.34967 | 0.34196 | 0.3148 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.51432 | 0.46826 | 0.50818 | 0.46531 | 0.45231 | 0.45061 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.42155 | 0.37216 | 0.4066 | 0.35642 | 0.37014 | 0.34856 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.42269 | 0.37358 | 0.40794 | 0.35797 | 0.37184 | 0.3505 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.51623 | 0.4635 | 0.49434 | 0.43933 | 0.44472 | 0.43228 |  |  |  |  | 2015-03-31
WY_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.56263 | 0.50835 | 0.54714 | 0.49191 | 0.49127 | 0.4845 |  |  |  |  | 2015-03-31
ME_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.4857 | 1.4071 | 1.3971 | 1.3067 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.6554 | 1.5655 | 1.6832 | 1.626 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2379 | 1.2171 | 1.2543 | 1.3017 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.388 | 1.3083 | 1.2838 | 1.1496 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4081 | 1.3573 | 1.4393 | 1.4512 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 572.0976 | 529.72 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 762.7968 | 741.608 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 550.9088 | 550.9088 | 572.0976 | 593.2864 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 529.72 | 550.9088 | 508.5312 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 635.664 | 614.4752 | 656.8528 | 656.8528 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.40589 | 0.37716 | 0.40687 | 0.37292 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.5008 | 0.46786 | 0.53716 | 0.51891 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.39505 | 0.38841 | 0.40027 | 0.41541 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.39985 | 0.37276 | 0.39079 | 0.36169 | [6 empty] | 2015-03-31
ME_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.44935 | 0.43314 | 0.45931 | 0.4631 | [6 empty] | 2015-03-31
ME_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 9789.2256 | 9407.8272 | 9789.2256 | 9407.8272 | [6 empty] | 2015-03-31
ME_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24028.0992 | 23731.456 | 24430.6864 | 24515.4416 | [6 empty] | 2015-03-31
ME_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 194513.1843 | 190995.8435 | 198263.6019 | 199958.7059 | [6 empty] | 2015-03-31
ME_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22375.3728 | 20722.6464 | 22672.016 | 21506.632 | [6 empty] | 2015-03-31
ME_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
ME_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
ME_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
ME_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
ME_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
ME_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
ME_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
ME_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
ME_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
ME_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
ME_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
ME_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ME_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ME_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ME_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
ME_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
ME_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
ME_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ME_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ME_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ME_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 345.2623 | 340.2239 | 323.2369 | 323.1165 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 345.2623 | 340.2239 | 323.2369 | 323.1165 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
ME_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 327.7058 | 322.916 | 306.8 | 306.6809 | [6 empty] | 2015-03-31
ME_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 327.7058 | 322.916 | 306.8 | 306.6809 | [6 empty] | 2015-03-31
ME_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.204 | 5.0762 | 5.8046 | 5.6648 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1625.7676 | 801.0468 | 1522.1018 | 760.768 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 801.0468 | 0 | 760.768 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1625.7676 | 1602.1507 | 1522.1018 | 1521.5343 | [6 empty] | 2015-03-31
ME_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1046.4415 | 1020.7529 | 1167.2226 | 1139.1025 | [6 empty] | 2015-03-31
ME_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1896.9667 | 1862.096 | 1775.8702 | 1768.5791 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ME_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.5098 | 10.1058 | 10.4945 | 10.1 | [6 empty] | 2015-03-31
ME_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 34.5433 | 34.1055 | 35.1317 | 35.2595 | [6 empty] | 2015-03-31
ME_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 273.5538 | 268.5939 | 278.8031 | 281.1919 | [6 empty] | 2015-03-31
ME_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.1707 | 29.7994 | 32.5916 | 30.9125 | [6 empty] | 2015-03-31
ME_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.5025 | 42.4146 | 43.3168 | 43.2269 | [6 empty] | 2015-03-31
ME_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.78985 | 0.77588 | 0.81839 | 0.82337 | [6 empty] | 2015-03-31
ME_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 9.9238 | 9.7743 | 10.3193 | 10.4161 | [6 empty] | 2015-03-31
ME_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.67873 | 0.65699 | 0.70346 | 0.70121 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 8.7707 | 4.3214 | 8.2112 | 4.1041 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.3214 | 0 | 4.1041 | [6 empty] | 2015-03-31
ME_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 26.3122 | 25.9282 | 24.6336 | 24.6244 | [6 empty] | 2015-03-31
ME_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 22.6194 | 22.0642 | 25.2302 | 24.6224 | [6 empty] | 2015-03-31
ME_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 35.1341 | 34.4896 | 32.8928 | 32.7553 | [6 empty] | 2015-03-31
ME_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8007 | 3.7765 | 3.8151 | 3.8158 | [6 empty] | 2015-03-31
ME_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4822.6491 | 4662.0275 | 5035.4567 | 4900.7712 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.153 | 8.0818 | 7.7433 | 7.6728 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 34.1697 | 33.3294 | 31.824 | 31.0754 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.7944 | 5.599 | 5.7241 | 5.6747 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 4.9752 | 4.7174 | 4.8377 | 4.7245 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3072.376 | 3029.9984 | 3051.1872 | 3008.8096 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12353.0704 | 11526.7072 | 12374.2592 | 11653.84 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2479.0896 | 2373.1456 | 2585.0336 | 2563.8448 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2034.1248 | 1906.992 | 2118.88 | 2076.5024 | [6 empty] | 2015-03-31
ME_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
ME_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 3.8437 | 2.5939 | 4.7677 | 3.3051 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.0795 | 2.0512 | 2.0702 | 2.0437 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.2462 | 12.3804 | 13.2699 | 12.5018 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7315 | 1.6631 | 1.8056 | 1.79 | [6 empty] | 2015-03-31
ME_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4282 | 1.3334 | 1.4906 | 1.4477 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 24.1892 | 21.0066 | 24.5179 | 21.9022 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 23.7776 | 20.6156 | 24.1106 | 21.4583 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 21.7532 | 19.3522 | 22.1355 | 20.2572 | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 27.9207 | 25.4654 | 25.3306 | 22.7903 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 14.9958 | 14.9958 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.8935 | 5.0321 | 5.7782 | 5.1106 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7267.7584 | 6314.2624 | 7352.5136 | 6568.528 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7140.6256 | 6187.1296 | 7225.3808 | 6441.3952 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6526.1504 | 5805.7312 | 6632.0944 | 6081.1856 | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8878.1072 | 7649.1568 | 8899.296 | 7585.5904 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 4492.0256 | 4492.0256 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1758.6704 | 1504.4048 | 1906.992 | 1525.5936 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
ME_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | [6 empty] | 2015-03-31
ME_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
ME_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
ME_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
ME_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
ME_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
ME_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
ME_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7258.7744 | 6303.7316 | 7357.4082 | 6572.5115 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7135.2648 | 6186.4092 | 7235.1912 | 6439.2763 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6527.7819 | 5807.278 | 6642.4981 | 6078.8337 | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 2584.9912 | 2584.9912 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ME_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ME_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ME_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.5698 | 1.4477 | 1.7144 | 1.5656 | [6 empty] | 2015-03-31
ME_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 157.8345 | 145.5557 | 172.3738 | 157.4078 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.6277 | 9.2999 | 10.7722 | 9.6964 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.4469 | 9.1268 | 10.5932 | 9.4999 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.6304 | 8.5675 | 9.7997 | 8.9681 | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 12.9895 | 11.1932 | 13.0199 | 11.0942 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 3.0475 | 3.0475 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2392 | 1.0581 | 1.3335 | 1.0746 | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
ME_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.4117 | 3.1463 | 3.7259 | 3.4025 | [6 empty] | 2015-03-31
ME_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ME_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 103.7833 | 98.4914 | 104.9444 | 97.7223 | [6 empty] | 2015-03-31
ME_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.792 | 1.6426 | 1.7429 | 1.5528 | [6 empty] | 2015-03-31
ME_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 4.913 | 4.7735 | 4.6146 | 4.44 | [6 empty] | 2015-03-31
ME_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.4241 | 2.2755 | 2.4078 | 2.2608 | [6 empty] | 2015-03-31
ME_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 3.8893 | 3.8544 | 3.7616 | 3.7402 | [6 empty] | 2015-03-31
ME_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 635.664 | 572.0976 | 678.0416 | 593.2864 | [6 empty] | 2015-03-31
ME_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1525.5936 | 1462.0272 | 1525.5936 | 1440.8384 | [6 empty] | 2015-03-31
ME_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 720.4192 | 678.0416 | 741.608 | 678.0416 | [6 empty] | 2015-03-31
ME_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1462.0272 | 1440.8384 | 1504.4048 | 1483.216 | [6 empty] | 2015-03-31
ME_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
ME_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
ME_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
ME_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
ME_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ME_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ME_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | No | [6 empty] | 2015-03-31
ME_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ME_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ME_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.0634 | 1.0344 | 1.0704 | 1.0289 | [6 empty] | 2015-03-31
ME_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0356 | 1.0236 | 1.0485 | 1.0532 | [6 empty] | 2015-03-31
ME_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.47823 | 0.46865 | 0.40989 | 0.41714 | [6 empty] | 2015-03-31
ME_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.47379 | 0.46457 | 0.40557 | 0.41243 | [6 empty] | 2015-03-31
ME_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.57463 | 0.56993 | 0.48405 | 0.51044 | [6 empty] | 2015-03-31
ME_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.75588 | 0.73593 | 0.6634 | 0.69168 | [6 empty] | 2015-03-31
ME_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.58224 | 0.56933 | 0.53131 | 0.56023 | [6 empty] | 2015-03-31
ME_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.5961 | 0.58377 | 0.54578 | 0.57487 | [6 empty] | 2015-03-31
ME_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.81421 | 0.78735 | 0.72942 | 0.7727 | [6 empty] | 2015-03-31
ME_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.342 | 1.3058 | 1.2127 | 1.2295 | [6 empty] | 2015-03-31
ME_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3345 | 1.2989 | 1.205 | 1.221 | [6 empty] | 2015-03-31
ME_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6386 | 1.6065 | 1.465 | 1.5294 | [6 empty] | 2015-03-31
ME_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.0442 | 1.9808 | 1.8719 | 1.9354 | [6 empty] | 2015-03-31
ME_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6163 | 1.569 | 1.5393 | 1.5981 | [6 empty] | 2015-03-31
ME_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.6218 | 1.574 | 1.5416 | 1.604 | [6 empty] | 2015-03-31
ME_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.0565 | 1.9845 | 1.9233 | 2.0142 | [6 empty] | 2015-03-31
ME_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.2013 | 2.118 | 2.0228 | 2.1184 | [6 empty] | 2015-03-31
ME_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0375 | 2.0299 | 2.0652 | 2.1242 | [6 empty] | 2015-03-31
ME_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.90836 | 0.79428 | 0.81753 | 0.72847 | [6 empty] | 2015-03-31
ME_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.90872 | 0.78608 | 0.81777 | 0.71852 | [6 empty] | 2015-03-31
ME_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1203 | 0.97712 | 0.99709 | 0.90575 | [6 empty] | 2015-03-31
ME_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.3228 | 1.2144 | 1.203 | 1.1635 | [6 empty] | 2015-03-31
ME_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.1532 | 1.0355 | 1.0947 | 1.034 | [6 empty] | 2015-03-31
ME_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.1569 | 1.039 | 1.0987 | 1.0382 | [6 empty] | 2015-03-31
ME_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.3786 | 1.2504 | 1.2876 | 1.2437 | [6 empty] | 2015-03-31
ME_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.4719 | 1.3403 | 1.3745 | 1.3339 | [6 empty] | 2015-03-31
ME_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ME_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
ME_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ME_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ME_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ME_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ME_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ME_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ME_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ME_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ME_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
ME_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ME_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 169.5104 | 169.5104 | 148.3216 | 169.5104 | [6 empty] | 2015-03-31
ME_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 169.5104 | 169.5104 | 148.3216 | 148.3216 | [6 empty] | 2015-03-31
ME_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 190.6992 | 211.888 | [6 empty] | 2015-03-31
ME_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 296.6432 | 275.4544 | 275.4544 | 296.6432 | [6 empty] | 2015-03-31
ME_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 211.888 | 211.888 | [6 empty] | 2015-03-31
ME_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 233.0768 | [6 empty] | 2015-03-31
ME_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 296.6432 | 296.6432 | 317.832 | [6 empty] | 2015-03-31
ME_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 508.5312 | 508.5312 | [6 empty] | 2015-03-31
ME_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 487.3424 | 487.3424 | 508.5312 | [6 empty] | 2015-03-31
ME_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 635.664 | 656.8528 | [6 empty] | 2015-03-31
ME_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 826.3632 | 805.1744 | 805.1744 | 826.3632 | [6 empty] | 2015-03-31
ME_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 635.664 | 656.8528 | [6 empty] | 2015-03-31
ME_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 635.664 | 656.8528 | [6 empty] | 2015-03-31
ME_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 783.9856 | 805.1744 | 847.552 | [6 empty] | 2015-03-31
ME_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 847.552 | 868.7408 | 911.1184 | [6 empty] | 2015-03-31
ME_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 911.1184 | 932.3072 | 953.496 | [6 empty] | 2015-03-31
ME_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 317.832 | 339.0208 | 296.6432 | [6 empty] | 2015-03-31
ME_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 296.6432 | 339.0208 | 296.6432 | [6 empty] | 2015-03-31
ME_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 402.5872 | 423.776 | 402.5872 | [6 empty] | 2015-03-31
ME_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 487.3424 | 529.72 | 508.5312 | [6 empty] | 2015-03-31
ME_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 402.5872 | 466.1536 | 444.9648 | [6 empty] | 2015-03-31
ME_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 423.776 | 466.1536 | 444.9648 | [6 empty] | 2015-03-31
ME_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 508.5312 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
ME_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 593.2864 | 572.0976 | [6 empty] | 2015-03-31
ME_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ME_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.11932 | 0.11615 | 0.11077 | 0.11322 | [6 empty] | 2015-03-31
ME_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.11788 | 0.1148 | 0.10931 | 0.11163 | [6 empty] | 2015-03-31
ME_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.15141 | 0.15048 | 0.13634 | 0.14688 | [6 empty] | 2015-03-31
ME_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.20681 | 0.20011 | 0.19311 | 0.20296 | [6 empty] | 2015-03-31
ME_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.14581 | 0.14187 | 0.14301 | 0.15298 | [6 empty] | 2015-03-31
ME_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15052 | 0.14677 | 0.14812 | 0.15815 | [6 empty] | 2015-03-31
ME_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.22205 | 0.21305 | 0.20703 | 0.22122 | [6 empty] | 2015-03-31
ME_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.36401 | 0.35178 | 0.35465 | 0.35803 | [6 empty] | 2015-03-31
ME_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.36149 | 0.34947 | 0.352 | 0.35508 | [6 empty] | 2015-03-31
ME_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.4645 | 0.45365 | 0.4444 | 0.46733 | [6 empty] | 2015-03-31
ME_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.58815 | 0.56473 | 0.57067 | 0.59291 | [6 empty] | 2015-03-31
ME_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.43837 | 0.4226 | 0.44663 | 0.46798 | [6 empty] | 2015-03-31
ME_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.44022 | 0.4243 | 0.44844 | 0.47004 | [6 empty] | 2015-03-31
ME_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.57726 | 0.55313 | 0.57305 | 0.60452 | [6 empty] | 2015-03-31
ME_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.6343 | 0.60436 | 0.6178 | 0.64754 | [6 empty] | 2015-03-31
ME_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65021 | 0.64779 | 0.65906 | 0.67789 | [6 empty] | 2015-03-31
ME_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.24877 | 0.21943 | 0.23636 | 0.21584 | [6 empty] | 2015-03-31
ME_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.24891 | 0.21668 | 0.23642 | 0.21239 | [6 empty] | 2015-03-31
ME_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.31361 | 0.27833 | 0.29384 | 0.2782 | [6 empty] | 2015-03-31
ME_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.38714 | 0.35139 | 0.37059 | 0.35988 | [6 empty] | 2015-03-31
ME_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.3321 | 0.29249 | 0.33399 | 0.3129 | [6 empty] | 2015-03-31
ME_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.33335 | 0.29367 | 0.33536 | 0.31438 | [6 empty] | 2015-03-31
ME_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.4016 | 0.35848 | 0.39625 | 0.38102 | [6 empty] | 2015-03-31
ME_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.43174 | 0.38833 | 0.42345 | 0.41031 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6419 | 1.5536 | 1.4496 | 1.3538 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9044 | 1.8003 | 1.7408 | 1.6751 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3636 | 1.3269 | 1.3324 | 1.3823 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.554 | 1.4815 | 1.3283 | 1.1797 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5437 | 1.4853 | 1.5043 | 1.5204 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 593.2864 | 550.9088 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 783.9856 | 741.608 | 783.9856 | 762.7968 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 593.2864 | 614.4752 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 572.0976 | 529.72 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 678.0416 | 678.0416 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42716 | 0.39633 | 0.4199 | 0.38451 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.55896 | 0.52091 | 0.55553 | 0.53457 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.43515 | 0.42344 | 0.42521 | 0.44112 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.43237 | 0.40637 | 0.40302 | 0.37272 | [6 empty] | 2015-03-31
MN_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.49265 | 0.47401 | 0.48007 | 0.48521 | [6 empty] | 2015-03-31
MN_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10107.0576 | 9704.4704 | 10064.68 | 9683.2816 | [6 empty] | 2015-03-31
MN_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25045.1616 | 24663.7632 | 24960.4064 | 25023.9728 | [6 empty] | 2015-03-31
MN_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 203751.5011 | 199365.4195 | 201505.4883 | 202819.1939 | [6 empty] | 2015-03-31
MN_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23837.4 | 21993.9744 | 23307.68 | 22078.7296 | [6 empty] | 2015-03-31
MN_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
MN_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
MN_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
MN_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
MN_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
MN_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
MN_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
MN_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
MN_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
MN_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
MN_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
MN_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MN_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MN_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MN_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MN_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MN_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
MN_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MN_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MN_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MN_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 380.6048 | 374.7022 | 334.6557 | 333.8442 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 380.6048 | 374.7022 | 334.6557 | 333.8442 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
MN_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 361.2478 | 355.6509 | 317.6366 | 316.8692 | [6 empty] | 2015-03-31
MN_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 361.2478 | 355.6509 | 317.6366 | 316.8692 | [6 empty] | 2015-03-31
MN_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.8113 | 5.6659 | 5.9847 | 5.8432 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1792.196 | 882.2242 | 1575.8724 | 786.0254 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 882.2242 | 0 | 786.0254 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1792.196 | 1764.458 | 1575.8724 | 1572.0509 | [6 empty] | 2015-03-31
MN_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1168.5698 | 1139.3387 | 1203.4326 | 1174.9781 | [6 empty] | 2015-03-31
MN_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2091.1331 | 2050.8733 | 1838.6375 | 1827.2253 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
MN_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.844 | 10.4258 | 10.7909 | 10.3833 | [6 empty] | 2015-03-31
MN_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 36.0197 | 35.4647 | 35.8936 | 35.9736 | [6 empty] | 2015-03-31
MN_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 286.547 | 280.358 | 283.3796 | 285.2224 | [6 empty] | 2015-03-31
MN_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 34.2759 | 31.6158 | 33.5175 | 31.7424 | [6 empty] | 2015-03-31
MN_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.748 | 43.6564 | 44.597 | 44.5049 | [6 empty] | 2015-03-31
MN_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.83102 | 0.8142 | 0.85091 | 0.85682 | [6 empty] | 2015-03-31
MN_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.4936 | 10.227 | 10.7477 | 10.8599 | [6 empty] | 2015-03-31
MN_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.71849 | 0.69293 | 0.73256 | 0.73137 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.6685 | 4.7593 | 8.5013 | 4.2403 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.7593 | 0 | 4.2403 | [6 empty] | 2015-03-31
MN_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 29.0056 | 28.5557 | 25.5038 | 25.442 | [6 empty] | 2015-03-31
MN_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 25.2593 | 24.6275 | 26.0129 | 25.3978 | [6 empty] | 2015-03-31
MN_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 38.7305 | 37.9847 | 34.0547 | 33.8428 | [6 empty] | 2015-03-31
MN_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8812 | 3.8532 | 3.8693 | 3.871 | [6 empty] | 2015-03-31
MN_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 5171.5914 | 4997.0995 | 5203.0777 | 5055.882 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.7996 | 8.7438 | 7.8249 | 7.8027 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 37.2281 | 36.5717 | 32.7762 | 32.3277 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4893 | 6.2711 | 5.8526 | 5.8041 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6496 | 5.357 | 5.0265 | 4.899 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3305.4528 | 3263.0752 | 3051.1872 | 3051.1872 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12734.4688 | 11971.672 | 12353.0704 | 11759.784 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2669.7888 | 2542.656 | 2627.4112 | 2606.2224 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2224.824 | 2055.3136 | 2182.4464 | 2118.88 | [6 empty] | 2015-03-31
MN_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
MN_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.6783 | 3.2355 | 8.1221 | 3.5492 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2347 | 2.2047 | 2.0726 | 2.0679 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.668 | 12.8428 | 13.2523 | 12.6145 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8643 | 1.7835 | 1.8461 | 1.8285 | [6 empty] | 2015-03-31
MN_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5545 | 1.4473 | 1.5242 | 1.4776 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 26.287 | 22.6638 | 25.4306 | 22.3886 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.9263 | 22.3529 | 25.0773 | 22.0014 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.6678 | 21.0117 | 22.9196 | 20.8082 | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.816 | 27.4314 | 27.1807 | 24.5454 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 14.9958 | 14.9958 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.4341 | 5.4599 | 6.3209 | 5.4126 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7882.2336 | 6801.6048 | 7627.968 | 6716.8496 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7776.2896 | 6716.8496 | 7522.024 | 6610.9056 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7098.248 | 6314.2624 | 6886.36 | 6250.696 | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9556.1488 | 8221.2544 | 9217.128 | 7839.856 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 4492.0256 | 4492.0256 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1928.1808 | 1631.5376 | 1991.7472 | 1631.5376 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
MN_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | n/a | [6 empty] | 2015-03-31
MN_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MN_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
MN_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
MN_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
MN_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
MN_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
MN_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 6801.0327 | 7631.2947 | 6718.46 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7780.0612 | 6707.7384 | 7525.2871 | 6602.2394 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6305.2784 | 6777.6191 | 6244.2122 | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 2584.9912 | 2584.9912 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
MN_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
MN_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.7566 | 1.5895 | 1.772 | 1.5968 | [6 empty] | 2015-03-31
MN_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 176.617 | 159.8141 | 178.1656 | 160.5432 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.5494 | 9.9576 | 11.1732 | 9.9117 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.391 | 9.8959 | 11.018 | 9.7403 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.3987 | 9.3022 | 10.0699 | 9.2121 | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.9786 | 12.0522 | 13.4844 | 11.4642 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 3.0475 | 3.0475 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3529 | 1.1481 | 1.4006 | 1.1381 | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
MN_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.8177 | 3.4545 | 3.8512 | 3.4702 | [6 empty] | 2015-03-31
MN_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
MN_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 106.3152 | 98.8067 | 105.6859 | 96.9928 | [6 empty] | 2015-03-31
MN_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0511 | 1.92 | 1.83 | 1.643 | [6 empty] | 2015-03-31
MN_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3768 | 5.1781 | 4.8661 | 4.6784 | [6 empty] | 2015-03-31
MN_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5557 | 2.4025 | 2.5254 | 2.3344 | [6 empty] | 2015-03-31
MN_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.2522 | 4.213 | 3.8939 | 3.8714 | [6 empty] | 2015-03-31
MN_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 635.664 | 699.2304 | 614.4752 | [6 empty] | 2015-03-31
MN_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1610.3488 | 1546.7824 | 1589.16 | 1504.4048 | [6 empty] | 2015-03-31
MN_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 699.2304 | [6 empty] | 2015-03-31
MN_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1546.7824 | 1525.5936 | [6 empty] | 2015-03-31
MN_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
MN_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
MN_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
MN_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
MN_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
MN_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MN_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
MN_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MN_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
MN_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1306 | 1.0888 | 1.1101 | 1.052 | [6 empty] | 2015-03-31
MN_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0719 | 1.0587 | 1.0814 | 1.0735 | [6 empty] | 2015-03-31
MN_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.58191 | 0.57071 | 0.44488 | 0.4533 | [6 empty] | 2015-03-31
MN_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.57656 | 0.56576 | 0.43996 | 0.44793 | [6 empty] | 2015-03-31
MN_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.71356 | 0.6979 | 0.53689 | 0.56675 | [6 empty] | 2015-03-31
MN_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.921 | 0.89602 | 0.72109 | 0.75248 | [6 empty] | 2015-03-31
MN_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.69818 | 0.67892 | 0.56118 | 0.59049 | [6 empty] | 2015-03-31
MN_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.7105 | 0.69305 | 0.57551 | 0.60499 | [6 empty] | 2015-03-31
MN_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.97761 | 0.94226 | 0.77389 | 0.81085 | [6 empty] | 2015-03-31
MN_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5801 | 1.539 | 1.2944 | 1.3063 | [6 empty] | 2015-03-31
MN_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5711 | 1.5306 | 1.286 | 1.2972 | [6 empty] | 2015-03-31
MN_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.9823 | 1.9262 | 1.6026 | 1.6617 | [6 empty] | 2015-03-31
MN_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.4359 | 2.3528 | 2.0047 | 2.0747 | [6 empty] | 2015-03-31
MN_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8974 | 1.8302 | 1.6122 | 1.6745 | [6 empty] | 2015-03-31
MN_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8994 | 1.8353 | 1.6178 | 1.6804 | [6 empty] | 2015-03-31
MN_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.4212 | 2.3232 | 2.0305 | 2.1198 | [6 empty] | 2015-03-31
MN_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5948 | 2.4838 | 2.1569 | 2.2505 | [6 empty] | 2015-03-31
MN_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1007 | 2.0944 | 2.0799 | 2.1366 | [6 empty] | 2015-03-31
MN_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0621 | 0.93495 | 0.85975 | 0.77235 | [6 empty] | 2015-03-31
MN_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0641 | 0.92548 | 0.86227 | 0.7585 | [6 empty] | 2015-03-31
MN_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.323 | 1.1792 | 1.0621 | 0.99392 | [6 empty] | 2015-03-31
MN_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5523 | 1.4356 | 1.2759 | 1.2494 | [6 empty] | 2015-03-31
MN_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3422 | 1.2045 | 1.1439 | 1.0785 | [6 empty] | 2015-03-31
MN_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.346 | 1.208 | 1.1476 | 1.0833 | [6 empty] | 2015-03-31
MN_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6123 | 1.458 | 1.3562 | 1.3085 | [6 empty] | 2015-03-31
MN_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7047 | 1.5471 | 1.4317 | 1.3943 | [6 empty] | 2015-03-31
MN_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
MN_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
MN_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MN_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MN_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MN_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MN_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MN_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MN_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MN_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
MN_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
MN_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
MN_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | [6 empty] | 2015-03-31
MN_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | [6 empty] | 2015-03-31
MN_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 211.888 | 211.888 | [6 empty] | 2015-03-31
MN_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 296.6432 | 317.832 | [6 empty] | 2015-03-31
MN_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 211.888 | 211.888 | [6 empty] | 2015-03-31
MN_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 211.888 | 233.0768 | [6 empty] | 2015-03-31
MN_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | 317.832 | 339.0208 | [6 empty] | 2015-03-31
MN_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 529.72 | 529.72 | [6 empty] | 2015-03-31
MN_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 550.9088 | 529.72 | 529.72 | [6 empty] | 2015-03-31
MN_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 656.8528 | 699.2304 | [6 empty] | 2015-03-31
MN_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | 847.552 | 889.9296 | [6 empty] | 2015-03-31
MN_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 656.8528 | 678.0416 | [6 empty] | 2015-03-31
MN_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 656.8528 | 656.8528 | 678.0416 | [6 empty] | 2015-03-31
MN_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 868.7408 | 847.552 | 889.9296 | [6 empty] | 2015-03-31
MN_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 974.6848 | 932.3072 | 974.6848 | [6 empty] | 2015-03-31
MN_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 932.3072 | 932.3072 | 953.496 | [6 empty] | 2015-03-31
MN_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
MN_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
MN_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 444.9648 | 423.776 | [6 empty] | 2015-03-31
MN_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 550.9088 | 550.9088 | [6 empty] | 2015-03-31
MN_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 487.3424 | 444.9648 | [6 empty] | 2015-03-31
MN_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 487.3424 | 466.1536 | [6 empty] | 2015-03-31
MN_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
MN_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 614.4752 | 593.2864 | [6 empty] | 2015-03-31
MN_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
MN_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14028 | 0.13653 | 0.11763 | 0.12052 | [6 empty] | 2015-03-31
MN_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.13853 | 0.13492 | 0.11597 | 0.11868 | [6 empty] | 2015-03-31
MN_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.17967 | 0.17546 | 0.14636 | 0.15718 | [6 empty] | 2015-03-31
MN_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.24605 | 0.23762 | 0.20807 | 0.2192 | [6 empty] | 2015-03-31
MN_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16719 | 0.16128 | 0.14698 | 0.15719 | [6 empty] | 2015-03-31
MN_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.17168 | 0.16599 | 0.15209 | 0.16236 | [6 empty] | 2015-03-31
MN_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.26159 | 0.24968 | 0.22394 | 0.23704 | [6 empty] | 2015-03-31
MN_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.41426 | 0.40032 | 0.37313 | 0.37727 | [6 empty] | 2015-03-31
MN_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.41125 | 0.39753 | 0.37018 | 0.37405 | [6 empty] | 2015-03-31
MN_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.53685 | 0.5179 | 0.47248 | 0.49592 | [6 empty] | 2015-03-31
MN_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.68176 | 0.65352 | 0.60724 | 0.63224 | [6 empty] | 2015-03-31
MN_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.49241 | 0.47122 | 0.45949 | 0.48133 | [6 empty] | 2015-03-31
MN_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.49415 | 0.47295 | 0.46147 | 0.48343 | [6 empty] | 2015-03-31
MN_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.65395 | 0.62131 | 0.59602 | 0.6286 | [6 empty] | 2015-03-31
MN_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.73141 | 0.69375 | 0.65981 | 0.6911 | [6 empty] | 2015-03-31
MN_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.66638 | 0.66407 | 0.66375 | 0.68184 | [6 empty] | 2015-03-31
MN_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.28094 | 0.25164 | 0.24597 | 0.22748 | [6 empty] | 2015-03-31
MN_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.28082 | 0.24845 | 0.24613 | 0.22375 | [6 empty] | 2015-03-31
MN_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.35666 | 0.32093 | 0.30853 | 0.29732 | [6 empty] | 2015-03-31
MN_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.44569 | 0.40719 | 0.39422 | 0.38579 | [6 empty] | 2015-03-31
MN_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.37365 | 0.32754 | 0.34492 | 0.32254 | [6 empty] | 2015-03-31
MN_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.37494 | 0.32874 | 0.34625 | 0.32425 | [6 empty] | 2015-03-31
MN_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.45398 | 0.40311 | 0.4123 | 0.39622 | [6 empty] | 2015-03-31
MN_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.48735 | 0.43654 | 0.44098 | 0.42773 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.5415 | 1.4554 | 1.4739 | 1.372 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.9026 | 1.7906 | 1.9597 | 1.8904 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.3794 | 1.3452 | 1.4115 | 1.4591 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4841 | 1.4131 | 1.4072 | 1.2665 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.6582 | 1.604 | 1.6203 | 1.6226 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 614.4752 | 572.0976 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 847.552 | 805.1744 | 889.9296 | 847.552 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 614.4752 | 614.4752 | 635.664 | 656.8528 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 635.664 | 593.2864 | 614.4752 | 572.0976 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 741.608 | 720.4192 | 720.4192 | 720.4192 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.44307 | 0.41105 | 0.4367 | 0.39807 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.60716 | 0.5665 | 0.62537 | 0.60327 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.44019 | 0.4293 | 0.45044 | 0.46564 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.45131 | 0.42454 | 0.43729 | 0.40418 | [6 empty] | 2015-03-31
ND_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.52917 | 0.51188 | 0.51706 | 0.51781 | [6 empty] | 2015-03-31
ND_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10424.8896 | 10022.3024 | 10191.8128 | 9810.4144 | [6 empty] | 2015-03-31
ND_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 25850.336 | 25490.1264 | 25574.8816 | 25659.6368 | [6 empty] | 2015-03-31
ND_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 210637.8611 | 206442.4787 | 206357.7235 | 207480.7299 | [6 empty] | 2015-03-31
ND_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 24960.4064 | 23053.4144 | 24727.3296 | 23265.3024 | [6 empty] | 2015-03-31
ND_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ND_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
ND_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
ND_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
ND_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
ND_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
ND_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
ND_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
ND_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
ND_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
ND_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
ND_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
ND_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ND_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ND_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ND_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
ND_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
ND_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
ND_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ND_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ND_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ND_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 338.2841 | 332.587 | 327.4773 | 326.6249 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 338.2841 | 332.587 | 327.4773 | 326.6249 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
ND_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 321.0768 | 315.6783 | 310.8224 | 310.0152 | [6 empty] | 2015-03-31
ND_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 321.0768 | 315.6783 | 310.8224 | 310.0152 | [6 empty] | 2015-03-31
ND_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 6.0335 | 5.8915 | 6.0241 | 5.871 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1592.9575 | 783.0662 | 1542.07 | 769.0276 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 783.0662 | 0 | 769.0276 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1592.9575 | 1566.1308 | 1542.07 | 1538.0551 | [6 empty] | 2015-03-31
ND_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1213.2503 | 1184.6928 | 1211.3673 | 1180.5844 | [6 empty] | 2015-03-31
ND_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1858.6089 | 1820.4096 | 1799.1702 | 1787.7579 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
ND_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.1842 | 10.752 | 10.9358 | 10.5202 | [6 empty] | 2015-03-31
ND_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 37.1603 | 36.6436 | 36.7551 | 36.883 | [6 empty] | 2015-03-31
ND_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 296.2302 | 290.305 | 290.2114 | 291.767 | [6 empty] | 2015-03-31
ND_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 35.8735 | 33.1548 | 35.5471 | 33.463 | [6 empty] | 2015-03-31
ND_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 45.0615 | 44.9677 | 45.0967 | 45.0033 | [6 empty] | 2015-03-31
ND_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.86584 | 0.84742 | 0.8683 | 0.87396 | [6 empty] | 2015-03-31
ND_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.97 | 10.6816 | 11.0053 | 11.1109 | [6 empty] | 2015-03-31
ND_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.75099 | 0.72407 | 0.75127 | 0.74897 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 8.5934 | 4.2244 | 8.3189 | 4.1486 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.2244 | 0 | 4.1486 | [6 empty] | 2015-03-31
ND_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 25.7803 | 25.3462 | 24.9568 | 24.8918 | [6 empty] | 2015-03-31
ND_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 26.2251 | 25.6078 | 26.1844 | 25.519 | [6 empty] | 2015-03-31
ND_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 34.424 | 33.7154 | 33.3243 | 33.111 | [6 empty] | 2015-03-31
ND_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8897 | 3.8611 | 3.8829 | 3.8839 | [6 empty] | 2015-03-31
ND_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 5304.058 | 5114.1735 | 5293.4873 | 5138.4277 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 7.8954 | 7.8507 | 7.7379 | 7.7516 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 32.1655 | 31.4786 | 31.2059 | 30.8309 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.3207 | 6.077 | 6.3171 | 6.2301 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.457 | 5.1553 | 5.4414 | 5.2824 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3369.0192 | 3326.6416 | 3241.8864 | 3241.8864 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13285.3776 | 12416.6368 | 12543.7696 | 11950.4832 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2818.1104 | 2712.1664 | 2839.2992 | 2796.9216 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2351.9568 | 2203.6352 | 2373.1456 | 2288.3904 | [6 empty] | 2015-03-31
ND_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
ND_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ND_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 8.1878 | 3.5801 | 8.1668 | 3.5699 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2874 | 2.2535 | 2.1901 | 2.1895 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.2604 | 13.3148 | 13.4715 | 12.829 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.9786 | 1.8943 | 1.9926 | 1.9652 | [6 empty] | 2015-03-31
ND_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.654 | 1.5413 | 1.6673 | 1.6108 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 27.8032 | 23.9278 | 27.8954 | 23.9221 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 27.4598 | 23.6569 | 27.5466 | 23.554 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 24.965 | 22.2383 | 25.0008 | 22.3841 | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 28.6901 | 26.0806 | 27.8038 | 24.8804 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 11.1636 | 14.9958 | 14.9958 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.2281 | 5.4747 | 6.4303 | 5.7478 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 8348.3872 | 7183.0032 | 8369.576 | 7183.0032 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 8242.4432 | 7098.248 | 8263.632 | 7077.0592 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 7500.8352 | 6674.472 | 7500.8352 | 6716.8496 | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9937.5472 | 8602.6528 | 9895.1696 | 8369.576 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | 4492.0256 | 4492.0256 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1928.1808 | 1652.7264 | 2118.88 | 1737.4816 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
ND_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
ND_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
ND_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
ND_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ND_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
ND_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
ND_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
ND_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
ND_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7180.3546 | 7852.8447 | 7178.6171 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7099.0532 | 7852.8447 | 7068.1599 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6673.349 | 6777.6191 | 6717.1039 | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 2584.9912 | 2584.9912 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ND_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ND_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ND_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | Yes | Yes | [6 empty] | 2015-03-31
ND_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
ND_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
ND_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.8607 | 1.6585 | 1.864 | 1.6442 | [6 empty] | 2015-03-31
ND_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 187.0845 | 166.7549 | 187.4158 | 165.3157 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 12.2156 | 10.5129 | 12.2561 | 10.5104 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 12.0647 | 10.3939 | 12.1028 | 10.3487 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.9686 | 9.8452 | 10.9843 | 9.9097 | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 14.5639 | 12.5921 | 14.5011 | 12.2641 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | 3.0475 | 3.0475 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3584 | 1.1512 | 1.4896 | 1.2105 | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
ND_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 4.0439 | 3.6045 | 4.0511 | 3.5734 | [6 empty] | 2015-03-31
ND_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
ND_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 108.2422 | 98.2699 | 108.9108 | 97.6568 | [6 empty] | 2015-03-31
ND_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.9854 | 1.849 | 1.9852 | 1.7785 | [6 empty] | 2015-03-31
ND_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.2336 | 5.1112 | 5.0912 | 4.8803 | [6 empty] | 2015-03-31
ND_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.6496 | 2.5205 | 2.6357 | 2.463 | [6 empty] | 2015-03-31
ND_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.1567 | 4.1144 | 4.1015 | 4.0691 | [6 empty] | 2015-03-31
ND_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 741.608 | 678.0416 | 762.7968 | 656.8528 | [6 empty] | 2015-03-31
ND_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1673.9152 | 1610.3488 | 1673.9152 | 1589.16 | [6 empty] | 2015-03-31
ND_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 805.1744 | 762.7968 | 783.9856 | 741.608 | [6 empty] | 2015-03-31
ND_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1589.16 | 1567.9712 | 1610.3488 | 1589.16 | [6 empty] | 2015-03-31
ND_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
ND_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
ND_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
ND_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
ND_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
ND_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ND_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
ND_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ND_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
ND_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.1737 | 1.1301 | 1.1703 | 1.1064 | [6 empty] | 2015-03-31
ND_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.1102 | 1.0962 | 1.1224 | 1.1114 | [6 empty] | 2015-03-31
ND_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.51541 | 0.50412 | 0.46622 | 0.47031 | [6 empty] | 2015-03-31
ND_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.50986 | 0.49891 | 0.46081 | 0.46461 | [6 empty] | 2015-03-31
ND_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.62293 | 0.60409 | 0.60173 | 0.62596 | [6 empty] | 2015-03-31
ND_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.86724 | 0.8427 | 0.78778 | 0.81456 | [6 empty] | 2015-03-31
ND_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.66443 | 0.64571 | 0.62924 | 0.65736 | [6 empty] | 2015-03-31
ND_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.67888 | 0.6601 | 0.64247 | 0.67117 | [6 empty] | 2015-03-31
ND_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.92836 | 0.89239 | 0.87061 | 0.90406 | [6 empty] | 2015-03-31
ND_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.4335 | 1.3923 | 1.3383 | 1.3465 | [6 empty] | 2015-03-31
ND_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.4238 | 1.3832 | 1.329 | 1.3366 | [6 empty] | 2015-03-31
ND_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7617 | 1.66 | 1.7597 | 1.8228 | [6 empty] | 2015-03-31
ND_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3246 | 2.2432 | 2.1467 | 2.2053 | [6 empty] | 2015-03-31
ND_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8365 | 1.7637 | 1.7798 | 1.8397 | [6 empty] | 2015-03-31
ND_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8417 | 1.7689 | 1.7853 | 1.8458 | [6 empty] | 2015-03-31
ND_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.345 | 2.244 | 2.2627 | 2.3532 | [6 empty] | 2015-03-31
ND_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5072 | 2.3947 | 2.3926 | 2.4713 | [6 empty] | 2015-03-31
ND_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2188 | 2.2108 | 2.1124 | 2.1642 | [6 empty] | 2015-03-31
ND_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0081 | 0.86569 | 0.94042 | 0.82247 | [6 empty] | 2015-03-31
ND_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0078 | 0.85546 | 0.95291 | 0.81146 | [6 empty] | 2015-03-31
ND_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2556 | 1.1198 | 1.1869 | 1.1027 | [6 empty] | 2015-03-31
ND_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.4926 | 1.3737 | 1.421 | 1.3666 | [6 empty] | 2015-03-31
ND_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3154 | 1.1725 | 1.2785 | 1.1972 | [6 empty] | 2015-03-31
ND_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3186 | 1.1761 | 1.2822 | 1.2014 | [6 empty] | 2015-03-31
ND_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5732 | 1.4153 | 1.5232 | 1.4594 | [6 empty] | 2015-03-31
ND_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6991 | 1.5458 | 1.5962 | 1.54 | [6 empty] | 2015-03-31
ND_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
ND_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
ND_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ND_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ND_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ND_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ND_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ND_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ND_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ND_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
ND_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
ND_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
ND_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
ND_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | 190.6992 | 190.6992 | [6 empty] | 2015-03-31
ND_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
ND_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 360.2096 | 339.0208 | 360.2096 | [6 empty] | 2015-03-31
ND_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 233.0768 | 254.2656 | [6 empty] | 2015-03-31
ND_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 254.2656 | 254.2656 | [6 empty] | 2015-03-31
ND_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 381.3984 | 381.3984 | 381.3984 | [6 empty] | 2015-03-31
ND_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | 572.0976 | 572.0976 | [6 empty] | 2015-03-31
ND_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 572.0976 | [6 empty] | 2015-03-31
ND_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 783.9856 | [6 empty] | 2015-03-31
ND_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1017.0624 | 974.6848 | 953.496 | 995.8736 | [6 empty] | 2015-03-31
ND_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 720.4192 | 741.608 | 762.7968 | [6 empty] | 2015-03-31
ND_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 720.4192 | 741.608 | 762.7968 | [6 empty] | 2015-03-31
ND_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 974.6848 | 932.3072 | 953.496 | 995.8736 | [6 empty] | 2015-03-31
ND_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1101.8176 | 1038.2512 | 1059.44 | 1101.8176 | [6 empty] | 2015-03-31
ND_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 995.8736 | 995.8736 | 953.496 | 974.6848 | [6 empty] | 2015-03-31
ND_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
ND_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 402.5872 | 360.2096 | 402.5872 | 360.2096 | [6 empty] | 2015-03-31
ND_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 466.1536 | 508.5312 | 487.3424 | [6 empty] | 2015-03-31
ND_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 614.4752 | 635.664 | 614.4752 | [6 empty] | 2015-03-31
ND_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 487.3424 | 550.9088 | 508.5312 | [6 empty] | 2015-03-31
ND_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 487.3424 | 550.9088 | 508.5312 | [6 empty] | 2015-03-31
ND_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 656.8528 | 635.664 | [6 empty] | 2015-03-31
ND_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 656.8528 | 720.4192 | 678.0416 | [6 empty] | 2015-03-31
ND_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
ND_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14581 | 0.14187 | 0.13322 | 0.13559 | [6 empty] | 2015-03-31
ND_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.14389 | 0.14007 | 0.13134 | 0.13361 | [6 empty] | 2015-03-31
ND_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.17958 | 0.17302 | 0.17288 | 0.183 | [6 empty] | 2015-03-31
ND_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.26079 | 0.25223 | 0.24089 | 0.25037 | [6 empty] | 2015-03-31
ND_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.181 | 0.17469 | 0.17195 | 0.18157 | [6 empty] | 2015-03-31
ND_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.18595 | 0.17962 | 0.17651 | 0.18627 | [6 empty] | 2015-03-31
ND_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.27617 | 0.26374 | 0.26438 | 0.27618 | [6 empty] | 2015-03-31
ND_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.42946 | 0.41501 | 0.40897 | 0.41185 | [6 empty] | 2015-03-31
ND_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.4261 | 0.41183 | 0.40566 | 0.40834 | [6 empty] | 2015-03-31
ND_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.53416 | 0.51435 | 0.53695 | 0.55929 | [6 empty] | 2015-03-31
ND_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.72223 | 0.69375 | 0.68296 | 0.70378 | [6 empty] | 2015-03-31
ND_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.52961 | 0.50672 | 0.51951 | 0.54016 | [6 empty] | 2015-03-31
ND_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.53138 | 0.50849 | 0.52143 | 0.54224 | [6 empty] | 2015-03-31
ND_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.69763 | 0.6632 | 0.67826 | 0.70945 | [6 empty] | 2015-03-31
ND_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.77479 | 0.73574 | 0.755 | 0.78286 | [6 empty] | 2015-03-31
ND_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.70806 | 0.70551 | 0.67413 | 0.69064 | [6 empty] | 2015-03-31
ND_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.29159 | 0.26132 | 0.28289 | 0.25415 | [6 empty] | 2015-03-31
ND_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.29148 | 0.25776 | 0.28161 | 0.25026 | [6 empty] | 2015-03-31
ND_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.3707 | 0.32478 | 0.35524 | 0.34026 | [6 empty] | 2015-03-31
ND_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.46963 | 0.43009 | 0.45347 | 0.43433 | [6 empty] | 2015-03-31
ND_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.39713 | 0.34956 | 0.39194 | 0.36386 | [6 empty] | 2015-03-31
ND_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.39822 | 0.35081 | 0.39323 | 0.36531 | [6 empty] | 2015-03-31
ND_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.48124 | 0.42863 | 0.47114 | 0.44911 | [6 empty] | 2015-03-31
ND_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.52486 | 0.47247 | 0.50528 | 0.48562 | [6 empty] | 2015-03-31
VT_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.511 | 1.4296 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.7344 | 1.6385 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2607 | 1.2322 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.4257 | 1.3427 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.4567 | 1.4039 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 699.2304 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 656.8528 | 635.664 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.41483 | 0.38503 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52903 | 0.49383 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.40233 | 0.39321 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.41303 | 0.38588 | [8 empty] | 2015-03-31
VT_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.46487 | 0.44801 | [8 empty] | 2015-03-31
VT_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 9895.1696 | 9513.7712 | [8 empty] | 2015-03-31
VT_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24303.5536 | 23985.7216 | [8 empty] | 2015-03-31
VT_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 196780.3859 | 192987.5907 | [8 empty] | 2015-03-31
VT_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 22947.4704 | 21231.1776 | [8 empty] | 2015-03-31
VT_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
VT_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
VT_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
VT_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
VT_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
VT_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
VT_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
VT_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
VT_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
VT_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
VT_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
VT_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
VT_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
VT_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
VT_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
VT_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
VT_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
VT_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
VT_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
VT_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
VT_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
VT_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 346.1459 | 340.7369 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 346.1459 | 340.7369 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
VT_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 328.5394 | 323.4056 | [8 empty] | 2015-03-31
VT_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 328.5394 | 323.4056 | [8 empty] | 2015-03-31
VT_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.5791 | 5.4343 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1630.0472 | 802.2546 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 802.2546 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1630.0472 | 1604.5282 | [8 empty] | 2015-03-31
VT_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1121.87 | 1092.7625 | [8 empty] | 2015-03-31
VT_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1901.7218 | 1864.949 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
VT_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.6247 | 10.2157 | [8 empty] | 2015-03-31
VT_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 34.9494 | 34.4813 | [8 empty] | 2015-03-31
VT_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 276.727 | 271.4066 | [8 empty] | 2015-03-31
VT_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 32.996 | 30.5297 | [8 empty] | 2015-03-31
VT_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.9476 | 42.8586 | [8 empty] | 2015-03-31
VT_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.8026 | 0.78809 | [8 empty] | 2015-03-31
VT_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.0999 | 9.8649 | [8 empty] | 2015-03-31
VT_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.69143 | 0.66865 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 8.7932 | 4.3279 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.3279 | [8 empty] | 2015-03-31
VT_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 26.3795 | 25.9673 | [8 empty] | 2015-03-31
VT_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 24.2499 | 23.6207 | [8 empty] | 2015-03-31
VT_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 35.224 | 34.5416 | [8 empty] | 2015-03-31
VT_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8188 | 3.7933 | [8 empty] | 2015-03-31
VT_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 5000.3557 | 4833.6958 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.2091 | 8.1715 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 33.966 | 33.2807 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 5.9773 | 5.7824 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.1471 | 4.8792 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3135.9424 | 3093.5648 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12416.6368 | 11653.84 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2563.8448 | 2457.9008 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2118.88 | 1970.5584 | [8 empty] | 2015-03-31
VT_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
VT_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | [8 empty] | 2015-03-31
VT_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.3464 | 2.9808 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.122 | 2.0968 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.3236 | 12.5088 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.7932 | 1.7208 | [8 empty] | 2015-03-31
VT_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.4854 | 1.3867 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.1089 | 21.6798 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 24.6941 | 21.3025 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 22.6017 | 20.0969 | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 28.598 | 26.0537 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.0477 | 5.1371 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7543.2128 | 6504.9616 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7416.08 | 6399.0176 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6780.416 | 6038.808 | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9153.5616 | 7882.2336 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1822.2368 | 1546.7824 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
VT_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | [8 empty] | 2015-03-31
VT_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
VT_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
VT_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
VT_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
VT_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
VT_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
VT_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
VT_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7534.7797 | 6505.7668 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7410.2743 | 6392.5338 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6030.7563 | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VT_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VT_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VT_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | [8 empty] | 2015-03-31
VT_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
VT_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
VT_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.6752 | 1.5293 | [8 empty] | 2015-03-31
VT_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 168.4271 | 153.764 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.0319 | 9.5979 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.8496 | 9.4309 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.9303 | 8.8972 | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.3957 | 11.527 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.2717 | 1.0802 | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
VT_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.6407 | 3.3237 | [8 empty] | 2015-03-31
VT_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
VT_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 105.0671 | 98.765 | [8 empty] | 2015-03-31
VT_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.8406 | 1.6917 | [8 empty] | 2015-03-31
VT_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.0105 | 4.8723 | [8 empty] | 2015-03-31
VT_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.4643 | 2.3148 | [8 empty] | 2015-03-31
VT_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 3.9663 | 3.9291 | [8 empty] | 2015-03-31
VT_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 656.8528 | 593.2864 | [8 empty] | 2015-03-31
VT_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1546.7824 | 1483.216 | [8 empty] | 2015-03-31
VT_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 741.608 | 699.2304 | [8 empty] | 2015-03-31
VT_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1483.216 | 1462.0272 | [8 empty] | 2015-03-31
VT_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
VT_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
VT_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
VT_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
VT_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
VT_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
VT_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
VT_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
VT_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
VT_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.082 | 1.0537 | [8 empty] | 2015-03-31
VT_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0545 | 1.0417 | [8 empty] | 2015-03-31
VT_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.49203 | 0.48291 | [8 empty] | 2015-03-31
VT_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.48732 | 0.47855 | [8 empty] | 2015-03-31
VT_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.58571 | 0.58048 | [8 empty] | 2015-03-31
VT_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.78756 | 0.76725 | [8 empty] | 2015-03-31
VT_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.60886 | 0.59438 | [8 empty] | 2015-03-31
VT_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.62141 | 0.60842 | [8 empty] | 2015-03-31
VT_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.84417 | 0.81483 | [8 empty] | 2015-03-31
VT_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3727 | 1.3376 | [8 empty] | 2015-03-31
VT_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3646 | 1.33 | [8 empty] | 2015-03-31
VT_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.6791 | 1.6271 | [8 empty] | 2015-03-31
VT_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.1208 | 2.0506 | [8 empty] | 2015-03-31
VT_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6804 | 1.6281 | [8 empty] | 2015-03-31
VT_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.6855 | 1.6327 | [8 empty] | 2015-03-31
VT_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.1245 | 2.0444 | [8 empty] | 2015-03-31
VT_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.2785 | 2.1835 | [8 empty] | 2015-03-31
VT_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.0554 | 2.0455 | [8 empty] | 2015-03-31
VT_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.93913 | 0.8191 | [8 empty] | 2015-03-31
VT_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.93968 | 0.81041 | [8 empty] | 2015-03-31
VT_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.1535 | 1.001 | [8 empty] | 2015-03-31
VT_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.364 | 1.2546 | [8 empty] | 2015-03-31
VT_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2029 | 1.0762 | [8 empty] | 2015-03-31
VT_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.2062 | 1.0799 | [8 empty] | 2015-03-31
VT_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.4282 | 1.2899 | [8 empty] | 2015-03-31
VT_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.5253 | 1.3888 | [8 empty] | 2015-03-31
VT_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
VT_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
VT_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VT_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VT_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VT_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VT_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VT_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VT_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VT_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
VT_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
VT_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
VT_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 169.5104 | 169.5104 | [8 empty] | 2015-03-31
VT_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 169.5104 | 169.5104 | [8 empty] | 2015-03-31
VT_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
VT_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 296.6432 | [8 empty] | 2015-03-31
VT_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
VT_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | [8 empty] | 2015-03-31
VT_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | [8 empty] | 2015-03-31
VT_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 508.5312 | [8 empty] | 2015-03-31
VT_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 529.72 | 508.5312 | [8 empty] | 2015-03-31
VT_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 678.0416 | 656.8528 | [8 empty] | 2015-03-31
VT_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 847.552 | [8 empty] | 2015-03-31
VT_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 2015-03-31
VT_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | [8 empty] | 2015-03-31
VT_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 805.1744 | [8 empty] | 2015-03-31
VT_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 889.9296 | [8 empty] | 2015-03-31
VT_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 911.1184 | [8 empty] | 2015-03-31
VT_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 317.832 | [8 empty] | 2015-03-31
VT_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 360.2096 | 317.832 | [8 empty] | 2015-03-31
VT_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 466.1536 | 402.5872 | [8 empty] | 2015-03-31
VT_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 529.72 | [8 empty] | 2015-03-31
VT_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | [8 empty] | 2015-03-31
VT_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 444.9648 | [8 empty] | 2015-03-31
VT_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | [8 empty] | 2015-03-31
VT_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 635.664 | 572.0976 | [8 empty] | 2015-03-31
VT_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
VT_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.12595 | 0.12288 | [8 empty] | 2015-03-31
VT_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.12438 | 0.12144 | [8 empty] | 2015-03-31
VT_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.15689 | 0.15528 | [8 empty] | 2015-03-31
VT_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.21982 | 0.21294 | [8 empty] | 2015-03-31
VT_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15441 | 0.15001 | [8 empty] | 2015-03-31
VT_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.15906 | 0.15478 | [8 empty] | 2015-03-31
VT_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.235 | 0.22508 | [8 empty] | 2015-03-31
VT_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.37994 | 0.36796 | [8 empty] | 2015-03-31
VT_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.3772 | 0.36543 | [8 empty] | 2015-03-31
VT_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.47879 | 0.46611 | [8 empty] | 2015-03-31
VT_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.61885 | 0.59493 | [8 empty] | 2015-03-31
VT_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.45993 | 0.44246 | [8 empty] | 2015-03-31
VT_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.46166 | 0.44401 | [8 empty] | 2015-03-31
VT_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.60165 | 0.57478 | [8 empty] | 2015-03-31
VT_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.66643 | 0.63413 | [8 empty] | 2015-03-31
VT_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.65592 | 0.65276 | [8 empty] | 2015-03-31
VT_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.25982 | 0.23068 | [8 empty] | 2015-03-31
VT_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.26 | 0.22773 | [8 empty] | 2015-03-31
VT_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.32576 | 0.28789 | [8 empty] | 2015-03-31
VT_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.40591 | 0.36993 | [8 empty] | 2015-03-31
VT_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34924 | 0.30715 | [8 empty] | 2015-03-31
VT_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.35036 | 0.30841 | [8 empty] | 2015-03-31
VT_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.4197 | 0.37377 | [8 empty] | 2015-03-31
VT_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.45286 | 0.40671 | [8 empty] | 2015-03-31
WI_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.6649 | 1.5784 | 1.4496 | 1.3538 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 1.8314 | 1.7388 | 1.7408 | 1.6751 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.311 | 1.2792 | 1.3324 | 1.3823 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.5644 | 1.4884 | 1.3283 | 1.1797 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.5157 | 1.4638 | 1.5043 | 1.5204 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 593.2864 | 550.9088 | 593.2864 | 550.9088 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 741.608 | 699.2304 | 783.9856 | 762.7968 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 593.2864 | 614.4752 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 593.2864 | 572.0976 | 572.0976 | 529.72 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 678.0416 | 656.8528 | 678.0416 | 678.0416 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.42477 | 0.39426 | 0.4199 | 0.38451 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.52568 | 0.49268 | 0.55553 | 0.53457 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.41837 | 0.40823 | 0.42521 | 0.44112 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.42712 | 0.40083 | 0.40302 | 0.37272 | [6 empty] | 2015-03-31
WI_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.48371 | 0.46576 | 0.48007 | 0.48521 | [6 empty] | 2015-03-31
WI_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 10085.8688 | 9704.4704 | 10064.68 | 9683.2816 | [6 empty] | 2015-03-31
WI_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 24833.2736 | 24494.2528 | 24960.4064 | 25023.9728 | [6 empty] | 2015-03-31
WI_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 201293.6003 | 197246.5395 | 201505.4883 | 202819.1939 | [6 empty] | 2015-03-31
WI_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 23519.568 | 21718.52 | 23307.68 | 22078.7296 | [6 empty] | 2015-03-31
WI_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
WI_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
WI_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
WI_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
WI_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
WI_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
WI_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
WI_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
WI_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
WI_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
WI_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
WI_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WI_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WI_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WI_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
WI_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
WI_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
WI_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WI_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WI_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WI_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 388.9605 | 383.4528 | 334.6557 | 333.8442 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 388.9605 | 383.4528 | 334.6557 | 333.8442 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | Centrifugal | Centrifugal | [6 empty] | 2015-03-31
WI_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 369.1867 | 363.947 | 317.6366 | 316.8692 | [6 empty] | 2015-03-31
WI_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 369.1867 | 363.947 | 317.6366 | 316.8692 | [6 empty] | 2015-03-31
WI_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.5674 | 5.4316 | 5.9847 | 5.8432 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1831.6633 | 902.8265 | 1575.8724 | 786.0254 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 902.8265 | 0 | 786.0254 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1831.6633 | 1805.6688 | 1575.8724 | 1572.0509 | [6 empty] | 2015-03-31
WI_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1119.5178 | 1092.2188 | 1203.4326 | 1174.9781 | [6 empty] | 2015-03-31
WI_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 2137.0991 | 2098.7413 | 1838.6375 | 1827.2253 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
WI_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.8349 | 10.4171 | 10.7909 | 10.3833 | [6 empty] | 2015-03-31
WI_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 35.7136 | 35.207 | 35.8936 | 35.9736 | [6 empty] | 2015-03-31
WI_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 283.0842 | 277.3798 | 283.3796 | 285.2224 | [6 empty] | 2015-03-31
WI_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 33.8237 | 31.2267 | 33.5175 | 31.7424 | [6 empty] | 2015-03-31
WI_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 43.7814 | 43.6904 | 44.597 | 44.5049 | [6 empty] | 2015-03-31
WI_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.82476 | 0.80884 | 0.85091 | 0.85682 | [6 empty] | 2015-03-31
WI_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.3954 | 10.1431 | 10.7477 | 10.8599 | [6 empty] | 2015-03-31
WI_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.7116 | 0.68717 | 0.73256 | 0.73137 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 9.8808 | 4.8704 | 8.5013 | 4.2403 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 4.8704 | 0 | 4.2403 | [6 empty] | 2015-03-31
WI_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 29.6424 | 29.2226 | 25.5038 | 25.442 | [6 empty] | 2015-03-31
WI_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 24.199 | 23.609 | 26.0129 | 25.3978 | [6 empty] | 2015-03-31
WI_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 39.5808 | 38.8718 | 34.0547 | 33.8428 | [6 empty] | 2015-03-31
WI_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.8825 | 3.8557 | 3.8693 | 3.871 | [6 empty] | 2015-03-31
WI_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 5019.152 | 4856.954 | 5203.0777 | 5055.882 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 8.8466 | 8.7573 | 7.8249 | 7.8027 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 37.8726 | 37.1614 | 32.7762 | 32.3277 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.4079 | 6.1896 | 5.8526 | 5.8041 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.5659 | 5.2792 | 5.0265 | 4.899 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3220.6976 | 3178.32 | 3051.1872 | 3051.1872 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 12692.0912 | 11908.1056 | 12353.0704 | 11759.784 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2585.0336 | 2479.0896 | 2627.4112 | 2606.2224 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2140.0688 | 1991.7472 | 2182.4464 | 2118.88 | [6 empty] | 2015-03-31
WI_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
WI_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.3953 | 3.0175 | 8.1221 | 3.5492 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.1847 | 2.1584 | 2.0726 | 2.0679 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 13.6097 | 12.7772 | 13.2523 | 12.6145 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.8129 | 1.7349 | 1.8461 | 1.8285 | [6 empty] | 2015-03-31
WI_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.5007 | 1.3953 | 1.5242 | 1.4776 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 25.6566 | 22.0832 | 25.4306 | 22.3886 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 25.258 | 21.7736 | 25.0773 | 22.0014 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 23.0707 | 20.4737 | 22.9196 | 20.8082 | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 31.3319 | 27.0001 | 27.1807 | 24.5454 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 11.1636 | 14.9958 | 14.9958 | 14.9958 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 6.2948 | 5.3303 | 6.3209 | 5.4126 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 10.5074 | 10.5074 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7691.5344 | 6632.0944 | 7627.968 | 6716.8496 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7585.5904 | 6526.1504 | 7522.024 | 6610.9056 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6928.7376 | 6144.752 | 6886.36 | 6250.696 | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 9407.8272 | 8094.1216 | 9217.128 | 7839.856 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 4492.0256 | 4492.0256 | 4492.0256 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1885.8032 | 1589.16 | 1991.7472 | 1631.5376 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
WI_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | [6 empty] | 2015-03-31
WI_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
WI_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
WI_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
WI_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
WI_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
WI_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
WI_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7699.12 | 6626.8184 | 7631.2947 | 6718.46 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7579.5092 | 6533.8843 | 7525.2871 | 6602.2394 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6143.8197 | 6777.6191 | 6244.2122 | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | 2584.9912 | 2584.9912 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
WI_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
WI_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.6793 | 1.5265 | 1.772 | 1.5968 | [6 empty] | 2015-03-31
WI_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 168.8408 | 153.4828 | 178.1656 | 160.5432 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 11.2725 | 9.7765 | 11.1732 | 9.9117 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 11.0973 | 9.6394 | 11.018 | 9.7403 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 10.1363 | 9.064 | 10.0699 | 9.2121 | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 13.766 | 11.8628 | 13.4844 | 11.4642 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 3.0475 | 3.0475 | 3.0475 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.3236 | 1.1208 | 1.4006 | 1.1381 | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
WI_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.6496 | 3.3176 | 3.8512 | 3.4702 | [6 empty] | 2015-03-31
WI_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
WI_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 104.4966 | 97.6833 | 105.6859 | 96.9928 | [6 empty] | 2015-03-31
WI_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 2.0139 | 1.8871 | 1.83 | 1.643 | [6 empty] | 2015-03-31
WI_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 5.3029 | 5.1057 | 4.8661 | 4.6784 | [6 empty] | 2015-03-31
WI_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.5302 | 2.3773 | 2.5254 | 2.3344 | [6 empty] | 2015-03-31
WI_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 4.2423 | 4.2063 | 3.8939 | 3.8714 | [6 empty] | 2015-03-31
WI_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 678.0416 | 614.4752 | 699.2304 | 614.4752 | [6 empty] | 2015-03-31
WI_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1589.16 | 1525.5936 | 1589.16 | 1504.4048 | [6 empty] | 2015-03-31
WI_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 762.7968 | 720.4192 | 762.7968 | 699.2304 | [6 empty] | 2015-03-31
WI_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1525.5936 | 1504.4048 | 1546.7824 | 1525.5936 | [6 empty] | 2015-03-31
WI_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
WI_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
WI_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
WI_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
WI_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
WI_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WI_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
WI_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WI_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
WI_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.115 | 1.0736 | 1.1101 | 1.052 | [6 empty] | 2015-03-31
WI_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0632 | 1.051 | 1.0814 | 1.0735 | [6 empty] | 2015-03-31
WI_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.5711 | 0.56064 | 0.44488 | 0.4533 | [6 empty] | 2015-03-31
WI_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.566 | 0.55591 | 0.43996 | 0.44793 | [6 empty] | 2015-03-31
WI_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.67907 | 0.66917 | 0.53689 | 0.56675 | [6 empty] | 2015-03-31
WI_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.89585 | 0.87312 | 0.72109 | 0.75248 | [6 empty] | 2015-03-31
WI_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.67362 | 0.65721 | 0.56118 | 0.59049 | [6 empty] | 2015-03-31
WI_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.68751 | 0.6717 | 0.57551 | 0.60499 | [6 empty] | 2015-03-31
WI_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.94136 | 0.90952 | 0.77389 | 0.81085 | [6 empty] | 2015-03-31
WI_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.5512 | 1.5124 | 1.2944 | 1.3063 | [6 empty] | 2015-03-31
WI_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.5426 | 1.5043 | 1.286 | 1.2972 | [6 empty] | 2015-03-31
WI_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.8968 | 1.8431 | 1.6026 | 1.6617 | [6 empty] | 2015-03-31
WI_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3711 | 2.2947 | 2.0047 | 2.0747 | [6 empty] | 2015-03-31
WI_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.8292 | 1.7707 | 1.6122 | 1.6745 | [6 empty] | 2015-03-31
WI_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.8313 | 1.7757 | 1.6178 | 1.6804 | [6 empty] | 2015-03-31
WI_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3176 | 2.2316 | 2.0305 | 2.1198 | [6 empty] | 2015-03-31
WI_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.498 | 2.3971 | 2.1569 | 2.2505 | [6 empty] | 2015-03-31
WI_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.1244 | 2.1153 | 2.0799 | 2.1366 | [6 empty] | 2015-03-31
WI_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 1.0479 | 0.92287 | 0.85975 | 0.77235 | [6 empty] | 2015-03-31
WI_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 1.0481 | 0.91372 | 0.86227 | 0.7585 | [6 empty] | 2015-03-31
WI_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2892 | 1.126 | 1.0621 | 0.99392 | [6 empty] | 2015-03-31
WI_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5083 | 1.3946 | 1.2759 | 1.2494 | [6 empty] | 2015-03-31
WI_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.2964 | 1.1651 | 1.1439 | 1.0785 | [6 empty] | 2015-03-31
WI_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3 | 1.1685 | 1.1476 | 1.0833 | [6 empty] | 2015-03-31
WI_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.5493 | 1.4047 | 1.3562 | 1.3085 | [6 empty] | 2015-03-31
WI_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.6497 | 1.5059 | 1.4317 | 1.3943 | [6 empty] | 2015-03-31
WI_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
WI_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
WI_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WI_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WI_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WI_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WI_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WI_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WI_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WI_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
WI_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
WI_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
WI_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | [6 empty] | 2015-03-31
WI_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 190.6992 | 190.6992 | 169.5104 | 169.5104 | [6 empty] | 2015-03-31
WI_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 233.0768 | 211.888 | 211.888 | [6 empty] | 2015-03-31
WI_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 317.832 | 296.6432 | 317.832 | [6 empty] | 2015-03-31
WI_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | 211.888 | 211.888 | [6 empty] | 2015-03-31
WI_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 211.888 | 211.888 | 233.0768 | [6 empty] | 2015-03-31
WI_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 317.832 | 339.0208 | [6 empty] | 2015-03-31
WI_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 550.9088 | 529.72 | 529.72 | [6 empty] | 2015-03-31
WI_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 529.72 | 529.72 | 529.72 | [6 empty] | 2015-03-31
WI_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 678.0416 | 656.8528 | 699.2304 | [6 empty] | 2015-03-31
WI_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 911.1184 | 889.9296 | 847.552 | 889.9296 | [6 empty] | 2015-03-31
WI_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 656.8528 | 678.0416 | [6 empty] | 2015-03-31
WI_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 635.664 | 656.8528 | 678.0416 | [6 empty] | 2015-03-31
WI_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 868.7408 | 826.3632 | 847.552 | 889.9296 | [6 empty] | 2015-03-31
WI_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 974.6848 | 932.3072 | 932.3072 | 974.6848 | [6 empty] | 2015-03-31
WI_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 953.496 | 932.3072 | 932.3072 | 953.496 | [6 empty] | 2015-03-31
WI_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
WI_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 339.0208 | 339.0208 | 317.832 | [6 empty] | 2015-03-31
WI_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 423.776 | 444.9648 | 423.776 | [6 empty] | 2015-03-31
WI_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 550.9088 | 550.9088 | 550.9088 | [6 empty] | 2015-03-31
WI_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 487.3424 | 444.9648 | [6 empty] | 2015-03-31
WI_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 508.5312 | 444.9648 | 487.3424 | 466.1536 | [6 empty] | 2015-03-31
WI_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 529.72 | 572.0976 | 550.9088 | [6 empty] | 2015-03-31
WI_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 656.8528 | 593.2864 | 614.4752 | 593.2864 | [6 empty] | 2015-03-31
WI_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
WI_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.13286 | 0.12941 | 0.11763 | 0.12052 | [6 empty] | 2015-03-31
WI_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.13118 | 0.12787 | 0.11597 | 0.11868 | [6 empty] | 2015-03-31
WI_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.16584 | 0.16344 | 0.14636 | 0.15718 | [6 empty] | 2015-03-31
WI_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.23385 | 0.22616 | 0.20807 | 0.2192 | [6 empty] | 2015-03-31
WI_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.15591 | 0.15093 | 0.14698 | 0.15719 | [6 empty] | 2015-03-31
WI_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.16057 | 0.15581 | 0.15209 | 0.16236 | [6 empty] | 2015-03-31
WI_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.24572 | 0.23497 | 0.22394 | 0.23704 | [6 empty] | 2015-03-31
WI_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.3972 | 0.38418 | 0.37313 | 0.37727 | [6 empty] | 2015-03-31
WI_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.3943 | 0.38148 | 0.37018 | 0.37405 | [6 empty] | 2015-03-31
WI_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.50319 | 0.4877 | 0.47248 | 0.49592 | [6 empty] | 2015-03-31
WI_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.65321 | 0.62712 | 0.60724 | 0.63224 | [6 empty] | 2015-03-31
WI_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.46432 | 0.446 | 0.45949 | 0.48133 | [6 empty] | 2015-03-31
WI_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.46614 | 0.44769 | 0.46147 | 0.48343 | [6 empty] | 2015-03-31
WI_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.61505 | 0.58629 | 0.59602 | 0.6286 | [6 empty] | 2015-03-31
WI_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.69253 | 0.65813 | 0.65981 | 0.6911 | [6 empty] | 2015-03-31
WI_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.66996 | 0.667 | 0.66375 | 0.68184 | [6 empty] | 2015-03-31
WI_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.27227 | 0.24259 | 0.24597 | 0.22748 | [6 empty] | 2015-03-31
WI_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.27235 | 0.23949 | 0.24613 | 0.22375 | [6 empty] | 2015-03-31
WI_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.3426 | 0.30249 | 0.30853 | 0.29732 | [6 empty] | 2015-03-31
WI_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.42812 | 0.39047 | 0.39422 | 0.38579 | [6 empty] | 2015-03-31
WI_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.35642 | 0.31219 | 0.34492 | 0.32254 | [6 empty] | 2015-03-31
WI_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.35766 | 0.31336 | 0.34625 | 0.32425 | [6 empty] | 2015-03-31
WI_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.43154 | 0.38285 | 0.4123 | 0.39622 | [6 empty] | 2015-03-31
WI_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.46706 | 0.41836 | 0.44098 | 0.42773 | [6 empty] | 2015-03-31
MT_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.5014 | 1.3914 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.0645 | 1.9375 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.5159 | 1.4897 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.501 | 1.4055 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.7552 | 1.6908 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 932.3072 | 868.7408 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 678.0416 | 678.0416 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 783.9856 | 762.7968 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.47915 | 0.44401 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.65882 | 0.61829 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.48376 | 0.47539 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.479 | 0.44852 | [8 empty] | 2015-03-31
MT_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.56014 | 0.53957 | [8 empty] | 2015-03-31
MT_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 11166.4976 | 10742.7216 | [8 empty] | 2015-03-31
MT_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 27672.5728 | 27227.608 | [8 empty] | 2015-03-31
MT_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 221211.0723 | 217036.8787 | [8 empty] | 2015-03-31
MT_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 26697.888 | 24706.1408 | [8 empty] | 2015-03-31
MT_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
MT_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | [8 empty] | 2015-03-31
MT_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | [8 empty] | 2015-03-31
MT_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | [8 empty] | 2015-03-31
MT_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | [8 empty] | 2015-03-31
MT_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
MT_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | [8 empty] | 2015-03-31
MT_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | [8 empty] | 2015-03-31
MT_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | [8 empty] | 2015-03-31
MT_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
MT_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | [8 empty] | 2015-03-31
MT_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | [8 empty] | 2015-03-31
MT_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | [8 empty] | 2015-03-31
MT_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | [8 empty] | 2015-03-31
MT_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | [8 empty] | 2015-03-31
MT_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
MT_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
MT_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | [8 empty] | 2015-03-31
MT_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
MT_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
MT_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
MT_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 283.8446 | 278.332 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 283.8446 | 278.332 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Centrifugal | Centrifugal | [8 empty] | 2015-03-31
MT_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 269.4076 | 264.1812 | [8 empty] | 2015-03-31
MT_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 269.4076 | 264.1812 | [8 empty] | 2015-03-31
MT_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.4301 | 5.2848 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1336.6054 | 655.3237 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 655.3237 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1336.6054 | 1310.6474 | [8 empty] | 2015-03-31
MT_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1091.9066 | 1062.6944 | [8 empty] | 2015-03-31
MT_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1581.6261 | 1542.2777 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | [8 empty] | 2015-03-31
MT_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 11.992 | 11.5381 | [8 empty] | 2015-03-31
MT_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 39.6302 | 38.9832 | [8 empty] | 2015-03-31
MT_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 311.096 | 305.2175 | [8 empty] | 2015-03-31
MT_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 38.3942 | 35.5247 | [8 empty] | 2015-03-31
MT_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 48.6618 | 48.5648 | [8 empty] | 2015-03-31
MT_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.93995 | 0.91963 | [8 empty] | 2015-03-31
MT_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 11.9041 | 11.5827 | [8 empty] | 2015-03-31
MT_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.8134 | 0.78406 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 7.2105 | 3.5352 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 3.5352 | [8 empty] | 2015-03-31
MT_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 21.6316 | 21.2115 | [8 empty] | 2015-03-31
MT_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 23.6022 | 22.9708 | [8 empty] | 2015-03-31
MT_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 29.2941 | 28.5653 | [8 empty] | 2015-03-31
MT_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 4.0919 | 4.0611 | [8 empty] | 2015-03-31
MT_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4864.148 | 4692.9834 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 7.4425 | 7.4637 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 29.9277 | 28.3461 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.7579 | 6.4856 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.6572 | 5.2918 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 3347.8304 | 3369.0192 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 13476.0768 | 12755.6576 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 3051.1872 | 2924.0544 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2542.656 | 2373.1456 | [8 empty] | 2015-03-31
MT_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
MT_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | No | Yes | [8 empty] | 2015-03-31
MT_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.817 | 3.3371 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 2.2689 | 2.2754 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 14.458 | 13.694 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 2.0602 | 2.0458 | [8 empty] | 2015-03-31
MT_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.7845 | 1.6692 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 23.4253 | 21.1708 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 23.2304 | 20.8858 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 20.7794 | 19.2393 | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 23.93 | 20.7323 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 9.342 | 9.342 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 5.3017 | 4.6938 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 8.7929 | 8.7929 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 9026.4288 | 7776.2896 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 8899.296 | 7670.3456 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 8115.3104 | 7225.3808 | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 10763.9104 | 9301.8832 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 3347.8304 | 3347.8304 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 2140.0688 | 1822.2368 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 2015-03-31
MT_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | [8 empty] | 2015-03-31
MT_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | [8 empty] | 2015-03-31
MT_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | n/a | VFD | [8 empty] | 2015-03-31
MT_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | [8 empty] | 2015-03-31
MT_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | [8 empty] | 2015-03-31
MT_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | [8 empty] | 2015-03-31
MT_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | [8 empty] | 2015-03-31
MT_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | [8 empty] | 2015-03-31
MT_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7852.8447 | 7770.3356 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7852.8447 | 7665.7265 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6777.6191 | 6777.6191 | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 1434.9903 | 1434.9903 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | [8 empty] | 2015-03-31
MT_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MT_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MT_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MT_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | No | No | [8 empty] | 2015-03-31
MT_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | [8 empty] | 2015-03-31
MT_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | [8 empty] | 2015-03-31
MT_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.7622 | 1.553 | [8 empty] | 2015-03-31
MT_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 177.1733 | 156.1457 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 13.2098 | 11.3767 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 13.0443 | 11.2236 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 11.8797 | 10.5728 | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 15.6703 | 13.6299 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 2.2687 | 2.2687 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.498 | 1.2799 | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | [8 empty] | 2015-03-31
MT_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.8297 | 3.3752 | [8 empty] | 2015-03-31
MT_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | [8 empty] | 2015-03-31
MT_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 103.3494 | 92.0497 | [8 empty] | 2015-03-31
MT_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.7631 | 1.6304 | [8 empty] | 2015-03-31
MT_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 4.4453 | 4.2995 | [8 empty] | 2015-03-31
MT_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 2.3423 | 2.2465 | [8 empty] | 2015-03-31
MT_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 3.877 | 3.835 | [8 empty] | 2015-03-31
MT_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 783.9856 | 720.4192 | [8 empty] | 2015-03-31
MT_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1779.8592 | 1716.2928 | [8 empty] | 2015-03-31
MT_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 847.552 | 805.1744 | [8 empty] | 2015-03-31
MT_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1716.2928 | 1695.104 | [8 empty] | 2015-03-31
MT_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | [8 empty] | 2015-03-31
MT_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | [8 empty] | 2015-03-31
MT_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | [8 empty] | 2015-03-31
MT_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | [8 empty] | 2015-03-31
MT_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | [8 empty] | 2015-03-31
MT_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | [8 empty] | 2015-03-31
MT_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | [8 empty] | 2015-03-31
MT_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | [8 empty] | 2015-03-31
MT_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | [8 empty] | 2015-03-31
MT_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 1.2465 | 1.1985 | [8 empty] | 2015-03-31
MT_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.2059 | 1.1908 | [8 empty] | 2015-03-31
MT_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.46099 | 0.45061 | [8 empty] | 2015-03-31
MT_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.45468 | 0.44479 | [8 empty] | 2015-03-31
MT_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.58264 | 0.57596 | [8 empty] | 2015-03-31
MT_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.83889 | 0.81299 | [8 empty] | 2015-03-31
MT_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.60077 | 0.58484 | [8 empty] | 2015-03-31
MT_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.61715 | 0.60147 | [8 empty] | 2015-03-31
MT_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.92559 | 0.88781 | [8 empty] | 2015-03-31
MT_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 1.3782 | 1.3342 | [8 empty] | 2015-03-31
MT_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 1.3674 | 1.3242 | [8 empty] | 2015-03-31
MT_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.7818 | 1.7318 | [8 empty] | 2015-03-31
MT_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 2.3279 | 2.2356 | [8 empty] | 2015-03-31
MT_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.7705 | 1.7049 | [8 empty] | 2015-03-31
MT_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.7775 | 1.7121 | [8 empty] | 2015-03-31
MT_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 2.3374 | 2.2391 | [8 empty] | 2015-03-31
MT_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.5873 | 2.4627 | [8 empty] | 2015-03-31
MT_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 2.2965 | 2.2989 | [8 empty] | 2015-03-31
MT_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.95228 | 0.84291 | [8 empty] | 2015-03-31
MT_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.95213 | 0.83155 | [8 empty] | 2015-03-31
MT_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.2159 | 1.0664 | [8 empty] | 2015-03-31
MT_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.5383 | 1.4044 | [8 empty] | 2015-03-31
MT_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.3352 | 1.1823 | [8 empty] | 2015-03-31
MT_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.3399 | 1.1873 | [8 empty] | 2015-03-31
MT_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.6206 | 1.4528 | [8 empty] | 2015-03-31
MT_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.7359 | 1.564 | [8 empty] | 2015-03-31
MT_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [8 empty] | 2015-03-31
MT_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | [8 empty] | 2015-03-31
MT_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MT_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MT_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MT_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MT_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MT_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MT_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MT_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | [8 empty] | 2015-03-31
MT_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | [8 empty] | 2015-03-31
MT_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | [8 empty] | 2015-03-31
MT_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 211.888 | [8 empty] | 2015-03-31
MT_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 211.888 | 190.6992 | [8 empty] | 2015-03-31
MT_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | [8 empty] | 2015-03-31
MT_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 381.3984 | 360.2096 | [8 empty] | 2015-03-31
MT_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 254.2656 | [8 empty] | 2015-03-31
MT_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 275.4544 | 275.4544 | [8 empty] | 2015-03-31
MT_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 402.5872 | [8 empty] | 2015-03-31
MT_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | [8 empty] | 2015-03-31
MT_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 614.4752 | 593.2864 | [8 empty] | 2015-03-31
MT_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 783.9856 | [8 empty] | 2015-03-31
MT_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 995.8736 | [8 empty] | 2015-03-31
MT_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | [8 empty] | 2015-03-31
MT_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 805.1744 | 762.7968 | [8 empty] | 2015-03-31
MT_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 1059.44 | 1017.0624 | [8 empty] | 2015-03-31
MT_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 1165.384 | 1101.8176 | [8 empty] | 2015-03-31
MT_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 1038.2512 | 1038.2512 | [8 empty] | 2015-03-31
MT_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | [8 empty] | 2015-03-31
MT_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 423.776 | 381.3984 | [8 empty] | 2015-03-31
MT_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 487.3424 | [8 empty] | 2015-03-31
MT_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 699.2304 | 635.664 | [8 empty] | 2015-03-31
MT_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | [8 empty] | 2015-03-31
MT_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 593.2864 | 529.72 | [8 empty] | 2015-03-31
MT_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 656.8528 | [8 empty] | 2015-03-31
MT_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 783.9856 | 699.2304 | [8 empty] | 2015-03-31
MT_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | [8 empty] | 2015-03-31
MT_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.14711 | 0.1438 | [8 empty] | 2015-03-31
MT_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.1451 | 0.14195 | [8 empty] | 2015-03-31
MT_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.18593 | 0.1838 | [8 empty] | 2015-03-31
MT_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.26771 | 0.25945 | [8 empty] | 2015-03-31
MT_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.19173 | 0.18663 | [8 empty] | 2015-03-31
MT_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.19694 | 0.19194 | [8 empty] | 2015-03-31
MT_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.29537 | 0.28332 | [8 empty] | 2015-03-31
MT_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.4398 | 0.42577 | [8 empty] | 2015-03-31
MT_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.43637 | 0.4226 | [8 empty] | 2015-03-31
MT_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.56861 | 0.55266 | [8 empty] | 2015-03-31
MT_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.74289 | 0.71342 | [8 empty] | 2015-03-31
MT_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.56501 | 0.54408 | [8 empty] | 2015-03-31
MT_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.56724 | 0.54636 | [8 empty] | 2015-03-31
MT_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.74592 | 0.71454 | [8 empty] | 2015-03-31
MT_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.82565 | 0.78591 | [8 empty] | 2015-03-31
MT_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.73286 | 0.73362 | [8 empty] | 2015-03-31
MT_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.30389 | 0.269 | [8 empty] | 2015-03-31
MT_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.30385 | 0.26536 | [8 empty] | 2015-03-31
MT_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.38802 | 0.34031 | [8 empty] | 2015-03-31
MT_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.49092 | 0.44818 | [8 empty] | 2015-03-31
MT_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.4261 | 0.3773 | [8 empty] | 2015-03-31
MT_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.4276 | 0.37889 | [8 empty] | 2015-03-31
MT_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.51718 | 0.46363 | [8 empty] | 2015-03-31
MT_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.55395 | 0.49913 | [8 empty] | 2015-03-31
AK_SO_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 1.2093 | 1.1308 | 1.193 | 1.1364 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 2.2009 | 2.235 | 2.3799 | 2.4264 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 1.2391 | 1.2965 | 1.2502 | 1.2993 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 1.0177 | 0.97864 | 1.1138 | 1.0835 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:5 Cooling Capacity [ton] | PSZ-AC:5 Cooling Capacity [ton] | 1.319 | 1.3564 | 1.3553 | 1.386 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 550.9088 | 508.5312 | 529.72 | 508.5312 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 995.8736 | 995.8736 | 1080.6288 | 1101.8176 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 550.9088 | 593.2864 | 572.0976 | 593.2864 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 466.1536 | 444.9648 | 508.5312 | 487.3424 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:5 Supply Flow Rate [cfm] | PSZ-AC:5 Supply Flow Rate [cfm] | 593.2864 | 614.4752 | 614.4752 | 614.4752 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 136.9178 | 136.9178 | 136.9178 | 136.9178 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 103.7925 | 103.7925 | 103.7925 | 103.7925 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:5 OA Rate [cfm] | PSZ-AC:5 OA Rate [cfm] | 61.5711 | 61.5711 | 61.5711 | 61.5711 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:5 OA Damper [gravity, motorized] | PSZ-AC:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:5 Optimum Start [yes/no] | PSZ-AC:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:1 Fan Power [bhp] | PSZ-AC:1 Fan Power [bhp] | 0.38592 | 0.36087 | 0.38073 | 0.36264 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:2 Fan Power [bhp] | PSZ-AC:2 Fan Power [bhp] | 0.70237 | 0.71325 | 0.75947 | 0.77433 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:3 Fan Power [bhp] | PSZ-AC:3 Fan Power [bhp] | 0.39544 | 0.41373 | 0.39898 | 0.41464 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:4 Fan Power [bhp] | PSZ-AC:4 Fan Power [bhp] | 0.32476 | 0.31231 | 0.35544 | 0.34578 | [6 empty] | 2015-03-31
AK_SO_PSZ-AC:5 Fan Power [bhp] | PSZ-AC:5 Fan Power [bhp] | 0.42092 | 0.43284 | 0.43252 | 0.44231 | [6 empty] | 2015-03-31
AK_LO_CAV_BAS Supply Flow Rate [cfm] | CAV_BAS Supply Flow Rate [cfm] | 9598.5264 | 9238.3168 | 9556.1488 | 9195.9392 | [6 empty] | 2015-03-31
AK_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 23583.1344 | 23858.5888 | 24642.5744 | 24854.4624 | [6 empty] | 2015-03-31
AK_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 187626.8243 | 191631.5075 | 199259.4755 | 202755.6275 | [6 empty] | 2015-03-31
AK_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 21082.856 | 20574.3248 | 22672.016 | 21951.5968 | [6 empty] | 2015-03-31
AK_LO_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_LO_Ventilation Reset Flag add_ck_vav_bot | Ventilation Reset Flag add_ck_vav_bot | Yes | No | Yes | No | [6 empty] | 2015-03-31
AK_LO_Ventilation Reset Flag add_ck_vav_mid | Ventilation Reset Flag add_ck_vav_mid | Yes | No | Yes | No | [6 empty] | 2015-03-31
AK_LO_Ventilation Reset Flag add_ck_vav_top | Ventilation Reset Flag add_ck_vav_top | Yes | No | Yes | No | [6 empty] | 2015-03-31
AK_LO_CAV_BAS OA Rate [cfm] | CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 2542.8255 | 2542.8255 | [6 empty] | 2015-03-31
AK_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
AK_LO_VAV_MID WITH REHEAT OA Rate [cfm] | VAV_MID WITH REHEAT OA Rate [cfm] | 53777.8808 | 53777.8808 | 53777.8808 | 53777.8808 | [6 empty] | 2015-03-31
AK_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.805 | 5377.805 | 5377.805 | 5377.805 | [6 empty] | 2015-03-31
AK_LO_DATACENTER BASEMENT OA Rate [cfm] | DATACENTER BASEMENT OA Rate [cfm] | 716.9654 | 716.9654 | 716.9654 | 716.9654 | [6 empty] | 2015-03-31
AK_LO_DATACENTER BOT OA Rate [cfm] | DATACENTER BOT OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
AK_LO_DATACENTER MID OA Rate [cfm] | DATACENTER MID OA Rate [cfm] | 331.2021 | 331.2021 | 331.2021 | 331.2021 | [6 empty] | 2015-03-31
AK_LO_DATACENTER TOP OA Rate [cfm] | DATACENTER TOP OA Rate [cfm] | 33.1211 | 33.1211 | 33.1211 | 33.1211 | [6 empty] | 2015-03-31
AK_LO_CAV_bas OA Damper [gravity, motorized] | CAV_bas OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | VAV_top WITH REHEAT OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | AirLoop DataCenter Basement OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_LO_AirLoop DataCenter bot OA Damper [gravity, motorized] | AirLoop DataCenter bot OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_LO_AirLoop DataCenter mid OA Damper [gravity, motorized] | AirLoop DataCenter mid OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_LO_AirLoop DataCenter top OA Damper [gravity, motorized] | AirLoop DataCenter top OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_LO_CAV_bas (economizer) | CAV_bas (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_LO_VAV_bot WITH REHEAT (economizer) | VAV_bot WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_LO_VAV_mid WITH REHEAT (economizer) | VAV_mid WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_LO_VAV_top WITH REHEAT (economizer) | VAV_top WITH REHEAT (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_LO_AirLoop DataCenter Basement (economizer) | AirLoop DataCenter Basement (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_LO_AirLoop DataCenter bot (economizer) | AirLoop DataCenter bot (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AK_LO_AirLoop DataCenter mid (economizer) | AirLoop DataCenter mid (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AK_LO_AirLoop DataCenter top (economizer) | AirLoop DataCenter top (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AK_LO_VAV_bot_WITH_REHEAT ERV Flag | VAV_bot_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AK_LO_VAV_mid_WITH_REHEAT ERV Flag | VAV_mid_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AK_LO_VAV_top_WITH_REHEAT ERV Flag | VAV_top_WITH_REHEAT ERV Flag | No | Yes | No | Yes | [6 empty] | 2015-03-31
AK_LO_VAV_BOT Optimum Start [yes/no] | VAV_BOT Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AK_LO_VAV_MID Optimum Start [yes/no] | VAV_MID Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AK_LO_VAV_TOP Optimum Start [yes/no] | VAV_TOP Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AK_LO_CAV_BAS Optimum Start [yes/no] | CAV_BAS Optimum Start [yes/no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 CHILLER1 Capacity [ton] | COOLSYS1 CHILLER1 Capacity [ton] | 213.6052 | 217.2847 | 265.0861 | 267.7464 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 CHILLER2 Capacity [ton] | COOLSYS1 CHILLER2 Capacity [ton] | 213.6052 | 217.2847 | 265.0861 | 267.7464 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 CHILLER1 Capacity Category | COOLSYS1 CHILLER1 Capacity Category | Screw | Screw | Screw | Screw | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 CHILLER2 Capacity Category | COOLSYS1 CHILLER2 Capacity Category | Screw | Screw | Screw | Screw | [6 empty] | 2015-03-31
AK_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 202.7471 | 206.2402 | 251.6112 | 254.1252 | [6 empty] | 2015-03-31
AK_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 202.7471 | 206.2402 | 251.6112 | 254.1252 | [6 empty] | 2015-03-31
AK_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | HEATSYS1 BOILER Capacity [MMBTU/h] | 5.5189 | 5.3853 | 7.1598 | 6.8732 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 PUMP Flow Rate [gal/min] | COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 1005.8536 | 511.5898 | 1248.2732 | 630.4006 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 0 | 511.5898 | 0 | 630.4006 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1005.8536 | 1023.1796 | 1248.2732 | 1260.7997 | [6 empty] | 2015-03-31
AK_LO_HEATSYS1 PUMP Flow Rate [gal/min] | HEATSYS1 PUMP Flow Rate [gal/min] | 1109.7762 | 1082.9163 | 1439.7245 | 1382.1133 | [6 empty] | 2015-03-31
AK_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | TOWERWATERSYS PUMP Flow Rate [gal/min] | 1203.5975 | 1218.3747 | 1493.6758 | 1501.3268 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | COOLSYS1 PUMP SECONDARY Pressure setpoint reset [yes,no] | yes | yes | yes | yes | [6 empty] | 2015-03-31
AK_LO_CAV_BAS Fan Power [hp] | CAV_BAS Fan Power [hp] | 10.2956 | 9.9153 | 10.2524 | 9.8761 | [6 empty] | 2015-03-31
AK_LO_VAV_BOT WITH REHEAT Fan Power [hp] | VAV_BOT WITH REHEAT Fan Power [hp] | 33.8948 | 34.2888 | 35.4367 | 35.7429 | [6 empty] | 2015-03-31
AK_LO_VAV_MID WITH REHEAT Fan Power [hp] | VAV_MID WITH REHEAT Fan Power [hp] | 263.8676 | 269.4785 | 280.225 | 285.1278 | [6 empty] | 2015-03-31
AK_LO_VAV_TOP WITH REHEAT Fan Power [hp] | VAV_TOP WITH REHEAT Fan Power [hp] | 30.3198 | 29.5766 | 32.6049 | 31.5655 | [6 empty] | 2015-03-31
AK_LO_DATACENTER BASEMENT Fan Power [hp] | DATACENTER BASEMENT Fan Power [hp] | 42.5385 | 42.4536 | 43.0875 | 43.0069 | [6 empty] | 2015-03-31
AK_LO_DATACENTER BOT Fan Power [hp] | DATACENTER BOT Fan Power [hp] | 0.81895 | 0.82602 | 0.8379 | 0.84463 | [6 empty] | 2015-03-31
AK_LO_DATACENTER MID Fan Power [hp] | DATACENTER MID Fan Power [hp] | 10.3624 | 10.4922 | 10.6371 | 10.7603 | [6 empty] | 2015-03-31
AK_LO_DATACENTER TOP Fan Power [hp] | DATACENTER TOP Fan Power [hp] | 0.69533 | 0.69925 | 0.71627 | 0.71861 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 CHILLER1 PUMP Pump Power [hp] | COOLSYS1 CHILLER1 PUMP Pump Power [hp] | 5.4262 | 2.7599 | 6.734 | 3.4008 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 CHILLER2 PUMP Pump Power [hp] | COOLSYS1 CHILLER2 PUMP Pump Power [hp] | 0 | 2.7599 | 0 | 3.4008 | [6 empty] | 2015-03-31
AK_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | COOLSYS1 PUMP SECONDARY Pump Power [hp] | 16.2787 | 16.5591 | 20.202 | 20.4047 | [6 empty] | 2015-03-31
AK_LO_HEATSYS1 PUMP Pump Power [hp] | HEATSYS1 PUMP Pump Power [hp] | 23.9885 | 23.4079 | 31.1205 | 29.8752 | [6 empty] | 2015-03-31
AK_LO_TOWERWATERSYS PUMP Pump Power [hp] | TOWERWATERSYS PUMP Pump Power [hp] | 22.2924 | 22.5661 | 27.6651 | 27.8068 | [6 empty] | 2015-03-31
AK_LO_Datacenter PLANT CIRC PUMP Pump Power [hp] | Datacenter PLANT CIRC PUMP Pump Power [hp] | 3.73 | 3.734 | 3.9271 | 3.9309 | [6 empty] | 2015-03-31
AK_LO_CAV_BAS Preheat Coil | CAV_BAS Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_LO_VAV_BOT WITH REHEAT Preheat Coil | VAV_BOT WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_LO_VAV_MID WITH REHEAT Preheat Coil | VAV_MID WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_LO_VAV_TOP WITH REHEAT Preheat Coil | VAV_TOP WITH REHEAT Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 4803.9476 | 4691.8942 | 5520.0318 | 5194.2997 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:1 Cooling Capacity [ton] | PSZ-AC:1 Cooling Capacity [ton] | 5.9932 | 6.0628 | 7.0142 | 7.0371 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:2 Cooling Capacity [ton] | PSZ-AC:2 Cooling Capacity [ton] | 24.7728 | 26.0265 | 26.1283 | 29.8006 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:3 Cooling Capacity [ton] | PSZ-AC:3 Cooling Capacity [ton] | 6.1142 | 6.1967 | 6.6272 | 6.6734 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:4 Cooling Capacity [ton] | PSZ-AC:4 Cooling Capacity [ton] | 5.1333 | 5.1309 | 5.6377 | 5.5729 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:1 Supply Flow Rate [cfm] | PSZ-AC:1 Supply Flow Rate [cfm] | 2648.6 | 2690.9776 | 2924.0544 | 2945.2432 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:2 Supply Flow Rate [cfm] | PSZ-AC:2 Supply Flow Rate [cfm] | 11145.3088 | 8899.296 | 11759.784 | 9174.7504 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:3 Supply Flow Rate [cfm] | PSZ-AC:3 Supply Flow Rate [cfm] | 2754.544 | 2796.9216 | 2987.6208 | 3008.8096 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:4 Supply Flow Rate [cfm] | PSZ-AC:4 Supply Flow Rate [cfm] | 2309.5792 | 2309.5792 | 2542.656 | 2500.2784 | [6 empty] | 2015-03-31
AK_RS_PSZ1 (SZ VAV) | PSZ1 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
AK_RS_PSZ2 (SZ VAV) | PSZ2 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:1 OA Rate [cfm] | PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 490.669 | 490.669 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:2 OA Rate [cfm] | PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 4005.1282 | 4005.1282 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:3 OA Rate [cfm] | PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:4 OA Rate [cfm] | PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 377.3937 | 377.3937 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:1 OA Damper [gravity, motorized] | PSZ-AC:1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:2 OA Damper [gravity, motorized] | PSZ-AC:2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:3 OA Damper [gravity, motorized] | PSZ-AC:3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:4 OA Damper [gravity, motorized] | PSZ-AC:4 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:1 (economizer) | PSZ-AC:1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:2 (economizer) | PSZ-AC:2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:3 (economizer) | PSZ-AC:3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:4 (economizer) | PSZ-AC:4 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_RS_PSZ_AC_2 Energy Recovery [yes/no] | PSZ_AC_2 Energy Recovery [yes/no] | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_RS_FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | FRONT_ENTRY UNIT HEATER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:1 Optimum Start [yes/no] | PSZ-AC:1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:2 Optimum Start [yes/no] | PSZ-AC:2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:3 Optimum Start [yes/no] | PSZ-AC:3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:4 Optimum Start [yes/no] | PSZ-AC:4 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | 4.3752 | 3.0037 | 10.7559 | 4.859 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:1 Fan Power [hp] | PSZ-AC:1 Fan Power [hp] | 1.8486 | 1.881 | 2.0553 | 2.0667 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:2 Fan Power [hp] | PSZ-AC:2 Fan Power [hp] | 11.9677 | 9.6324 | 12.6226 | 9.9302 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:3 Fan Power [hp] | PSZ-AC:3 Fan Power [hp] | 1.9286 | 1.9546 | 2.0904 | 2.0345 | [6 empty] | 2015-03-31
AK_RS_PSZ-AC:4 Fan Power [hp] | PSZ-AC:4 Fan Power [hp] | 1.6192 | 1.6185 | 1.7783 | 1.7579 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_1 Cooling Capacity [ton] | VAV_POD_1 Cooling Capacity [ton] | 16.254 | 15.361 | 18.1812 | 16.8942 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_2 Cooling Capacity [ton] | VAV_POD_2 Cooling Capacity [ton] | 15.9564 | 15.0503 | 17.8828 | 16.5713 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_3 Cooling Capacity [ton] | VAV_POD_3 Cooling Capacity [ton] | 14.6269 | 14.2489 | 16.4634 | 15.7415 | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER Cooling Capacity [ton] | VAV_OTHER Cooling Capacity [ton] | 18.094 | 16.1127 | 19.3657 | 16.9856 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_1:6 Cooling Capacity [ton] | PSZ-AC_1:6 Cooling Capacity [ton] | 9.9964 | 9.9964 | 10.5156 | 10.5156 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:5 Cooling Capacity [ton] | PSZ-AC_2:5 Cooling Capacity [ton] | 3.7074 | 3.1818 | 3.6887 | 3.4167 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:7 Cooling Capacity [ton] | PSZ-AC_2:7 Cooling Capacity [ton] | 7.0043 | 7.0043 | 7.3682 | 7.3682 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_1 Supply Flow Rate [cfm] | VAV_POD_1 Supply Flow Rate [cfm] | 7310.136 | 6907.5488 | 7839.856 | 7288.9472 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_2 Supply Flow Rate [cfm] | VAV_POD_2 Supply Flow Rate [cfm] | 7183.0032 | 6780.416 | 7712.7232 | 7161.8144 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_3 Supply Flow Rate [cfm] | VAV_POD_3 Supply Flow Rate [cfm] | 6589.7168 | 6420.2064 | 7183.0032 | 6801.6048 | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER Supply Flow Rate [cfm] | VAV_OTHER Supply Flow Rate [cfm] | 8136.4992 | 7246.5696 | 8708.5968 | 7649.1568 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | PSZ-AC_1:6 Supply Flow Rate [cfm] | 4492.0256 | 4492.0256 | 4492.0256 | 4492.0256 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | PSZ-AC_2:5 Supply Flow Rate [cfm] | 1673.9152 | 1440.8384 | 1589.16 | 1462.0272 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3157.1312 | 3157.1312 | [6 empty] | 2015-03-31
AK_PS_PSZ2_5 (SZ VAV) | PSZ2_5 (SZ VAV) | n/a | n/a | n/a | n/a | [6 empty] | 2015-03-31
AK_PS_PSZ1_6 (SZ VAV) | PSZ1_6 (SZ VAV) | VFD | VFD | VFD | VFD | [6 empty] | 2015-03-31
AK_PS_PSZ2_7 (SZ VAV) | PSZ2_7 (SZ VAV) | n/a | VFD | n/a | VFD | [6 empty] | 2015-03-31
AK_PS_Supply Air Temp. Reset Flag | Supply Air Temp. Reset Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_PS_Ventilation Reset Flag add_ck_vav_other | Ventilation Reset Flag add_ck_vav_other | No | No | No | No | [6 empty] | 2015-03-31
AK_PS_Ventilation Reset Flag add_ck_vav_pod_1 | Ventilation Reset Flag add_ck_vav_pod_1 | No | No | No | No | [6 empty] | 2015-03-31
AK_PS_Ventilation Reset Flag add_ck_vav_pod_2 | Ventilation Reset Flag add_ck_vav_pod_2 | No | No | No | No | [6 empty] | 2015-03-31
AK_PS_Ventilation Reset Flag add_ck_vav_pod_3 | Ventilation Reset Flag add_ck_vav_pod_3 | No | No | No | No | [6 empty] | 2015-03-31
AK_PS_VAV_POD_1 OA Rate [cfm] | VAV_POD_1 OA Rate [cfm] | 7316.9588 | 6914.9437 | 7848.501 | 7292.9095 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_2 OA Rate [cfm] | VAV_POD_2 OA Rate [cfm] | 7183.0032 | 6775.0976 | 7719.6731 | 7153.5296 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_3 OA Rate [cfm] | VAV_POD_3 OA Rate [cfm] | 6584.462 | 6414.3371 | 6777.6191 | 6777.6191 | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER OA Rate [cfm] | VAV_OTHER OA Rate [cfm] | 4736.2887 | 4736.2887 | 4736.2887 | 4736.2887 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_1:6 OA Rate [cfm] | PSZ-AC_1:6 OA Rate [cfm] | 2584.9912 | 2584.9912 | 2584.9912 | 2584.9912 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:5 OA Rate [cfm] | PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 1152.7343 | 1152.7343 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:7 OA Rate [cfm] | PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 3153.0841 | 3153.0841 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_1 OA Damper [gravity, motorized] | VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_PS_VAV_POD_2 OA Damper [gravity, motorized] | VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_PS_VAV_POD_3 OA Damper [gravity, motorized] | VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER OA Damper [gravity, motorized] | VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_1:6 OA Damper [gravity, motorized] | PSZ-AC_1:6 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_PS_VAV_POD_1 (economizer) | VAV_POD_1 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_PS_VAV_POD_2 (economizer) | VAV_POD_2 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_PS_VAV_POD_3 (economizer) | VAV_POD_3 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER (economizer) | VAV_OTHER (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:5 (economizer) | PSZ-AC_2:5 (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_1:6 (economizer) | PSZ-AC_1:6 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:7 (economizer) | PSZ-AC_2:7 (economizer) | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | [6 empty] | 2015-03-31
AK_PS_VAV_Pod_1_ERV Flag | VAV_Pod_1_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_PS_VAV_Pod_2_ERV Flag | VAV_Pod_2_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_PS_VAV_Pod_3_ERV Flag | VAV_Pod_3_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER_ERV Flag | VAV_OTHER_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_PS_PSZ_AC_2_5_ERV Flag | PSZ_AC_2_5_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_PS_PSZ_AC_2_7_ERV Flag | PSZ_AC_2_7_ERV Flag | Yes | Yes | Yes | Yes | [6 empty] | 2015-03-31
AK_PS_Kitchen Exhaust Fan Flow [cfm] | Kitchen Exhaust Fan Flow [cfm] | 5000 | 5000 | 5000 | 5000 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_1 Optimum Start [yes/no] | VAV_POD_1 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_PS_VAV_POD_2 Optimum Start [yes/no] | VAV_POD_2 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_PS_VAV_POD_3 Optimum Start [yes/no] | VAV_POD_3 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER Optimum Start [yes/no] | VAV_OTHER Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_1:6 Optimum Start [yes/no] | PSZ-AC_1:6 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:5 Optimum Start [yes/no] | PSZ-AC_2:5 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:7 Optimum Start [yes/no] | PSZ-AC_2:7 Optimum Start [yes/no] | no | no | no | no | [6 empty] | 2015-03-31
AK_PS_HEATSYS1 Capacity [MMBTU/h] | HEATSYS1 Capacity [MMBTU/h] | 1.6386 | 1.5366 | 2.1295 | 1.9227 | [6 empty] | 2015-03-31
AK_PS_HEATSYS1 Flow Rate [gal/min] | HEATSYS1 Flow Rate [gal/min] | 164.7467 | 154.4921 | 214.1062 | 193.3121 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_1 Fan Power [hp] | VAV_POD_1 Fan Power [hp] | 10.7129 | 10.1243 | 11.4912 | 10.6777 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_2 Fan Power [hp] | VAV_POD_2 Fan Power [hp] | 10.5168 | 9.9196 | 11.3026 | 10.4737 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_3 Fan Power [hp] | VAV_POD_3 Fan Power [hp] | 9.7141 | 9.4631 | 10.5145 | 9.955 | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER Fan Power [hp] | VAV_OTHER Fan Power [hp] | 11.9256 | 10.6198 | 12.7638 | 11.1951 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_1:6 Fan Power [hp] | PSZ-AC_1:6 Fan Power [hp] | 3.0475 | 3.0475 | 3.0475 | 3.0475 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:5 Fan Power [hp] | PSZ-AC_2:5 Fan Power [hp] | 1.1694 | 1.0154 | 1.1202 | 1.0396 | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:7 Fan Power [hp] | PSZ-AC_2:7 Fan Power [hp] | 2.1353 | 2.1353 | 2.1353 | 2.1353 | [6 empty] | 2015-03-31
AK_PS_HEATSYS1 Pump Power [hp] | HEATSYS1 Pump Power [hp] | 3.5611 | 3.3394 | 4.628 | 4.1786 | [6 empty] | 2015-03-31
AK_PS_VAV_POD_1 Preheat Coil | VAV_POD_1 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_PS_VAV_POD_2 Preheat Coil | VAV_POD_2 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_PS_VAV_POD_3 Preheat Coil | VAV_POD_3 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_PS_VAV_OTHER Preheat Coil | VAV_OTHER Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_1:6 Preheat Coil | PSZ-AC_1:6 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:5 Preheat Coil | PSZ-AC_2:5 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_PS_PSZ-AC_2:7 Preheat Coil | PSZ-AC_2:7 Preheat Coil | YES | YES | YES | YES | [6 empty] | 2015-03-31
AK_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 103.7796 | 97.4287 | 114.1427 | 101.5304 | [6 empty] | 2015-03-31
AK_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | SAC_FRONTOFFICE Cooling Capacity [ton] | 1.5729 | 1.3512 | 1.6688 | 1.4151 | [6 empty] | 2015-03-31
AK_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | SAC_FRONTLOUNGE Cooling Capacity [ton] | 3.1132 | 2.9681 | 3.2835 | 3.1192 | [6 empty] | 2015-03-31
AK_SH_SAC_MEETINGROOM Cooling Capacity [ton] | SAC_MEETINGROOM Cooling Capacity [ton] | 1.6276 | 1.5305 | 1.8639 | 1.7508 | [6 empty] | 2015-03-31
AK_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 3.3412 | 3.3068 | 3.4394 | 3.3924 | [6 empty] | 2015-03-31
AK_SH_SAC_FRONTOFFICE Supply Flow Rate [cfm] | SAC_FRONTOFFICE Supply Flow Rate [cfm] | 699.2304 | 614.4752 | 741.608 | 635.664 | [6 empty] | 2015-03-31
AK_SH_SAC_FRONTLOUNGE Supply Flow Rate [cfm] | SAC_FRONTLOUNGE Supply Flow Rate [cfm] | 1398.4608 | 1334.8944 | 1483.216 | 1398.4608 | [6 empty] | 2015-03-31
AK_SH_SAC_MEETINGROOM Supply Flow Rate [cfm] | SAC_MEETINGROOM Supply Flow Rate [cfm] | 678.0416 | 635.664 | 720.4192 | 656.8528 | [6 empty] | 2015-03-31
AK_SH_SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | SAC_EXC_EMPLGE_RESTRM Supply Flow Rate [cfm] | 1504.4048 | 1483.216 | 1546.7824 | 1525.5936 | [6 empty] | 2015-03-31
AK_SH_SAC_FRONTOFFICE OA Rate [cfm] | SAC_FRONTOFFICE OA Rate [cfm] | 119.2938 | 119.2938 | 119.2938 | 119.2938 | [6 empty] | 2015-03-31
AK_SH_SAC_FRONTLOUNGE OA Rate [cfm] | SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 500.0133 | 500.0133 | [6 empty] | 2015-03-31
AK_SH_SAC_MEETINGROOM OA Rate [cfm] | SAC_MEETINGROOM OA Rate [cfm] | 267.7629 | 267.7629 | 267.7629 | 267.7629 | [6 empty] | 2015-03-31
AK_SH_SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | SAC_EXC_EMPLGE_RESTRM OA Rate [cfm] | 199.9928 | 199.9928 | 199.9928 | 199.9928 | [6 empty] | 2015-03-31
AK_SH_SAC_FrontLounge OA Damper [gravity, motorized] | SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | motorized | motorized | [6 empty] | 2015-03-31
AK_SH_SAC_FrontOffice (economizer) | SAC_FrontOffice (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AK_SH_SAC_FrontLounge (economizer) | SAC_FrontLounge (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AK_SH_SAC_MeetingRoom (economizer) | SAC_MeetingRoom (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AK_SH_SAC_Exc_EmpLge_RestRm (economizer) | SAC_Exc_EmpLge_RestRm (economizer) | No | No | No | No | [6 empty] | 2015-03-31
AK_SH_SAC_FRONTLOUNGE Fan Power [hp] | SAC_FRONTLOUNGE Fan Power [hp] | 0.99348 | 0.94719 | 1.0478 | 0.99541 | [6 empty] | 2015-03-31
AK_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | 1.0539 | 1.0553 | 1.0849 | 1.0701 | [6 empty] | 2015-03-31
AK_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.29242 | 0.3079 | 0.33979 | 0.35421 | [6 empty] | 2015-03-31
AK_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.28752 | 0.3025 | 0.33464 | 0.34861 | [6 empty] | 2015-03-31
AK_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.3783 | 0.4164 | 0.42656 | 0.46373 | [6 empty] | 2015-03-31
AK_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.51468 | 0.55655 | 0.58604 | 0.62456 | [6 empty] | 2015-03-31
AK_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.52418 | 0.56777 | 0.57917 | 0.62371 | [6 empty] | 2015-03-31
AK_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.53877 | 0.58259 | 0.59365 | 0.63831 | [6 empty] | 2015-03-31
AK_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.6838 | 0.74908 | 0.76233 | 0.82586 | [6 empty] | 2015-03-31
AK_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 0.99526 | 1.0272 | 1.1553 | 1.181 | [6 empty] | 2015-03-31
AK_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 0.98623 | 1.0173 | 1.1456 | 1.1707 | [6 empty] | 2015-03-31
AK_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | SPLIT MNE COOLING COIL Cooling Capacity [ton] | 1.2938 | 1.383 | 1.4718 | 1.5565 | [6 empty] | 2015-03-31
AK_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | SPLIT MNW COOLING COIL Cooling Capacity [ton] | 1.5902 | 1.6891 | 1.8101 | 1.8982 | [6 empty] | 2015-03-31
AK_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 1.6236 | 1.7205 | 1.8027 | 1.9008 | [6 empty] | 2015-03-31
AK_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 1.6303 | 1.7275 | 1.8087 | 1.9072 | [6 empty] | 2015-03-31
AK_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | SPLIT MSE COOLING COIL Cooling Capacity [ton] | 1.9586 | 2.0939 | 2.1941 | 2.3288 | [6 empty] | 2015-03-31
AK_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | SPLIT MSW COOLING COIL Cooling Capacity [ton] | 2.049 | 2.1981 | 2.2876 | 2.4342 | [6 empty] | 2015-03-31
AK_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.8909 | 1.949 | 1.9745 | 2.0484 | [6 empty] | 2015-03-31
AK_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.58738 | 0.56479 | 0.69286 | 0.66519 | [6 empty] | 2015-03-31
AK_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.58049 | 0.55337 | 0.68523 | 0.65347 | [6 empty] | 2015-03-31
AK_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | SPLIT TNE COOLING COIL Cooling Capacity [ton] | 0.75423 | 0.77645 | 0.87688 | 0.88105 | [6 empty] | 2015-03-31
AK_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | SPLIT TNW COOLING COIL Cooling Capacity [ton] | 0.9699 | 0.98079 | 1.1208 | 1.1061 | [6 empty] | 2015-03-31
AK_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 1.0859 | 1.0765 | 1.2202 | 1.1976 | [6 empty] | 2015-03-31
AK_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 1.0906 | 1.0817 | 1.2249 | 1.2026 | [6 empty] | 2015-03-31
AK_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.2393 | 1.2514 | 1.402 | 1.399 | [6 empty] | 2015-03-31
AK_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.2909 | 1.317 | 1.4621 | 1.4689 | [6 empty] | 2015-03-31
AK_MA_SPLIT GN1 COOLING COIL Cooling Coil Type | SPLIT GN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT GN2 COOLING COIL Cooling Coil Type | SPLIT GN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT GNE COOLING COIL Cooling Coil Type | SPLIT GNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT GNW COOLING COIL Cooling Coil Type | SPLIT GNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT GS1 COOLING COIL Cooling Coil Type | SPLIT GS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT GS2 COOLING COIL Cooling Coil Type | SPLIT GS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT GSW COOLING COIL Cooling Coil Type | SPLIT GSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT MN1 COOLING COIL Cooling Coil Type | SPLIT MN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT MN2 COOLING COIL Cooling Coil Type | SPLIT MN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT MNE COOLING COIL Cooling Coil Type | SPLIT MNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT MNW COOLING COIL Cooling Coil Type | SPLIT MNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT MS1 COOLING COIL Cooling Coil Type | SPLIT MS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT MS2 COOLING COIL Cooling Coil Type | SPLIT MS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT MSE COOLING COIL Cooling Coil Type | SPLIT MSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT MSW COOLING COIL Cooling Coil Type | SPLIT MSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT OFFICE COOLING COIL Cooling Coil Type | SPLIT OFFICE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT TN1 COOLING COIL Cooling Coil Type | SPLIT TN1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT TN2 COOLING COIL Cooling Coil Type | SPLIT TN2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT TNE COOLING COIL Cooling Coil Type | SPLIT TNE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT TNW COOLING COIL Cooling Coil Type | SPLIT TNW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT TS1 COOLING COIL Cooling Coil Type | SPLIT TS1 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT TS2 COOLING COIL Cooling Coil Type | SPLIT TS2 COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT TSE COOLING COIL Cooling Coil Type | SPLIT TSE COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT TSW COOLING COIL Cooling Coil Type | SPLIT TSW COOLING COIL Cooling Coil Type | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | Coil:Cooling:DX:SingleSpeed | [6 empty] | 2015-03-31
AK_MA_SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT GSW FURNACE WITH DX COOLING OA Rate [cfm] | 56.9945 | 56.9945 | 56.9945 | 56.9945 | [6 empty] | 2015-03-31
AK_MA_SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AK_MA_SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MN2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AK_MA_SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AK_MA_SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MNW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AK_MA_SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS1 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AK_MA_SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MS2 FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AK_MA_SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSE FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AK_MA_SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT MSW FURNACE WITH DX COOLING OA Rate [cfm] | 109.9824 | 109.9824 | 109.9824 | 109.9824 | [6 empty] | 2015-03-31
AK_MA_SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT OFFICE FURNACE WITH DX COOLING OA Rate [cfm] | 80.7372 | 80.7372 | 80.7372 | 80.7372 | [6 empty] | 2015-03-31
AK_MA_SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TN2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TNW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS1 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TS2 FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSE FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | SPLIT TSW FURNACE WITH DX COOLING OA Rate [cfm] | 54.9913 | 54.9913 | 54.9913 | 54.9913 | [6 empty] | 2015-03-31
AK_MA_SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN1 SUPPLY FAN Supply Flow Rate [cfm] | 127.1328 | 148.3216 | 148.3216 | 169.5104 | [6 empty] | 2015-03-31
AK_MA_SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GN2 SUPPLY FAN Supply Flow Rate [cfm] | 127.1328 | 127.1328 | 148.3216 | 148.3216 | [6 empty] | 2015-03-31
AK_MA_SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNE SUPPLY FAN Supply Flow Rate [cfm] | 169.5104 | 190.6992 | 190.6992 | 211.888 | [6 empty] | 2015-03-31
AK_MA_SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GNW SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 254.2656 | 254.2656 | 275.4544 | [6 empty] | 2015-03-31
AK_MA_SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS1 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 254.2656 | 254.2656 | 275.4544 | [6 empty] | 2015-03-31
AK_MA_SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GS2 SUPPLY FAN Supply Flow Rate [cfm] | 233.0768 | 254.2656 | 275.4544 | 296.6432 | [6 empty] | 2015-03-31
AK_MA_SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT GSW SUPPLY FAN Supply Flow Rate [cfm] | 317.832 | 339.0208 | 339.0208 | 381.3984 | [6 empty] | 2015-03-31
AK_MA_SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN1 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 466.1536 | 529.72 | 529.72 | [6 empty] | 2015-03-31
AK_MA_SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MN2 SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 466.1536 | 508.5312 | 529.72 | [6 empty] | 2015-03-31
AK_MA_SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNE SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 614.4752 | 656.8528 | 699.2304 | [6 empty] | 2015-03-31
AK_MA_SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MNW SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 762.7968 | 805.1744 | 847.552 | [6 empty] | 2015-03-31
AK_MA_SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS1 SUPPLY FAN Supply Flow Rate [cfm] | 720.4192 | 783.9856 | 805.1744 | 847.552 | [6 empty] | 2015-03-31
AK_MA_SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MS2 SUPPLY FAN Supply Flow Rate [cfm] | 741.608 | 783.9856 | 805.1744 | 868.7408 | [6 empty] | 2015-03-31
AK_MA_SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSE SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 932.3072 | 995.8736 | 1038.2512 | [6 empty] | 2015-03-31
AK_MA_SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT MSW SUPPLY FAN Supply Flow Rate [cfm] | 932.3072 | 995.8736 | 1038.2512 | 1101.8176 | [6 empty] | 2015-03-31
AK_MA_SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT OFFICE SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 868.7408 | 889.9296 | 932.3072 | [6 empty] | 2015-03-31
AK_MA_SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN1 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 317.832 | 296.6432 | [6 empty] | 2015-03-31
AK_MA_SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TN2 SUPPLY FAN Supply Flow Rate [cfm] | 254.2656 | 254.2656 | 317.832 | 296.6432 | [6 empty] | 2015-03-31
AK_MA_SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNE SUPPLY FAN Supply Flow Rate [cfm] | 339.0208 | 339.0208 | 402.5872 | 402.5872 | [6 empty] | 2015-03-31
AK_MA_SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TNW SUPPLY FAN Supply Flow Rate [cfm] | 444.9648 | 444.9648 | 508.5312 | 487.3424 | [6 empty] | 2015-03-31
AK_MA_SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS1 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 487.3424 | 550.9088 | 529.72 | [6 empty] | 2015-03-31
AK_MA_SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TS2 SUPPLY FAN Supply Flow Rate [cfm] | 487.3424 | 487.3424 | 550.9088 | 550.9088 | [6 empty] | 2015-03-31
AK_MA_SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSE SUPPLY FAN Supply Flow Rate [cfm] | 550.9088 | 572.0976 | 635.664 | 635.664 | [6 empty] | 2015-03-31
AK_MA_SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | SPLIT TSW SUPPLY FAN Supply Flow Rate [cfm] | 572.0976 | 593.2864 | 656.8528 | 656.8528 | [6 empty] | 2015-03-31
AK_MA_SPLIT GN1 SUPPLY FAN Fan Type | SPLIT GN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT GN2 SUPPLY FAN Fan Type | SPLIT GN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT GNE SUPPLY FAN Fan Type | SPLIT GNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT GNW SUPPLY FAN Fan Type | SPLIT GNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT GS1 SUPPLY FAN Fan Type | SPLIT GS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT GS2 SUPPLY FAN Fan Type | SPLIT GS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT GSW SUPPLY FAN Fan Type | SPLIT GSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT MN1 SUPPLY FAN Fan Type | SPLIT MN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT MN2 SUPPLY FAN Fan Type | SPLIT MN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT MNE SUPPLY FAN Fan Type | SPLIT MNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT MNW SUPPLY FAN Fan Type | SPLIT MNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT MS1 SUPPLY FAN Fan Type | SPLIT MS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT MS2 SUPPLY FAN Fan Type | SPLIT MS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT MSE SUPPLY FAN Fan Type | SPLIT MSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT MSW SUPPLY FAN Fan Type | SPLIT MSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT OFFICE SUPPLY FAN Fan Type | SPLIT OFFICE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT TN1 SUPPLY FAN Fan Type | SPLIT TN1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT TN2 SUPPLY FAN Fan Type | SPLIT TN2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT TNE SUPPLY FAN Fan Type | SPLIT TNE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT TNW SUPPLY FAN Fan Type | SPLIT TNW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT TS1 SUPPLY FAN Fan Type | SPLIT TS1 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT TS2 SUPPLY FAN Fan Type | SPLIT TS2 SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT TSE SUPPLY FAN Fan Type | SPLIT TSE SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT TSW SUPPLY FAN Fan Type | SPLIT TSW SUPPLY FAN Fan Type | Fan:OnOff | Fan:OnOff | Fan:OnOff | Fan:OnOff | [6 empty] | 2015-03-31
AK_MA_SPLIT GN1 SUPPLY FAN Fan Power [hp] | SPLIT GN1 SUPPLY FAN Fan Power [hp] | 0.093322 | 0.098257 | 0.10844 | 0.11303 | [6 empty] | 2015-03-31
AK_MA_SPLIT GN2 SUPPLY FAN Fan Power [hp] | SPLIT GN2 SUPPLY FAN Fan Power [hp] | 0.091753 | 0.09654 | 0.10679 | 0.11125 | [6 empty] | 2015-03-31
AK_MA_SPLIT GNE SUPPLY FAN Fan Power [hp] | SPLIT GNE SUPPLY FAN Fan Power [hp] | 0.12072 | 0.13288 | 0.13613 | 0.14798 | [6 empty] | 2015-03-31
AK_MA_SPLIT GNW SUPPLY FAN Fan Power [hp] | SPLIT GNW SUPPLY FAN Fan Power [hp] | 0.16425 | 0.1776 | 0.18702 | 0.19932 | [6 empty] | 2015-03-31
AK_MA_SPLIT GS1 SUPPLY FAN Fan Power [hp] | SPLIT GS1 SUPPLY FAN Fan Power [hp] | 0.16728 | 0.18119 | 0.18483 | 0.19905 | [6 empty] | 2015-03-31
AK_MA_SPLIT GS2 SUPPLY FAN Fan Power [hp] | SPLIT GS2 SUPPLY FAN Fan Power [hp] | 0.17193 | 0.18592 | 0.18945 | 0.2037 | [6 empty] | 2015-03-31
AK_MA_SPLIT GSW SUPPLY FAN Fan Power [hp] | SPLIT GSW SUPPLY FAN Fan Power [hp] | 0.21822 | 0.23905 | 0.24327 | 0.26355 | [6 empty] | 2015-03-31
AK_MA_SPLIT MN1 SUPPLY FAN Fan Power [hp] | SPLIT MN1 SUPPLY FAN Fan Power [hp] | 0.31761 | 0.32779 | 0.36867 | 0.37689 | [6 empty] | 2015-03-31
AK_MA_SPLIT MN2 SUPPLY FAN Fan Power [hp] | SPLIT MN2 SUPPLY FAN Fan Power [hp] | 0.31472 | 0.32463 | 0.3656 | 0.37358 | [6 empty] | 2015-03-31
AK_MA_SPLIT MNE SUPPLY FAN Fan Power [hp] | SPLIT MNE SUPPLY FAN Fan Power [hp] | 0.41287 | 0.44134 | 0.46969 | 0.49673 | [6 empty] | 2015-03-31
AK_MA_SPLIT MNW SUPPLY FAN Fan Power [hp] | SPLIT MNW SUPPLY FAN Fan Power [hp] | 0.50747 | 0.53902 | 0.57766 | 0.60575 | [6 empty] | 2015-03-31
AK_MA_SPLIT MS1 SUPPLY FAN Fan Power [hp] | SPLIT MS1 SUPPLY FAN Fan Power [hp] | 0.51812 | 0.54904 | 0.57527 | 0.60658 | [6 empty] | 2015-03-31
AK_MA_SPLIT MS2 SUPPLY FAN Fan Power [hp] | SPLIT MS2 SUPPLY FAN Fan Power [hp] | 0.52026 | 0.55129 | 0.57719 | 0.60864 | [6 empty] | 2015-03-31
AK_MA_SPLIT MSE SUPPLY FAN Fan Power [hp] | SPLIT MSE SUPPLY FAN Fan Power [hp] | 0.62504 | 0.66822 | 0.70019 | 0.74317 | [6 empty] | 2015-03-31
AK_MA_SPLIT MSW SUPPLY FAN Fan Power [hp] | SPLIT MSW SUPPLY FAN Fan Power [hp] | 0.65388 | 0.70145 | 0.73004 | 0.77683 | [6 empty] | 2015-03-31
AK_MA_SPLIT OFFICE SUPPLY FAN Fan Power [hp] | SPLIT OFFICE SUPPLY FAN Fan Power [hp] | 0.60342 | 0.62199 | 0.63011 | 0.65371 | [6 empty] | 2015-03-31
AK_MA_SPLIT TN1 SUPPLY FAN Fan Power [hp] | SPLIT TN1 SUPPLY FAN Fan Power [hp] | 0.18745 | 0.18023 | 0.22111 | 0.21228 | [6 empty] | 2015-03-31
AK_MA_SPLIT TN2 SUPPLY FAN Fan Power [hp] | SPLIT TN2 SUPPLY FAN Fan Power [hp] | 0.18525 | 0.17659 | 0.21867 | 0.20854 | [6 empty] | 2015-03-31
AK_MA_SPLIT TNE SUPPLY FAN Fan Power [hp] | SPLIT TNE SUPPLY FAN Fan Power [hp] | 0.2407 | 0.24778 | 0.27983 | 0.28116 | [6 empty] | 2015-03-31
AK_MA_SPLIT TNW SUPPLY FAN Fan Power [hp] | SPLIT TNW SUPPLY FAN Fan Power [hp] | 0.30952 | 0.31299 | 0.35769 | 0.35298 | [6 empty] | 2015-03-31
AK_MA_SPLIT TS1 SUPPLY FAN Fan Power [hp] | SPLIT TS1 SUPPLY FAN Fan Power [hp] | 0.34653 | 0.34352 | 0.38941 | 0.38218 | [6 empty] | 2015-03-31
AK_MA_SPLIT TS2 SUPPLY FAN Fan Power [hp] | SPLIT TS2 SUPPLY FAN Fan Power [hp] | 0.34802 | 0.34521 | 0.39088 | 0.38379 | [6 empty] | 2015-03-31
AK_MA_SPLIT TSE SUPPLY FAN Fan Power [hp] | SPLIT TSE SUPPLY FAN Fan Power [hp] | 0.39549 | 0.39936 | 0.44742 | 0.44645 | [6 empty] | 2015-03-31
AK_MA_SPLIT TSW SUPPLY FAN Fan Power [hp] | SPLIT TSW SUPPLY FAN Fan Power [hp] | 0.41196 | 0.42029 | 0.46658 | 0.46877 | [6 empty] | 2015-03-31

## HVAC_Summary
Small Office | Climate Zone 1 | 2A | [5 empty] | Small Office | Climate Zone 2 | 3A | [5 empty] | Small Office | Climate Zone 3 | 3B | [5 empty] | Small Office | Climate Zone 4 | 4A | [5 empty] | Small Office | Climate Zone 5 | 5A
90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 89003.2575 | 89003.2575 | New Construction | 88590.9613 | 88590.9613 | -412.2962 | -412.2962 | New Construction | 87346.8177 | 87346.8177 | New Construction | 87024.8309 | 87024.8309 | -321.9867 | -321.9867 | New Construction | 89181.2744 | 89181.2744 | New Construction | 88752.3229 | 88752.3229 | -428.9515 | -428.9515 | New Construction | 85119.2734 | 85119.2734 | New Construction | 85140.9706 | 85140.9706 | 21.6972 | 21.6972 | New Construction | 84608.5077 | 84608.5077 | New Construction | 84592.4791 | 84592.4791 | -16.0286 | -16.0286
Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 28481.0241 | 28481.0241 | 15 | 27758.7733 | 27758.7733 | -722.2508 | -722.2508 | 15 | 27129.4588 | 27129.4588 | 15 | 26522.7927 | 26522.7927 | -606.6661 | -606.6661 | 15 | 26800.4588 | 26800.4588 | 15 | 26066.477 | 26066.477 | -733.9818 | -733.9818 | 15 | 25839.0307 | 25839.0307 | 15 | 25432.0642 | 25432.0642 | -406.9664 | -406.9664 | 15 | 25335.7739 | 25335.7739 | 15 | 25093.2772 | 25093.2772 | -242.4968 | -242.4968
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 70191.2681 | 98672.2923 | 30 | 69006.2624 | 96765.0356 | 0 | -1907.2566 | 30 | 69302.5138 | 96431.9726 | 30 | 68117.508 | 94640.3007 | 0 | -1791.6719 | 30 | 72857.5311 | 99657.99 | 30 | 71672.5254 | 97739.0024 | 0 | -1918.9876 | 30 | 67376.8794 | 93215.9101 | 30 | 66488.1251 | 91920.1893 | 0 | -1295.7208 | 30 | 67228.7537 | 92564.5276 | 30 | 66043.7479 | 91137.0251 | 0 | -1427.5025
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 1030.7541 | 40 | 0 | 0 | 40 | 0 | 0 |  | 992.2259 | 40 | 0 | 0 | 40 | 0 | 0 |  | 1034.6645 | 40 | 0 | 0 | 40 | 0 | 0 |  | 728.1584 | 40 | 0 | 0 | 40 | 0 | 0 |  | 870.8361
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0
Residual Year 40 |  | -56287.8535 | Residual Year 40 |  | -55257.0993 |  |  | Residual Year 40 |  | -55244.8288 | Residual Year 40 |  | -54252.6029 |  |  | Residual Year 40 |  | -57505.1737 | Residual Year 40 |  | -56470.5093 |  |  | Residual Year 40 |  | -53530.9298 | Residual Year 40 |  | -52802.7715 |  |  | Residual Year 40 |  | -53264.4271 | Residual Year 40 |  | -52393.591
Large Office | Climate Zone 1 | 2A | [5 empty] | Large Office | Climate Zone 2 | 3A | [5 empty] | Large Office | Climate Zone 3 | 3B | [5 empty] | Large Office | Climate Zone 4 | 4A | [5 empty] | Large Office | Climate Zone 5 | 5A
90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 9571093.7701 | 9571093.7701 | New Construction | 9411207.2739 | 9411207.2739 | -159886.4963 | -159886.4963 | New Construction | 9675103.5811 | 9675103.5811 | New Construction | 9556732.4775 | 9556732.4775 | -118371.1036 | -118371.1036 | New Construction | 9326080.4172 | 9326080.4172 | New Construction | 9255585.64 | 9255585.64 | -70494.7772 | -70494.7772 | New Construction | 9723286.2462 | 9723286.2462 | New Construction | 9546437.8272 | 9546437.8272 | -176848.419 | -176848.419 | New Construction | 9717248.476 | 9717248.476 | New Construction | 9581811.9314 | 9581811.9314 | -135436.5446 | -135436.5446
Maintenance | 3060.99 | 3060.99 | Maintenance | 3060.99 | 3060.99 | 0 | 0 | Maintenance | 3060.99 | 3060.99 | Maintenance | 3060.99 | 3060.99 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 3060.99 | 3060.99 | Maintenance | 3060.99 | 3060.99 | 0 | 0 | Maintenance | 3060.99 | 3060.99 | Maintenance | 3060.99 | 3060.99 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 |  | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 1217887.6749 | 1217887.6749 | 15 | 1106059.2975 | 1106059.2975 | -111828.3774 | -111828.3774 | 15 | 1226793.1493 | 1226793.1493 | 15 | 1114476.8127 | 1114476.8127 | -112316.3366 | -112316.3366 | 15 | 788203.2086 | 788203.2086 | 15 | 757738.1602 | 757738.1602 | -30465.0485 | -30465.0485 | 15 | 1232069.4284 | 1232069.4284 | 15 | 1128899.9013 | 1128899.9013 | -103169.5271 | -103169.5271 | 15 | 1233898.4779 | 1233898.4779 | 15 | 1130449.0868 | 1130449.0868 | -103449.3911 | -103449.3911
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 1734840.1215 | 1734840.1215 | 20 | 1816874.856 | 1816874.856 | 82034.7344 | 82034.7344 | 20 | 1708761.2847 | 1708761.2847 | 20 | 1800181.0131 | 1800181.0131 | 91419.7285 | 91419.7285 | 20 | 1641622.7929 | 1641622.7929 | 20 | 1704038.5143 | 1704038.5143 | 62415.7214 | 62415.7214 | 20 | 1708576.7608 | 1708576.7608 | 20 | 1728748.3749 | 1728748.3749 | 20171.6141 | 20171.6141 | 20 | 1678556.357 | 1678556.357 | 20 | 1734152.9587 | 1734152.9587 | 55596.6018 | 55596.6018
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 577866.4212 | 577866.4212 | 23 | 542344.2025 | 542344.2025 | -35522.2187 | -35522.2187 | 23 | 549094.7571 | 549094.7571 | 23 | 538428.4425 | 538428.4425 | -10666.3147 | -10666.3147 | 23 | 534026.0439 | 534026.0439 | 23 | 530085.2416 | 530085.2416 | -3940.8024 | -3940.8024 | 23 | 545972.7228 | 545972.7228 | 23 | 533859.0499 | 533859.0499 | -12113.6729 | -12113.6729 | 23 | 539306.5203 | 539306.5203 | 23 | 534281.3061 | 534281.3061 | -5025.2142 | -5025.2142
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 10588936.6952 | 11806824.37 | 30 | 10433885.8611 | 11539945.1586 | -15169.7864 | -266879.2114 | 30 | 10751964.3648 | 11978757.5141 | 30 | 10611651.9154 | 11726128.7281 | -36770.1112 | -252628.7861 | 30 | 10974860.6498 | 11763063.8584 | 30 | 10762835.85 | 11520574.0102 | -27117.6057 | -242489.8483 | 30 | 10768752.2491 | 12000821.6775 | 30 | 10610083.3367 | 11738983.238 | 81.5611 | -261838.4395 | 30 | 10782946.4069 | 12016844.8848 | 30 | 10642283.7215 | 11772732.8082 | -22237.1644 | -244112.0766
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 121421.6116 | 121421.6116 | 35 | 113466.3067 | 113466.3067 |  | -7955.3048 | 35 | 151838.3713 | 151838.3713 | 35 | 141200.4146 | 141200.4146 |  | -10637.9567 | 35 | 140948.1135 | 140948.1135 | 35 | 131506.323 | 131506.323 |  | -9441.7905 | 35 | 164395.6055 | 164395.6055 | 35 | 152212.3489 | 152212.3489 |  | -12183.2566 | 35 | 175410.873 | 175410.873 | 35 | 160953.526 | 160953.526 |  | -14457.347
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 156728.847 | 40 | 0 | 0 | 40 | 0 | 0 |  | 142881.1773 | 40 | 0 | 0 | 40 | 0 | 0 |  | 160625.8814 | 40 | 0 | 0 | 40 | 0 | 0 |  | 153771.9973 | 40 | 0 | 0 | 40 | 0 | 0 |  | 141961.1912
Residual Year 30 |  | -1286760.0374 | Residual Year 30 |  | -1301929.8238 |  |  | Residual Year 30 |  | -1258050.7997 | Residual Year 30 |  | -1294820.9109 |  |  | Residual Year 30 |  | -1212443.2196 | Residual Year 30 |  | -1239560.8253 |  |  | Residual Year 30 |  | -1257580.5784 | Residual Year 30 |  | -1257499.0173 |  |  | Residual Year 30 |  | -1239506.6279 | Residual Year 30 |  | -1261743.7923
Residual Year 40 |  | -7720077.1175 | Residual Year 40 |  | -7563348.2705 |  |  | Residual Year 40 |  | -7850296.5789 | Residual Year 40 |  | -7707415.4017 |  |  | Residual Year 40 |  | -7839431.98 | Residual Year 40 |  | -7678806.0986 |  |  | Residual Year 40 |  | -7873196.1613 | Residual Year 40 |  | -7719424.1641 |  |  | Residual Year 40 |  | -7890971.2649 | Residual Year 40 |  | -7749010.0737
Standalone Retail | Climate Zone 1 | 2A | [5 empty] | Standalone Retail | Climate Zone 2 | 3A | [5 empty] | Standalone Retail | Climate Zone 3 | 3B | [5 empty] | Standalone Retail | Climate Zone 4 | 4A | [5 empty] | Standalone Retail | Climate Zone 5 | 5A
90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 287320.9066 | 287320.9066 | New Construction | 282527.3879 | 282527.3879 | -4793.5187 | -4793.5187 | New Construction | 285039.3541 | 285039.3541 | New Construction | 280375.9435 | 280375.9435 | -4663.4106 | -4663.4106 | New Construction | 294310.257 | 294310.257 | New Construction | 289121.9689 | 289121.9689 | -5188.2881 | -5188.2881 | New Construction | 283083.6302 | 283083.6302 | New Construction | 279038.9129 | 279038.9129 | -4044.7173 | -4044.7173 | New Construction | 278218.0493 | 278218.0493 | New Construction | 273547.7874 | 273547.7874 | -4670.2619 | -4670.2619
Maintenance | 430.584 | 430.584 | Maintenance | 430.584 | 430.584 | 0 | 0 | Maintenance | 430.584 | 430.584 | Maintenance | 430.584 | 430.584 | 0 | 0 | Maintenance | 430.584 | 430.584 | Maintenance | 430.584 | 430.584 | 0 | 0 | Maintenance | 430.584 | 430.584 | Maintenance | 430.584 | 430.584 | 0 | 0 | Maintenance | 430.584 | 430.584 | Maintenance | 430.584 | 430.584 | 0 | 0
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 78542.0117 | 78542.0117 | 15 | 76478.0851 | 76478.0851 | -2063.9266 | -2063.9266 | 15 | 75980.5424 | 75980.5424 | 15 | 74310.5076 | 74310.5076 | -1670.0347 | -1670.0347 | 15 | 75273.0579 | 75273.0579 | 15 | 73210.4793 | 73210.4793 | -2062.5786 | -2062.5786 | 15 | 74839.9983 | 74839.9983 | 15 | 73273.4062 | 73273.4062 | -1566.5921 | -1566.5921 | 15 | 70850.0297 | 70850.0297 | 15 | 69170.9788 | 69170.9788 | -1679.0509 | -1679.0509
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 3350.0384 | 3350.0384 | 20 | 4181.6738 | 4181.6738 | 831.6354 | 831.6354 | 20 | 3350.0384 | 3350.0384 | 20 | 4181.6738 | 4181.6738 | 831.6354 | 831.6354 | 20 | 3350.0384 | 3350.0384 | 20 | 4181.6738 | 4181.6738 | 831.6354 | 831.6354 | 20 | 3350.0384 | 3350.0384 | 20 | 4181.6738 | 4181.6738 | 831.6354 | 831.6354 | 20 | 3350.0384 | 3350.0384 | 20 | 4181.6738 | 4181.6738 | 831.6354 | 831.6354
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 264505.3799 | 343047.3916 | 30 | 259528.3597 | 336006.4448 | 1675.0192 | -7040.9468 | 30 | 264342.1989 | 340322.7413 | 30 | 259120.4073 | 333430.9149 | 0 | -6891.8264 | 30 | 276417.5922 | 351690.65 | 30 | 270951.029 | 344161.5083 | -2090.8369 | -7529.1418 | 30 | 263118.3415 | 337958.3398 | 30 | 258549.2738 | 331822.68 | -415.8177 | -6135.6598 | 30 | 261160.1696 | 332010.1994 | 30 | 255856.7875 | 325027.7663 | -415.8177 | -6982.4331
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 202517.5905 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | -205037.5124 | 40 | 0 | 0 | 40 | 0 | 0 |  | 3568.2425 | 40 | 0 | 0 | 40 | 0 | 0 |  | 4095.2717
Residual Year 30 |  | -1675.0192 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | -2090.8369 |  |  | Residual Year 30 |  | -1675.0192 | Residual Year 30 |  | -2090.8369 |  |  | Residual Year 30 |  | -1675.0192 | Residual Year 30 |  | -2090.8369
Residual Year 40 |  | -202517.5905 | Residual Year 40 |  | 0 |  |  | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  |  | Residual Year 40 |  | 0 | Residual Year 40 |  | -205037.5124 |  |  | Residual Year 40 |  | -200358.8938 | Residual Year 40 |  | -196790.6513 |  |  | Residual Year 40 |  | -197723.4563 | Residual Year 40 |  | -193628.1846
Primary School | Climate Zone 1 | 2A | [5 empty] | Primary School | Climate Zone 2 | 3A | [5 empty] | Primary School | Climate Zone 3 | 3B | [5 empty] | Primary School | Climate Zone 4 | 4A | [5 empty] | Primary School | Climate Zone 5 | 5A
90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 1166932.6649 | 1166932.6649 | New Construction | 1146712.2582 | 1146712.2582 | -20220.4067 | -20220.4067 | New Construction | 1158819.4473 | 1158819.4473 | New Construction | 1158051.2424 | 1158051.2424 | -768.205 | -768.205 | New Construction | 1059982.112 | 1059982.112 | New Construction | 1046315.4697 | 1046315.4697 | -13666.6424 | -13666.6424 | New Construction | 1157975.1305 | 1157975.1305 | New Construction | 1149028.5542 | 1149028.5542 | -8946.5763 | -8946.5763 | New Construction | 1159653.6467 | 1159653.6467 | New Construction | 1148961.247 | 1148961.247 | -10692.3997 | -10692.3997
Maintenance | 2567.0514 | 2567.0514 | Maintenance | 2557.2198 | 2557.2198 | -9.8316 | -9.8316 | Maintenance | 2566.2068 | 2566.2068 | Maintenance | 2551.5891 | 2551.5891 | -14.6177 | -14.6177 | Maintenance | 1256.5922 | 1256.5922 | Maintenance | 1285.1666 | 1285.1666 | 28.5744 | 28.5744 | Maintenance | 2563.3914 | 2563.3914 | Maintenance | 2550.4629 | 2550.4629 | -12.9285 | -12.9285 | Maintenance | 2564.7991 | 2564.7991 | Maintenance | 2549.8999 | 2549.8999 | -14.8992 | -14.8992
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 545454.3329 | 545454.3329 | 15 | 533495.3074 | 533495.3074 | -11959.0255 | -11959.0255 | 15 | 534669.0529 | 534669.0529 | 15 | 528784.1563 | 528784.1563 | -5884.8965 | -5884.8965 | 15 | 385514.0549 | 385514.0549 | 15 | 383277.5473 | 383277.5473 | -2236.5076 | -2236.5076 | 15 | 531803.5571 | 531803.5571 | 15 | 528118.2229 | 528118.2229 | -3685.3342 | -3685.3342 | 15 | 531301.0107 | 531301.0107 | 15 | 525981.6046 | 525981.6046 | -5319.4061 | -5319.4061
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 26059.7564 | 26059.7564 | 20 | 26149.8859 | 26149.8859 | 90.1295 | 90.1295 | 20 | 28007.4059 | 28007.4059 | 20 | 41137.4758 | 41137.4758 | 13130.0699 | 13130.0699 | 20 | 27773.3324 | 27773.3324 | 20 | 27757.8085 | 27757.8085 | -15.5239 | -15.5239 | 20 | 28503.9842 | 28503.9842 | 20 | 28826.7908 | 28826.7908 | 322.8066 | 322.8066 | 20 | 28960.5732 | 28960.5732 | 20 | 29295.7782 | 29295.7782 | 335.2051 | 335.2051
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 1114095.3516 | 1659549.6845 | 30 | 1039392.2165 | 1572887.5239 | 120.3201 | -86662.1606 | 30 | 1049354.9443 | 1584023.9972 | 30 | 1035436.9173 | 1564221.0736 | -6419.9892 | -19802.9236 | 30 | 1103950.0881 | 1489464.143 | 30 | 1082719.9741 | 1465997.5214 | 229.896 | -23466.6215 | 30 | 1047666.1018 | 1579469.659 | 30 | 1036017.2675 | 1564135.4904 | -19.2218 | -15334.1686 | 30 | 1047659.668 | 1578960.6786 | 30 | 1035345.6924 | 1561327.297 | -27.4351 | -17633.3817
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 28273.4863 | 28273.4863 | 35 | 27115.7923 | 27115.7923 |  | -1157.694 | 35 | 34571.4086 | 34571.4086 | 35 | 33556.0884 | 33556.0884 |  | -1015.3202 | 35 | 33548.495 | 33548.495 | 35 | 31993.5568 | 31993.5568 |  | -1554.9383 | 35 | 37240.0547 | 37240.0547 | 35 | 36244.7844 | 36244.7844 |  | -995.2703 | 35 | 39693.7625 | 39693.7625 | 35 | 38712.5904 | 38712.5904 |  | -981.1721
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 54780.741 | 40 | 0 | 0 | 40 | 0 | 0 |  | 12110.5913 | 40 | 0 | 0 | 40 | 0 | 0 |  | 16231.7161 | 40 | 0 | 0 | 40 | 0 | 0 |  | 9847.4231 | 40 | 0 | 0 | 40 | 0 | 0 |  | 10823.4571
Residual Year 30 |  | -17068.9477 | Residual Year 30 |  | -16948.6276 |  |  | Residual Year 30 |  | -18942.4756 | Residual Year 30 |  | -25362.4648 |  |  | Residual Year 30 |  | -18679.3083 | Residual Year 30 |  | -18449.4124 |  |  | Residual Year 30 |  | -19571.9999 | Residual Year 30 |  | -19591.2217 |  |  | Residual Year 30 |  | -20150.8241 | Residual Year 30 |  | -20178.2592
Residual Year 40 |  | -948782.7622 | Residual Year 40 |  | -894002.0211 |  |  | Residual Year 40 |  | -907425.6165 | Residual Year 40 |  | -895315.0251 |  |  | Residual Year 40 |  | -893227.2632 | Residual Year 40 |  | -876995.5472 |  |  | Residual Year 40 |  | -907631.9672 | Residual Year 40 |  | -897784.544 |  |  | Residual Year 40 |  | -909563.3405 | Residual Year 40 |  | -898739.8834
Small Hotel | Climate Zone 1 | 2A | [5 empty] | Small Hotel | Climate Zone 2 | 3A | [5 empty] | Small Hotel | Climate Zone 3 | 3B | [5 empty] | Small Hotel | Climate Zone 4 | 4A | [5 empty] | Small Hotel | Climate Zone 5 | 5A
90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 151413.908 | 151413.908 | New Construction | 151219.1053 | 151219.1053 | -194.8027 | -194.8027 | New Construction | 151554.2089 | 151554.2089 | New Construction | 151314.1282 | 151314.1282 | -240.0807 | -240.0807 | New Construction | 158184.2937 | 158184.2937 | New Construction | 158067.577 | 158067.577 | -116.7167 | -116.7167 | New Construction | 148205.4273 | 148205.4273 | New Construction | 148506.1082 | 148506.1082 | 300.6809 | 300.6809 | New Construction | 147848.1487 | 147848.1487 | New Construction | 147688.291 | 147688.291 | -159.8577 | -159.8577
Maintenance | 396.0573 | 396.0573 | Maintenance | 394.3681 | 394.3681 | -1.6892 | -1.6892 | Maintenance | 396.902 | 396.902 | Maintenance | 395.2127 | 395.2127 | -1.6892 | -1.6892 | Maintenance | 403.9404 | 403.9404 | Maintenance | 402.2512 | 402.2512 | -1.6892 | -1.6892 | Maintenance | 394.3681 | 394.3681 | Maintenance | 393.242 | 393.242 | -1.1261 | -1.1261 | Maintenance | 394.9312 | 394.9312 | Maintenance | 393.242 | 393.242 | -1.6892 | -1.6892
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 50249.9977 | 50249.9977 | 15 | 49266.2143 | 49266.2143 | -983.7834 | -983.7834 | 15 | 49988.6603 | 49988.6603 | 15 | 48971.5938 | 48971.5938 | -1017.0665 | -1017.0665 | 15 | 50378.3291 | 50378.3291 | 15 | 49489.8982 | 49489.8982 | -888.4308 | -888.4308 | 15 | 48598.0217 | 48598.0217 | 15 | 47773.1589 | 47773.1589 | -824.8628 | -824.8628 | 15 | 47698.3361 | 47698.3361 | 15 | 46939.4986 | 46939.4986 | -758.8375 | -758.8375
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 717.5341 | 717.5341 | 20 | 900.0741 | 900.0741 | 182.54 | 182.54 | 20 | 717.5341 | 717.5341 | 20 | 900.0741 | 900.0741 | 182.54 | 182.54 | 20 | 717.5341 | 717.5341 | 20 | 900.0741 | 900.0741 | 182.54 | 182.54 | 20 | 717.5341 | 717.5341 | 20 | 900.0741 | 900.0741 | 182.54 | 182.54 | 20 | 717.5341 | 717.5341 | 20 | 900.0741 | 900.0741 | 182.54 | 182.54
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 155443.3725 | 205693.3702 | 30 | 152605.957 | 201872.1713 | -91.27 | -3821.1989 | 30 | 156010.8556 | 205999.5159 | 30 | 153173.4401 | 202145.034 | -91.27 | -3854.482 | 30 | 166509.2928 | 216887.6219 | 30 | 163671.8774 | 213161.7756 | -91.27 | -3725.8463 | 30 | 152322.2155 | 200920.2372 | 30 | 150052.2831 | 197825.442 | -91.27 | -3094.7952 | 30 | 152889.6986 | 200588.0347 | 30 | 149768.5416 | 196708.0402 | -91.27 | -3879.9946
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 2219.5381 | 40 | 0 | 0 | 40 | 0 | 0 |  | 2230.6325 | 40 | 0 | 0 | 40 | 0 | 0 |  | 2187.7539 | 40 | 0 | 0 | 40 | 0 | 0 |  | 1788.2425 | 40 | 0 | 0 | 40 | 0 | 0 |  | 2333.7172
Residual Year 30 |  | -358.7671 | Residual Year 30 |  | -450.0371 |  |  | Residual Year 30 |  | -358.7671 | Residual Year 30 |  | -450.0371 |  |  | Residual Year 30 |  | -358.7671 | Residual Year 30 |  | -450.0371 |  |  | Residual Year 30 |  | -358.7671 | Residual Year 30 |  | -450.0371 |  |  | Residual Year 30 |  | -358.7671 | Residual Year 30 |  | -450.0371
Residual Year 40 |  | -120378.9142 | Residual Year 40 |  | -118159.3761 |  |  | Residual Year 40 |  | -120670.1238 | Residual Year 40 |  | -118439.4914 |  |  | Residual Year 40 |  | -127798.9716 | Residual Year 40 |  | -125611.2177 |  |  | Residual Year 40 |  | -117747.4842 | Residual Year 40 |  | -115959.2417 |  |  | Residual Year 40 |  | -117825.9111 | Residual Year 40 |  | -115492.1939
Mid-rise Apartment | Climate Zone 1 | 2A | [5 empty] | Mid-rise Apartment | Climate Zone 2 | 3A | [5 empty] | Mid-rise Apartment | Climate Zone 3 | 3B | [5 empty] | Mid-rise Apartment | Climate Zone 4 | 4A | [5 empty] | Mid-rise Apartment | Climate Zone 5 | 5A
90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost
Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs with First Replacement Only | With Repeated Replacements | Category | All Costs with First Replacement Only | With Repeated Replacements | 30 Year | 40 Year
New Construction | 369637.0211 | 369637.0211 | New Construction | 378654.305 | 378654.305 | 9017.2839 | 9017.2839 | New Construction | 357413.6473 | 357413.6473 | New Construction | 366277.2907 | 366277.2907 | 8863.6433 | 8863.6433 | New Construction | 348463.0086 | 348463.0086 | New Construction | 356054.5001 | 356054.5001 | 7591.4915 | 7591.4915 | New Construction | 354779.9994 | 354779.9994 | New Construction | 366206.8531 | 366206.8531 | 11426.8537 | 11426.8537 | New Construction | 333912.0184 | 333912.0184 | New Construction | 345631.6847 | 345631.6847 | 11719.6663 | 11719.6663
Maintenance | 0 | 0 | Maintenance | 480 | 480 | 480 | 480 | Maintenance | 0 | 0 | Maintenance | 480 | 480 | 480 | 480 | Maintenance | 0 | 0 | Maintenance | 480 | 480 | 480 | 480 | Maintenance | 0 | 0 | Maintenance | 480 | 480 | 480 | 480 | Maintenance | 0 | 0 | Maintenance | 480 | 480 | 480 | 480
Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
15 | 511654.8615 | 511654.8615 | 15 | 521338.7028 | 521338.7028 | 9683.8412 | 9683.8412 | 15 | 493612.6503 | 493612.6503 | 15 | 503069.8836 | 503069.8836 | 9457.2333 | 9457.2333 | 15 | 480432.9109 | 480432.9109 | 15 | 488015.9 | 488015.9 | 7582.9891 | 7582.9891 | 15 | 489736.2103 | 489736.2103 | 15 | 501721.975 | 501721.975 | 11985.7647 | 11985.7647 | 15 | 458960.9745 | 458960.9745 | 15 | 471385.9948 | 471385.9948 | 12425.0202 | 12425.0202
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 511654.8615 | 30 | 0 | 521338.7028 | 0 | 9683.8412 | 30 | 0 | 493612.6503 | 30 | 0 | 503069.8836 | 0 | 9457.2333 | 30 | 0 | 480432.9109 | 30 | 0 | 488015.9 | 0 | 7582.9891 | 30 | 0 | 489736.2103 | 30 | 0 | 501721.975 | 0 | 11985.7647 | 30 | 0 | 458960.9745 | 30 | 0 | 471385.9948 | 0 | 12425.0202
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | -3227.9471 | 40 | 0 | 0 | 40 | 0 | 0 |  | -3152.4111 | 40 | 0 | 0 | 40 | 0 | 0 |  | -2527.663 | 40 | 0 | 0 | 40 | 0 | 0 |  | -3995.2549 | 40 | 0 | 0 | 40 | 0 | 0 |  | -4141.6734
Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  |  | Residual Year 30 |  | 0 | Residual Year 30 |  | 0
Residual Year 40 |  | -170551.6205 | Residual Year 40 |  | -173779.5676 |  |  | Residual Year 40 |  | -164537.5501 | Residual Year 40 |  | -167689.9612 |  |  | Residual Year 40 |  | -160144.3036 | Residual Year 40 |  | -162671.9667 |  |  | Residual Year 40 |  | -163245.4034 | Residual Year 40 |  | -167240.6583 |  |  | Residual Year 40 |  | -152986.9915 | Residual Year 40 |  | -157128.6649
| 511654.8615 |  |  | 521338.7028 |  |  |  |  | 493612.6503 |  |  | 503069.8836 |  |  |  |  | 480432.9109 |  |  | 488015.9 |  |  |  |  | 489736.2103 |  |  | 501721.975 |  |  |  |  | 458960.9745 |  |  | 471385.9948

## HVAC Small Office Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Small Office | [7 empty] | Small Office
[8 empty] | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
[7 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 2 | 3A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 3 | 3B | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 4 | 4A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 5 | 5A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | First cost difference |  | 2016 | vs | 2019
Costs row marked x, other rows not marked | [7 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Total new construction (added cost)
| Addendum or general | Key Word | Description |  |  | Parameter | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | 2A | 3A | 3B | 4A | 5A
| load change | [6 empty] | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
| HVAC System - general load change |  | Prototype Data is set to a minimum of 1.5 tons as no incremental cost benefit below minimum size.
x |  | Heat_Pump |  | PSZ-AC:1 | CAVDX | PSZ-AC:1 Cooling Capacity [ton] | US_SO_PSZ-AC:1 Cooling Capacity [ton] | 2.0555 | 1.9588 | 5270.0634 | 0 | 15 | 6421.4732 | 5080.7822 | 0 | 15 | 6188.0866 | 1.9522 | 1.8608 | 5065.9161 | 0 | 15 | 6170.392 | 4861.4243 | 0 | 15 | 5926.9939 | 1.8175 | 1.7154 | 4764.47 | 0 | 15 | 5811.5932 | 4535.8843 | 0 | 15 | 5539.5172 | 1.8066 | 1.715 | 4740.0516 | 0 | 15 | 5782.529 | 4535.0125 | 0 | 15 | 5538.4794 | 1.6903 | 1.5992 | 4479.7164 | 0 | 15 | 5472.6628 | 4275.9818 | 0 | 15 | 5230.166 | -189.2812 | -204.4918 | -228.5856 | -205.0391 | -203.7345
x |  | Heat_Pump |  | PSZ-AC:2 | CAVDX | PSZ-AC:2 Cooling Capacity [ton] | US_SO_PSZ-AC:2 Cooling Capacity [ton] | 1.9302 | 1.8385 | 5016.7357 | 0 | 15 | 6111.8547 | 4811.5184 | 0 | 15 | 5867.593 | 1.7058 | 1.6451 | 4514.5143 | 0 | 15 | 5514.0813 | 4378.5809 | 0 | 15 | 5352.2855 | 1.7105 | 1.6322 | 4524.9066 | 0 | 15 | 5526.4508 | 4349.6378 | 0 | 15 | 5317.8357 | 1.5726 | 1.5114 | 4216.3328 | 0 | 15 | 5159.1683 | 4079.4576 | 0 | 15 | 4996.2514 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | -205.2173 | -135.9333 | -175.2687 | -136.8752 | 0
x |  | Heat_Pump |  | PSZ-AC:3 | CAVDX | PSZ-AC:3 Cooling Capacity [ton] | US_SO_PSZ-AC:3 Cooling Capacity [ton] | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 0 | 0 | 0 | 0 | 0
x |  | Heat_Pump |  | PSZ-AC:4 | CAVDX | PSZ-AC:4 Cooling Capacity [ton] | US_SO_PSZ-AC:4 Cooling Capacity [ton] | 1.8943 | 1.8025 | 4936.3213 | 0 | 15 | 6016.1406 | 4730.8176 | 0 | 15 | 5771.5381 | 1.7056 | 1.63 | 4513.967 | 0 | 15 | 5513.4299 | 4344.6994 | 0 | 15 | 5311.9577 | 1.7121 | 1.617 | 4528.6104 | 0 | 15 | 5530.8593 | 4315.8072 | 0 | 15 | 5277.5686 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | -205.5037 | -169.2675 | -212.8031 | 0 | 0
x |  | Heat_Pump |  | PSZ-AC:5 | CAVDX | PSZ-AC:5 Cooling Capacity [ton] | US_SO_PSZ-AC:5 Cooling Capacity [ton] | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 1.5 | 1.5 | 4053.8551 | 0 | 15 | 4965.7778 | 4053.8551 | 0 | 15 | 4965.7778 | 0 | 0 | 0 | 0 | 0
90.1-16bo furnace efficiency
x |  | Furnace_eff | 5 units |  |  | Furnace heating capacity [Btuh] | US_SO_Furnace heating capacity [Btuh] | 5 | 5 | 22556.2958 | 0 | 75 | 26616.5276 | 23296.8958 | 0 | 75 | 27431.1876 | 5 | 5 | 22556.2958 | 0 | 75 | 26616.5276 | 23296.8958 | 0 | 75 | 27431.1876 | 5 | 5 | 22556.2958 | 0 | 75 | 26616.5276 | 23296.8958 | 0 | 75 | 27431.1876 | 5 | 5 | 22556.2958 | 0 | 75 | 26616.5276 | 23296.8958 | 0 | 75 | 27431.1876 | 5 | 5 | 22556.2958 | 0 | 75 | 26616.5276 | 23296.8958 | 0 | 75 | 27431.1876 | 740.6 | 740.6 | 740.6 | 740.6 | 740.6
x | 90.1-16g occ standby controls | occ_standby | 5 conditioned zones |  |  |  |  | 0 | 5 | 0 | 0 | 0 | 0 | 150.7284 | 0 | 75 | 264.5105 | 0 | 5 | 0 | 0 | 0 | 0 | 150.7284 | 0 | 75 | 264.5105 | 0 | 5 | 0 | 0 | 0 | 0 | 150.7284 | 0 | 75 | 264.5105 | 0 | 5 | 0 | 0 | 0 | 0 | 150.7284 | 0 | 75 | 264.5105 | 0 | 5 | 0 | 0 | 0 | 0 | 150.7284 | 0 | 75 | 264.5105 | 150.7284 | 150.7284 | 150.7284 | 150.7284 | 150.7284
X | HVAC System - general load change | Air Distribution | curve fit from Solarc cost calculations - described in HVAC Costs Comp. Material, labor, and project cost adjustments applied in this worksheet. |  |  | Sum of PSZ-AC:1 Supply Flow Rate [cfm] to PSZ-AC:5 Supply Flow Rate [cfm] |  | 3093.5648 | 2924.0544 | 43116.1311 | 0 | 30 | 70191.2681 | 42412.5087 | 0 | 30 | 69006.2624 | 2966.432 | 2796.9216 | 42588.4143 | 0 | 30 | 69302.5138 | 41884.7919 | 0 | 30 | 68117.508 | 3474.9632 | 3305.4528 | 44699.2815 | 0 | 30 | 72857.5311 | 43995.6591 | 0 | 30 | 71672.5254 | 2690.9776 | 2563.8448 | 41445.0279 | 0 | 30 | 67376.8794 | 40917.3111 | 0 | 30 | 66488.1251 | 2669.7888 | 2500.2784 | 41357.0751 | 0 | 30 | 67228.7537 | 40653.4527 | 0 | 30 | 66043.7479 | -703.6224 | -703.6224 | -703.6224 | -527.7168 | -703.6224
|  |  | Material y = 0.2902x + 4511.3 R² = 0.8963 |  |  | PSZ-AC:1 Supply Flow Rate [cfm] | US_SO_PSZ-AC:1 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 699.2304 | 656.8528 | [8 empty] | 783.9856 | 741.608 | [8 empty] | 635.664 | 593.2864 | [8 empty] | 635.664 | 593.2864
|  |  | Labor y = 1.5764x + 9922.5 R² = 0.9473 |  |  | PSZ-AC:2 Supply Flow Rate [cfm] | US_SO_PSZ-AC:2 Supply Flow Rate [cfm] | 678.0416 | 635.664 | [8 empty] | 635.664 | 593.2864 | [8 empty] | 762.7968 | 720.4192 | [8 empty] | 572.0976 | 550.9088 | [8 empty] | 550.9088 | 508.5312
[6 empty] | PSZ-AC:3 Supply Flow Rate [cfm] | US_SO_PSZ-AC:3 Supply Flow Rate [cfm] | 508.5312 | 487.3424 | [8 empty] | 466.1536 | 444.9648 | [8 empty] | 529.72 | 508.5312 | [8 empty] | 444.9648 | 423.776 | [8 empty] | 444.9648 | 423.776
[6 empty] | PSZ-AC:4 Supply Flow Rate [cfm] | US_SO_PSZ-AC:4 Supply Flow Rate [cfm] | 656.8528 | 614.4752 | [8 empty] | 635.664 | 593.2864 | [8 empty] | 762.7968 | 720.4192 | [8 empty] | 529.72 | 508.5312 | [8 empty] | 508.5312 | 466.1536
[6 empty] | PSZ-AC:5 Supply Flow Rate [cfm] | US_SO_PSZ-AC:5 Supply Flow Rate [cfm] | 572.0976 | 550.9088 | [8 empty] | 529.72 | 508.5312 | [8 empty] | 635.664 | 614.4752 | [8 empty] | 508.5312 | 487.3424 | [8 empty] | 529.72 | 508.5312
[8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
[8 empty] | 550.9088 3: 89003.2575; 550.9088 6: 125288.8199; 550.9088 7: 88590.9613 |  | 124460.7337 |  |  | 87346.8177 |  |  | 123048.5002 | 87024.8309 |  |  | 122335.9988 |  |  | 89181.2744 |  |  | 126274.5176 | 88752.3229 |  |  | 125434.7005 |  |  | 85119.2734 |  |  | 119832.4377 | 85140.9706 |  |  | 119615.8874 |  |  | 84608.5077 |  |  | 119181.0552 | 84592.4791 |  |  | 118832.7232
[8 empty] | 550.9088 2: 98672.2923; 550.9088 6: 96765.0356 |  |  |  | 96431.9726 |  |  |  | 94640.3007 | [5 empty] | 99657.99 |  |  |  | 97739.0024 | [5 empty] | 93215.9101 |  |  |  | 91920.1893 | [5 empty] | 92564.5276 |  |  |  | 91137.0251

## HVAC Large Office Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Large Office | [5 empty] | US National |  | Large Office
[6 empty] | CAV_BAS Preheat Coil |  |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW | Find Row
|  |  | YES |  |  | VAV_BOT WITH REHEAT Preheat Coil |  | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
[6 empty] | VAV_MID WITH REHEAT Preheat Coil | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[6 empty] | VAV_MID WITH REHEAT Preheat Coil | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 2 | 3A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 3 | 3B | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 4 | 4A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 5 | 5A | Base Code | 2016 |  |  | Target Code | 2019 |  |  |  | Z1 v Z2 |  |  |  |  | First cost difference |  | 2016 | vs | 2019
Costs row marked x, other rows not marked | [7 empty] | Base Code | Target Code | [8 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [9 empty] | First Only |  |  |  |  | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameter | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total |  | 2013 | 2016 |  | 3dT | 5dT | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
| HVAC System - General load change |  | lookup cost based on supply airflow, cfm
x |  | VAV_AHU |  | VAV_BOT | VAVCHW | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18963.976 | 18010.48 | 46664.2028 | 0 | 15 | 57477.424 | 45577.7027 | 0 | 15 | 55940.4393 | 19387.752 | 18413.0672 | 47147.0917 | 0 | 15 | 58160.5283 | 46036.4472 | 0 | 15 | 56589.3884 | 22036.352 | 20955.7232 | 52614.8244 | 0 | 15 | 64991.8231 | 50083.4902 | 0 | 15 | 61890.3901 | 19620.8288 | 18688.5216 | 47412.6806 | 0 | 15 | 58536.2356 | 46350.325 | 0 | 15 | 57033.4062 | 19790.3392 | 18858.032 | 47605.8362 | 0 | 15 | 58809.4774 | 46543.4805 | 0 | 15 | 57306.6479 | [6 empty] | -1086.5001 | -1110.6446 | -2531.3342 | -1062.3557 | -1062.3557
x |  | Multiplier for MID systems: | 10 | VAV_MID (Asjusted for floor multiplier from below) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] |  |  |  | 449789.2039 | 0 | 15 | 550933.8994 | 439407.0918 | 0 | 15 | 536247.1568 |  |  | 455245.8489 | 0 | 15 | 558652.978 | 444574.0034 | 0 | 15 | 543556.3729 |  |  | 489419.0807 | 0 | 15 | 604917.0461 | 472026.2395 | 0 | 15 | 582390.8527 |  |  | 459060.6715 | 0 | 15 | 564049.5021 | 448968.2927 | 0 | 15 | 549772.6221 |  |  | 459760.8605 | 0 | 15 | 565040.0033 | 449499.4706 | 0 | 15 | 550524.0368 |  | -5456.645 | -15838.7571 |  |  |  | -10382.1122 | -10671.8455 | -17392.8412 | -10092.3788 | -10261.3899
|  | VAV_AHU |  | VAV_MID | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 17484.9978 | 16573.8794 | 44978.9204 | 0 | 15 | 55093.3899 | 43940.7092 | 0 | 15 | 53624.7157 | 17963.8647 | 17027.3197 | 45524.5849 | 0 | 15 | 55865.2978 | 44457.4003 | 0 | 15 | 54355.6373 | 20468.3808 | 19436.4863 | 48941.9081 | 0 | 15 | 60491.7046 | 47202.6239 | 0 | 15 | 58239.0853 | 18298.6477 | 17412.9559 | 45906.0672 | 0 | 15 | 56404.9502 | 44896.8293 | 0 | 15 | 54977.2622 | 18360.0952 | 17459.5712 | 45976.086 | 0 | 15 | 56504.0003 | 44949.9471 | 0 | 15 | 55052.4037 |  | -545.6645 | -1583.8757
x |  | VAV_AHU |  | VAV_TOP | VAVCHW | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18497.8224 | 17650.2704 | 46133.025 | 0 | 15 | 56726.0092 | 45167.2471 | 0 | 15 | 55359.8006 | 18963.976 | 18137.6128 | 46664.2028 | 0 | 15 | 57477.424 | 45722.5694 | 0 | 15 | 56145.3706 | 22142.296 | 21209.9888 | 52862.9944 | 0 | 15 | 65295.8851 | 50679.0982 | 0 | 15 | 62620.139 | 18985.1648 | 18201.1792 | 46688.3472 | 0 | 15 | 57511.5792 | 45795.0027 | 0 | 15 | 56247.8362 | 19133.4864 | 18349.5008 | 46857.3584 | 0 | 15 | 57750.6657 | 45964.0138 | 0 | 15 | 56486.9227 |  | -531.1778 | -1496.9557 |  |  |  | -965.7779 | -941.6334 | -2183.8962 | -893.3445 | -893.3445
0 | 90.1-10au | VAV_AHU | If PH coil = NO | VAV_BOT | VAVCHW | VAV_BOT WITH REHEAT Preheat Coil | US_LO_VAV_BOT WITH REHEAT Preheat Coil | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A |  | 0 | #N/A
0 |  | VAV_AHU | increase | VAV_MID | VAVCHW | VAV_MID WITH REHEAT Preheat Coil | US_LO_VAV_MID WITH REHEAT Preheat Coil | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 |  | 0 | 0
|  | VAV_AHU | duct cost by | VAV_MID | VAVCHW | CAV_BAS Preheat Coil | US_LO_CAV_BAS Preheat Coil | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | NO | 0 | 0 | 15 | 0 | 1234.6628 | 0 | 15 | 1511.8747 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 |  | 0 | 0
0 |  | VAV_AHU | 2.75% | VAV_TOP | VAVCHW | VAV_MID WITH REHEAT Preheat Coil | US_LO_VAV_MID WITH REHEAT Preheat Coil | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | NO | 0 | 0 | 15 | 0 | 1259.3626 | 0 | 15 | 1546.8155 | N/A | -999 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 |  | 0 | 0
2016 |  | CAV_AHU | lookup cost based on cooling tons | [55 empty] | 0 | 0
x |  | CAV_AHU |  | CAV_BAS | CAVCHW | CAV_BAS Supply Flow Rate [cfm] | US_LO_CAV_BAS Supply Flow Rate [cfm] | 12014.0496 | 11166.4976 | 34391.5402 | 0 | 15 | 41859.2165 | 33076.5193 | 0 | 15 | 40224.6583 | 11886.9168 | 10996.9872 | 34191.7137 | 0 | 15 | 41611.0932 | 32814.1207 | 0 | 15 | 39898.4384 | 13391.3216 | 12395.448 | 36820.3149 | 0 | 15 | 44848.7683 | 35064.124 | 0 | 15 | 42687.0924 | 11611.4624 | 10742.7216 | 33765.3159 | 0 | 15 | 41080.9858 | 32420.5226 | 0 | 15 | 39409.1084 | 11780.9728 | 10891.0432 | 34027.7145 | 0 | 15 | 41407.2057 | 32650.1215 | 0 | 15 | 39694.5509 |  | 199.8265 | -1115.1944 |  |  |  | -1315.0209 | -1377.5931 | -1756.1909 | -1344.7932 | -1377.5931
[59 empty] | 0 | 0
x | HVAC System - General load change | Air Distribution material y = 0.7091x + 503192 labor y = 3.2521x + 1.604E+06 | curve fit from Solarc cost calculations - described in HVAC Costs Comp. Material, labor, and project cost adjustments applied in this worksheet. | All systems |  | Sum of Supply Airflow (cfm) values for all 4 systems from above values |  | 136900.837 | 129696.645 | 5740106.8326 | 0 | 30 | 9465905.8232 | 5677204.904 | 0 | 30 | 9360688.7312 | 140057.9682 | 132684.2658 | 5767672.6778 | 0 | 30 | 9512015.6665 | 5703290.7038 | 0 | 30 | 9404322.8782 | 159911.8738 | 151743.5914 | 5941022.993 | 0 | 30 | 9801981.5937 | 5869703.3062 | 0 | 30 | 9682683.979 | 141710.6946 | 134697.2018 | 5782103.1203 | 0 | 30 | 9536153.7053 | 5720866.2427 | 0 | 30 | 9433721.7716 | 142505.2746 | 135396.4322 | 5789040.833 | 0 | 30 | 9547758.5316 | 5726971.4299 | 0 | 30 | 9443934.0187 |  | -27565.8452 | -90467.7739 |  |  |  | -62901.9286 | -64381.974 | -71319.6867 | -61236.8776 | -62069.4031
check differential of above | [8 empty] | -5.262% | -1.096% | -62901.9286 | [7 empty] | -5.265% | -1.116% | -64381.974 | [7 empty] | -5.108% | -1.2% | -71319.6867 | [7 empty] | -4.949% | -1.059% | -61236.8776 | [7 empty] | -4.988% | -1.072% | -62069.4031 | [7 empty] | 0.00020424 | 0.011163
| 90.1-2016ap SAT reset only 0A, 1A, 2A, 3A MZ systems only <3000 cfm design OA is exempt; <10,000 for 2A | Material cost = 4E-07x2 + 0.0307x + 1618 Labor hours = 0.0054x + 3.6055 | lookup cost based on supply airflow, cfm new for 2019, thus base code = 0 costs
x |  | SAT_reset_16ap |  | VAV_BOT | VAVCHW | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18963.976 | 18010.48 | 0 | 0 |  | 0 | 3791.1906 | 0 | 20 | 4325.4516 | 19387.752 | 18413.0672 | 0 | 0 |  | 0 | 3824.4522 | 0 | 20 | 4365.3833 | 22036.352 | 20955.7232 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19620.8288 | 18688.5216 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19790.3392 | 18858.032 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | [6 empty] | 3791.1906 | 3824.4522 | 0 | 0 | 0
x |  | Multiplier for MID systems: | 10 | VAV_MID (Asjusted for floor multiplier from below) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] |  |  |  | 0 | 0 |  | 0 | 36741.3191 | 0 | 20 | 41847.5459 |  |  | 0 | 0 |  | 0 | 37108.0414 | 0 | 20 | 42288.6035 |  |  | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 |  |  | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | [6 empty] | 36741.3191 | 37108.0414 | 0 | 0 | 0
|  | SAT_reset_16ap |  | VAV_MID | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 17484.9978 | 16573.8794 | 0 | 0 |  | 0 | 3674.1319 | 0 | 20 | 4184.7546 | 17963.8647 | 17027.3197 | 0 | 0 |  | 0 | 3710.8041 | 0 | 20 | 4228.8604 | 20468.3808 | 19436.4863 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 18298.6477 | 17412.9559 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 18360.0952 | 17459.5712 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
x |  | SAT_reset_16ap |  | VAV_TOP | VAVCHW | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18497.8224 | 17650.2704 | 0 | 0 |  | 0 | 3761.6 | 0 | 20 | 4289.9101 | 18963.976 | 18137.6128 | 0 | 0 |  | 0 | 3801.6726 | 0 | 20 | 4338.0378 | 22142.296 | 21209.9888 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 18985.1648 | 18201.1792 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 19133.4864 | 18349.5008 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | [6 empty] | 3761.6 | 3801.6726 | 0 | 0 | 0
| 90.1-07bh | Supply_Air_Temp_Reset | apply cost if "Yes" Add test *IF(Base_Code = 2009,0,1) | single line lookup | 2010 ONLY | Only one parameter - same value for all VAV systems. Note that HVAC Data parameter values are [Yes, No] | [52 empty] | 0 | 0
Not in 2016 |  | Supply_Air_Temp_Reset |  | VAV_BOT | VAVCHW | Supply Air Temp. Reset Flag | US_LO_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  | 1 | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 |  | 0 | 0
Not in 2016 |  | VAV_AHU |  | VAV_MID (estimate based on 5 systems, not 1 as modeled, costs multiplied by 5. Modeled system is too large for real application. Row included to screen out Out of Range * 5 which gives a Value error) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | [7 empty] | 0 | 0 | 0 | 0 | [6 empty] | 93670 | 0 | 20 | 93670 | [6 empty] | 468350 | 0 | 20 | 93670 | [6 empty] | 468350 | 0 | 20 | 93670 | [6 empty] | 468350 | 0 | 20 | 93670 |  | 0 | 0
|  | Supply_Air_Temp_Reset |  | VAV_MID | VAVCHW | Supply Air Temp. Reset Flag | US_LO_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 93670 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 93670 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 93670 | 0 | 20 | 18734 |  | 0 | 0
Not in 2016 |  | Supply_Air_Temp_Reset |  | VAV_TOP | VAVCHW | Supply Air Temp. Reset Flag | US_LO_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 |  | 0 | 0
Not in 2016 |  | Supply_Air_Temp_Reset | interior zone added HVAC duct etc. for large office only | VAV_MID and VAV_TOP (cost is for all five systems, and VAV_Top interior areas - see description) | VAVCHW | Supply Air Temp. Reset Flag | US_LO_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 |  | 20 | 0 | No | Yes |  |  |  |  | 18734 |  | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 |  | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 |  | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 |  | 20 | 18734 |  | 0 | 0
| 90.1-13 i requires ventilation optimization without exception for DCV | Vent_Optimize | apply cost if "Yes", cost value times number of perimeter zones | NOTE: EXTRACTING THE COSTS IN THE SECOND LINE, AND APPLYING THE YES/NO CONDITION IN THE FIRST LINE. Single line lookup range. |  | Note that HVAC Data parameter values are [Yes, No] | [52 empty] | 0 | 0
|  |  |  | VAV_BOT | VAVCHW | Ventilation Reset Flag add_ck_vav_bot | US_LO_Ventilation Reset Flag add_ck_vav_bot | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Vent_Optimize |  |  |  | Number of perimeter zones (hard coded - doesn't change) |  | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 |  | 0 | 0
|  |  |  | VAV_MID (cost is for top floor and all 10 Mid floors, no multiplier of 5 needed) | VAVCHW | Ventilation Reset Flag add_ck_vav_mid | US_LO_Ventilation Reset Flag add_ck_vav_mid | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Vent_Optimize |  |  |  | Number of perimeter zones (hard coded - doesn't change) |  | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 | 120 | 120 | 14741.16 | 0 | 0 | 0 | 14741.16 | 0 | 0 | 0 |  | 0 | 0
|  |  |  | VAV_TOP | VAVCHW | Ventilation Reset Flag add_ck_vav_top | US_LO_Ventilation Reset Flag add_ck_vav_top | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Vent_Optimize |  |  |  | Number of perimeter zones (hard coded - doesn't change) |  | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 | 12 | 12 | 1474.116 | 0 | 0 | 0 | 1474.116 | 0 | 0 | 0 |  | 0 | 0
| 90.1-07cb | Outdoor_Air_Dampers | Use the upper rows for gravity dampers if value is "gravity", cost is 0. If "motorized, cost is difference between motorized and gravity. If system has an economizer, then there is no added cost for a motorized damper vs. a gravity damper and value is set to $0, | [55 empty] | 0 | 0
Not in 2016 |  | Outdoor_Air_Dampers | system cost | VAV_BOT | VAVCHW | VAV_bot WITH REHEAT OA Damper [gravity, motorized] | US_LO_VAV_bot WITH REHEAT OA Damper [gravity, motorized] | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_BOT WITH REHEAT OA Rate [cfm] | US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 |  | 0 | -109.4648
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | VAV_BOT WITH REHEAT OA Rate [cfm] | US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 |  | 0 | 22.8803
Not in 2016 |  |  |  | VAV_MID (estimate based on 5 systems, not 1 as modeled, costs multiplied by 5. Modeled system is too large for real application. Row included to screen out Out of Range * 5 which gives a Value error) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] |  |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers | system cost | VAV_MID | VAVCHW | VAV_mid WITH REHEAT OA Damper [gravity, motorized] | US_LO_VAV_mid WITH REHEAT OA Damper [gravity, motorized] | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_MID WITH REHEAT OA Rate [cfm] | US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | 10755.5875 | 8604.3479 | 1455.297 | 197.4878 | 20 | 1661.9585 | 1334.9735 | 171.0438 | 20 | 1673.2729 | 10755.5875 | 8604.3479 | 1455.297 | 197.4878 | 20 | 1661.9585 | 1334.9735 | 171.0438 | 20 | 1673.2729 | 10755.5875 | 8604.3479 | 1455.297 | 197.4878 | 20 | 1661.9585 | 1334.9735 | 171.0438 | 20 | 1673.2729 | 10755.5875 | 8604.3479 | 1455.297 | 197.4878 | 20 | 1661.9585 | 1334.9735 | 171.0438 | 20 | 1673.2729 | 10755.5875 | 8604.3479 | 1455.297 | 197.4878 | 20 | 1661.9585 | 1334.9735 | 171.0438 | 20 | 1673.2729 |  | 0 | -120.3235
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | VAV_MID WITH REHEAT OA Rate [cfm] | US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | 10755.5875 | 8604.3479 | 1809.1081 | 197.4878 | 20 | 1968.7249 | 1814.1181 | 171.0438 | 20 | 2177.4677 | 10755.5875 | 8604.3479 | 1809.1081 | 197.4878 | 20 | 1968.7249 | 1814.1181 | 171.0438 | 20 | 2177.4677 | 10755.5875 | 8604.3479 | 1809.1081 | 197.4878 | 20 | 1968.7249 | 1814.1181 | 171.0438 | 20 | 2177.4677 | 10755.5875 | 8604.3479 | 1809.1081 | 197.4878 | 20 | 1968.7249 | 1814.1181 | 171.0438 | 20 | 2177.4677 | 10755.5875 | 8604.3479 | 1809.1081 | 197.4878 | 20 | 1968.7249 | 1814.1181 | 171.0438 | 20 | 2177.4677 |  | 0 | 5.0101
Not in 2016 |  | Outdoor_Air_Dampers | system cost | VAV_TOP | VAVCHW | VAV_top WITH REHEAT OA Damper [gravity, motorized] | US_LO_VAV_top WITH REHEAT OA Damper [gravity, motorized] | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_TOP WITH REHEAT OA Rate [cfm] | US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 | 5377.8022 | 4302.174 | 838.0588 | 142.1373 | 20 | 965.4366 | 728.594 | 137.3057 | 20 | 893.1455 |  | 0 | -109.4648
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | VAV_TOP WITH REHEAT OA Rate [cfm] | US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 | 5377.8022 | 4302.174 | 1285.6984 | 142.1373 | 20 | 1410.097 | 1308.5788 | 137.3057 | 20 | 1563.041 |  | 0 | 22.8803
Not in 2016 |  | Outdoor_Air_Dampers | system cost | CAV_BAS | CAVCHW | CAV_bas OA Damper [gravity, motorized] | US_LO_CAV_bas OA Damper [gravity, motorized] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | CAV_BAS OA Rate [cfm] | US_LO_CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 451.6944 | 116.312 | 20 | 489.7845 | 489.7922 | 116.312 | 20 | 585.0822 | 2542.8255 | 2542.8255 | 451.6944 | 116.312 | 20 | 489.7845 | 489.7922 | 116.312 | 20 | 585.0822 | 2542.8255 | 2542.8255 | 451.6944 | 116.312 | 20 | 489.7845 | 489.7922 | 116.312 | 20 | 585.0822 | 2542.8255 | 2542.8255 | 451.6944 | 116.312 | 20 | 489.7845 | 489.7922 | 116.312 | 20 | 585.0822 | 2542.8255 | 2542.8255 | 451.6944 | 116.312 | 20 | 489.7845 | 489.7922 | 116.312 | 20 | 585.0822 |  | 0 | 38.0978
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | CAV_BAS OA Rate [cfm] | US_LO_CAV_BAS OA Rate [cfm] | 2542.8255 | 2542.8255 | 939.7233 | 116.312 | 20 | 1012.0104 | 1059.9262 | 116.312 | 20 | 1256.535 | 2542.8255 | 2542.8255 | 939.7233 | 116.312 | 20 | 1012.0104 | 1059.9262 | 116.312 | 20 | 1256.535 | 2542.8255 | 2542.8255 | 939.7233 | 116.312 | 20 | 1012.0104 | 1059.9262 | 116.312 | 20 | 1256.535 | 2542.8255 | 2542.8255 | 939.7233 | 116.312 | 20 | 1012.0104 | 1059.9262 | 116.312 | 20 | 1256.535 | 2542.8255 | 2542.8255 | 939.7233 | 116.312 | 20 | 1012.0104 | 1059.9262 | 116.312 | 20 | 1256.535 |  | 0 | 120.203
Not in 2016 |  | Outdoor_Air_Dampers | system cost - Added this, copied and pasted, verify | AirLoop DataCenter Basement | WSHP | AirLoop DataCenter Basement OA Damper [gravity, motorized] | US_LO_AirLoop DataCenter Basement OA Damper [gravity, motorized] | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | #N/A | #N/A | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | DATACENTER BASEMENT OA Rate [cfm] | US_LO_DATACENTER BASEMENT OA Rate [cfm] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | Outdoor_Air_Dampers_Motorized | item cost |  |  | DATACENTER BASEMENT OA Rate [cfm] | US_LO_DATACENTER BASEMENT OA Rate [cfm] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
| 90.1-07cy | AHU_Economizer | If any value other than "no" lookup cost based on supply air cfm | NOTE: I'M EXTRACTING THE COSTS IN THE SECOND LINE, AND APPLYING THE YES/NO CONDITION IN THE FIRST LINE. |  | Note that HVAC Data parameter range is [No, DifferentialEnthalpy] | [52 empty] | 0 | 0
Not in 2016 | 90.1-07cy | AHU_Economizer |  | VAV_BOT | VAVCHW | VAV_bot WITH REHEAT (economizer) | US_LO_VAV_bot WITH REHEAT (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | AHU_Economizer |  |  |  | VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_BOT WITH REHEAT Supply Flow Rate [cfm] | 18963.976 | 18010.48 | 21103.182 | 347.4145 | 15 | 23520.6868 | 20042.1282 | 338.0441 | 15 | 22338.0825 | 19387.752 | 18413.0672 | 21574.7615 | 351.5791 | 15 | 24046.2888 | 20490.1287 | 342.0005 | 15 | 22837.4043 | 22036.352 | 20955.7232 | 24522.1333 | 377.6081 | 15 | 27331.3009 | 23319.6056 | 366.9883 | 15 | 25991.0159 | 19620.8288 | 18688.5216 | 21834.1302 | 353.8697 | 15 | 24335.3698 | 20796.6553 | 344.7075 | 15 | 23179.0456 | 19790.3392 | 18858.032 | 22022.762 | 355.5355 | 15 | 24545.6106 | 20985.2871 | 346.3734 | 15 | 23389.2863 |  | -471.5795 | -1532.6333
Not in 2016 |  |  |  | VAV_MID (estimate based on 5 systems, not 1 as modeled, costs multiplied by 5. Modeled system is too large for real application. Row included to screen out Out of Range * 5 which gives a Value error) | VAVCHW |  |  |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  | #VALUE! | #VALUE!
Not in 2016 |  | AHU_Economizer |  | VAV_MID | VAVCHW | VAV_mid WITH REHEAT (economizer) | US_LO_VAV_mid WITH REHEAT (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | AHU_Economizer |  |  |  | VAV_MID WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_MID WITH REHEAT Supply Flow Rate [cfm] | 34969.9956 | 33147.7588 | 38914.7392 | 504.7127 | 15 | 43372.6721 | 36886.9474 | 486.8048 | 15 | 41112.5838 | 35927.7293 | 34054.6394 | 39980.5088 | 514.1248 | 15 | 44560.5325 | 37896.1275 | 495.7171 | 15 | 42237.3719 | 40936.7617 | 38872.9725 | 45554.5783 | 563.3507 | 15 | 50773.1474 | 43257.9863 | 543.069 | 15 | 48213.466 | 36597.2954 | 34825.9117 | 40725.6044 | 520.7049 | 15 | 45390.9835 | 38754.4022 | 503.2967 | 15 | 43193.9674 | 36720.1905 | 34919.1425 | 40862.3625 | 521.9126 | 15 | 45543.4081 | 38858.1496 | 504.213 | 15 | 43309.5999 |  | -1065.7696 | -3093.5614
Not in 2016 |  | AHU_Economizer |  | VAV_TOP | VAVCHW | VAV_top WITH REHEAT (economizer) | US_LO_VAV_top WITH REHEAT (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | AHU_Economizer |  |  |  | VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | US_LO_VAV_TOP WITH REHEAT Supply Flow Rate [cfm] | 18497.8224 | 17650.2704 | 20584.4446 | 342.8334 | 15 | 22942.5247 | 19641.2856 | 334.5041 | 15 | 21891.3208 | 18963.976 | 18137.6128 | 21103.182 | 347.4145 | 15 | 23520.6868 | 20183.602 | 339.2935 | 15 | 22495.763 | 22142.296 | 21209.9888 | 24640.0281 | 378.6493 | 15 | 27462.7014 | 23602.5533 | 369.4871 | 15 | 26306.3771 | 18985.1648 | 18201.1792 | 21126.761 | 347.6227 | 15 | 23546.9669 | 20254.3389 | 339.9182 | 15 | 22574.6033 | 19133.4864 | 18349.5008 | 21291.8138 | 349.0804 | 15 | 23730.9276 | 20419.3917 | 341.3758 | 15 | 22758.564 |  | -518.7374 | -1461.8964
Not in 2016 |  | AHU_Economizer |  | CAV_BAS | CAVCHW | CAV_bas (economizer) | US_LO_CAV_bas (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
|  | AHU_Economizer |  |  |  | CAV_BAS Supply Flow Rate [cfm] | US_LO_CAV_BAS Supply Flow Rate [cfm] | 12014.0496 | 11166.4976 | 13369.2784 | 279.1145 | 15 | 14900.815 | 12426.1195 | 270.7853 | 15 | 13849.6111 | 11886.9168 | 10996.9872 | 13227.8046 | 277.8651 | 15 | 14743.1344 | 12237.4877 | 269.1194 | 15 | 13639.3703 | 13391.3216 | 12395.448 | 14901.9118 | 292.6496 | 15 | 16609.0213 | 13793.7 | 282.8627 | 15 | 15373.8567 | 11611.4624 | 10742.7216 | 12921.2779 | 275.1581 | 15 | 14401.4932 | 11954.54 | 266.6206 | 15 | 13324.0092 | 11780.9728 | 10891.0432 | 13109.9097 | 276.824 | 15 | 14611.7339 | 12119.5928 | 268.0782 | 15 | 13507.9699 |  | 141.4738 | -801.6851
Not in 2019 | 90.1-13 i | AHU_Economizer |  | AirLoop DataCenter Basement | DX | AirLoop DataCenter Basement (economizer) | US_LO_AirLoop DataCenter Basement (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
| Lowers computer room economizer threshold | AHU_Economizer | Includes both load adjustments and requirement changes |  |  | DATACENTER BASEMENT Fan SA [cfm] | US_LO_DATACENTER BASEMENT Fan SA [cfm] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A
| ERV load change from OA reduction from 90.1-16 au, cm, & co | Energy_Recovery_AHU | if "yes" lookup up based on outside airflow, cfm. |  | 2010 ONLY | Note that HVAC Data ERV Flag parameter values are [Yes, No] | [52 empty] | 0 | 0
x |  | Energy_Recovery_AHU |  | VAV_BOT | VAVCHW | VAV_bot_WITH_REHEAT ERV Flag | US_LO_VAV_bot_WITH_REHEAT ERV Flag | Yes | Yes | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | Yes | Yes | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | Yes | Yes | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 |  | 0 | -6914.6614 |  |  |  | -6914.6614 | -6914.6614 | 0 | -6914.6614 | -6914.6614
|  | Energy_Recovery_AHU |  |  |  | VAV_BOT WITH REHEAT OA Rate [cfm] | US_LO_VAV_BOT WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 |  | 0 | -6914.6614
x |  | MID SYS multiplier: | 10 | VAV_MID (estimate based on 10 systems, not 1 as modeled, costs multiplied by 10. Modeled system is too large for real application. Parameter adjusted by multiplier) | VAVCHW | VAV_MID WITH REHEAT Supply Flow Rate [cfm] |  |  |  | 361457.4144 | 2550.825 | 15 | 413460.6854 | 292311.3449 | 2550.825 | 15 | 336290.884 |  |  | 361457.4144 | 2550.825 | 15 | 413460.6854 | 292311.3449 | 2550.825 | 15 | 336290.884 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 361457.4144 | 2550.825 | 15 | 413460.6854 | 292311.3449 | 2550.825 | 15 | 336290.884 |  |  | 361457.4144 | 2550.825 | 15 | 413460.6854 | 292311.3449 | 2550.825 | 15 | 336290.884 |  | 0 | -69146.0694 |  |  |  | -69146.0694 | -69146.0694 | 0 | -69146.0694 | -69146.0694
|  | Energy_Recovery_AHU |  | VAV_MID | VAVCHW | VAV_mid_WITH_REHEAT ERV Flag | US_LO_VAV_mid_WITH_REHEAT ERV Flag | Yes | Yes | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 | Yes | Yes | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 | Yes | Yes | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 |  | 0 | -6914.6069
|  | Energy_Recovery_AHU |  |  |  | VAV_MID WITH REHEAT OA Rate [cfm] | US_LO_VAV_MID WITH REHEAT OA Rate [cfm] | 5377.7937 | 4302.174 | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.7937 | 4302.174 | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.7937 | 4302.174 | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.7937 | 4302.174 | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.7937 | 4302.174 | 36145.7414 | 255.0825 | 15 | 41346.0685 | 29231.1345 | 255.0825 | 15 | 33629.0884 |  | 0 | -6914.6069
x |  | Energy_Recovery_AHU |  | VAV_TOP | VAVCHW | VAV_top_WITH_REHEAT ERV Flag | US_LO_VAV_top_WITH_REHEAT ERV Flag | Yes | Yes | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | Yes | Yes | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | Yes | Yes | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 |  | 0 | -6914.6614 |  |  |  | -6914.6614 | -6914.6614 | 0 | -6914.6614 | -6914.6614
|  | Energy_Recovery_AHU |  |  |  | VAV_TOP WITH REHEAT OA Rate [cfm] | US_LO_VAV_TOP WITH REHEAT OA Rate [cfm] | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 | 5377.8022 | 4302.174 | 36145.7959 | 255.0825 | 15 | 41346.1293 | 29231.1345 | 255.0825 | 15 | 33629.0884 |  | 0 | -6914.6614
| HVAC Plant - General load change |  | lookup cost based on cooling tons | [55 empty] | 0 | 0
x |  | Cent_WC_Chiller_Capacity |  | Chiller 1 | centrifugal, water-cooled | COOLSYS1 CHILLER1 Capacity [ton] | US_LO_COOLSYS1 CHILLER1 Capacity [ton] | 438.8299 | 391.2284 | 241634.0952 | 0 | 23 | 288933.2106 | 226022.7379 | 0 | 23 | 271172.1012 | 406.1299 | 365.9173 | 228866.4615 | 0 | 23 | 274547.3786 | 224723.3665 | 0 | 23 | 269214.2212 | 337.4605 | 311.9875 | 223262.5131 | 0 | 23 | 267013.022 | 221954.8318 | 0 | 23 | 265042.6208 | 402.5817 | 336.3811 | 227481.0362 | 0 | 23 | 272986.3614 | 223207.0993 | 0 | 23 | 266929.5249 | 371.5931 | 339.1105 | 225014.7401 | 0 | 23 | 269653.2602 | 223347.2171 | 0 | 23 | 267140.6531 |  | 12767.6337 | -2843.7236 |  |  |  | -15611.3572 | -4143.095 | -1307.6813 | -4273.9369 | -1667.523
x |  | Cent_WC_Chiller_Capacity |  | Chiller 2 | centrifugal, water-cooled | COOLSYS1 CHILLER2 Capacity [ton] | US_LO_COOLSYS1 CHILLER2 Capacity [ton] | 438.8299 | 391.2284 | 241634.0952 | 0 | 23 | 288933.2106 | 226022.7379 | 0 | 23 | 271172.1012 | 406.1299 | 365.9173 | 228866.4615 | 0 | 23 | 274547.3786 | 224723.3665 | 0 | 23 | 269214.2212 | 337.4605 | 311.9875 | 223262.5131 | 0 | 23 | 267013.022 | 221954.8318 | 0 | 23 | 265042.6208 | 402.5817 | 336.3811 | 227481.0362 | 0 | 23 | 272986.3614 | 223207.0993 | 0 | 23 | 266929.5249 | 371.5931 | 339.1105 | 225014.7401 | 0 | 23 | 269653.2602 | 223347.2171 | 0 | 23 | 267140.6531 |  | 12767.6337 | -2843.7236 |  |  |  | -15611.3572 | -4143.095 | -1307.6813 | -4273.9369 | -1667.523
| General load change | Cooling_Tower_Capacity | lookup based on cooling tons | [55 empty] | 0 | 0
x |  | Cooling_Tower_Capacity |  | Cooling Tower |  | TOWERWATERSYS COOLTOWER 1 Capacity [ton] | US_LO_TOWERWATERSYS COOLTOWER 1 Capacity [ton] | 416.5333 | 371.3501 | 107683.5753 | 0 | 20 | 125022.4045 | 93732.2222 | 0 | 20 | 108367.4932 | 385.4879 | 347.3277 | 98097.5932 | 0 | 20 | 113578.8062 | 87117.0013 | 0 | 20 | 100499.5513 | 320.5792 | 296.3791 | 82073.9642 | 0 | 20 | 94596.3385 | 77511.3768 | 0 | 20 | 89255.5243 | 382.1274 | 319.2884 | 97059.9561 | 0 | 20 | 112340.091 | 81830.589 | 0 | 20 | 94311.4515 | 352.7198 | 321.8836 | 88133.6185 | 0 | 20 | 101689.5698 | 82319.8832 | 0 | 20 | 94884.2031 |  | 9585.9821 | -4365.3711 |  |  |  | -13951.3531 | -10980.5919 | -4562.5874 | -15229.3672 | -5813.7354
x |  | Cooling_Tower_Capacity |  | Cooling Tower |  | TOWERWATERSYS COOLTOWER 2 Capacity [ton] | US_LO_TOWERWATERSYS COOLTOWER 2 Capacity [ton] | 416.5333 | 371.3501 | 107683.5753 | 0 | 20 | 125022.4045 | 93732.2222 | 0 | 20 | 108367.4932 | 385.4879 | 347.3277 | 98097.5932 | 0 | 20 | 113578.8062 | 87117.0013 | 0 | 20 | 100499.5513 | 320.5792 | 296.3791 | 82073.9642 | 0 | 20 | 94596.3385 | 77511.3768 | 0 | 20 | 89255.5243 | 382.1274 | 319.2884 | 97059.9561 | 0 | 20 | 112340.091 | 81830.589 | 0 | 20 | 94311.4515 | 352.7198 | 321.8836 | 88133.6185 | 0 | 20 | 101689.5698 | 82319.8832 | 0 | 20 | 94884.2031 |  | 9585.9821 | -4365.3711 |  |  |  | -13951.3531 | -10980.5919 | -4562.5874 | -15229.3672 | -5813.7354
| General Load impact | Boiler_Capacity | lookup cost based on boiler millions of Btu/h | [55 empty] | 0 | 0
x |  | Boiler_Capacity |  | Boiler |  | HEATSYS1 BOILER Capacity [MMBTU/h] | US_LO_HEATSYS1 BOILER Capacity [MMBTU/h] | 4.338 | 4.0326 | 92997.1871 | 0 | 35 | 121421.6116 | 86808.0028 | 0 | 35 | 113466.3067 | 5.5056 | 5.0972 | 116661.2624 | 0 | 35 | 151838.3713 | 108384.9894 | 0 | 35 | 141200.4146 | 5.0875 | 4.7251 | 108188.7005 | 0 | 35 | 140948.1135 | 100843.0383 | 0 | 35 | 131506.323 | 5.9876 | 5.5199 | 126430.7231 | 0 | 35 | 164395.6055 | 116952.215 | 0 | 35 | 152212.3489 | 6.4105 | 5.8555 | 135000.5419 | 0 | 35 | 175410.873 | 123752.8037 | 0 | 35 | 160953.526 |  | -23664.0753 | -29853.2597 |  |  |  | -6189.1843 | -8276.273 | -7345.6622 | -9478.5081 | -11247.7382
| General Load impact and 90.1-16 an - clean water pump | Pump_Flow | lookup based on flow, GPM | [55 empty] | 0 | 0
x |  | Pump_FlPri | Test for N/A | Pump | Primary CHW | COOLSYS1 PUMP Flow Rate [gal/min] | US_LO_COOLSYS1 PUMP Flow Rate [gal/min] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
x |  | Pump_FlPri | Test for N/A | Pump | Primary CHW | COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | US_LO_COOLSYS1 CHILLER1 PUMP Flow Rate [gal/min] | 688.9739 | 613.9337 | 37296.2156 | 0 | 20 | 48333.457 | 36741.1976 | 0 | 20 | 47564.8721 | 639.96 | 573.7627 | 36379.0618 | 0 | 20 | 47221.3445 | 35968.3487 | 0 | 20 | 46630.1218 | 527.5495 | 487.632 | 34275.6259 | 0 | 20 | 44670.7829 | 34311.2856 | 0 | 20 | 44625.9262 | 634.3299 | 526.9345 | 36273.7121 | 0 | 20 | 47093.6006 | 35067.4235 | 0 | 20 | 45540.4649 | 585.2605 | 534.0085 | 35355.5202 | 0 | 20 | 45980.2294 | 35203.5198 | 0 | 20 | 45705.0716 |  | 917.1538 | 362.1358 |  |  |  | -555.018 | -410.7131 | 35.6597 | -1206.2885 | -152.0003
x |  | Pump_FlPri | Test for N/A | Pump | Primary CHW | COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | US_LO_COOLSYS1 CHILLER2 PUMP Flow Rate [gal/min] | 688.9739 | 613.9337 | 37296.2156 | 0 | 20 | 48333.457 | 36741.1976 | 0 | 20 | 47564.8721 | 639.96 | 573.7627 | 36379.0618 | 0 | 20 | 47221.3445 | 35968.3487 | 0 | 20 | 46630.1218 | 527.5495 | 487.632 | 34275.6259 | 0 | 20 | 44670.7829 | 34311.2856 | 0 | 20 | 44625.9262 | 634.3299 | 526.9345 | 36273.7121 | 0 | 20 | 47093.6006 | 35067.4235 | 0 | 20 | 45540.4649 | 585.2605 | 534.0085 | 35355.5202 | 0 | 20 | 45980.2294 | 35203.5198 | 0 | 20 | 45705.0716 |  | 917.1538 | 362.1358 |  |  |  | -555.018 | -410.7131 | 35.6597 | -1206.2885 | -152.0003
x |  | Pump_Flow |  | Pump | Secondary CHW | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | US_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1377.9463 | 1227.8691 | 77442.0208 | 0 | 20 | 96838.7362 | 74504.0639 | 0 | 20 | 93093.2782 | 1279.9215 | 1147.5238 | 74288.2183 | 0 | 20 | 93034.0205 | 71845.4604 | 0 | 20 | 89893.7972 | 1055.1005 | 975.2656 | 67054.9322 | 0 | 20 | 84307.8568 | 66145.4858 | 0 | 20 | 83034.1956 | 1268.6614 | 1053.869 | 73925.942 | 0 | 20 | 92596.9741 | 68746.4487 | 0 | 20 | 86164.3094 | 1170.5194 | 1068.017 | 70768.3658 | 0 | 20 | 88787.7058 | 69214.602 | 0 | 20 | 86727.7058 |  | 3153.8025 | 215.8457 |  |  |  | -2937.9568 | -2442.7579 | -909.4463 | -5179.4934 | -1553.7638
x |  | Pump_Flow |  | Pump | Circulate | PLANT CIRC PUMP Flow Rate [gal/min] | US_LO_PLANT CIRC PUMP Flow Rate [gal/min] | 208.6949 | 207.8072 | 37209.7142 | 0 | 20 | 47643.3358 | 38071.1716 | 0 | 20 | 48578.786 | 209.3162 | 208.4508 | 37247.4885 | 0 | 20 | 47693.3946 | 38111.1678 | 0 | 20 | 48631.5927 | 223.442 | 222.4688 | 38106.2775 | 0 | 20 | 48831.4679 | 38982.4155 | 0 | 20 | 49781.8949 | 207.4443 | 206.6169 | 37133.6836 | 0 | 20 | 47542.5795 | 37997.1884 | 0 | 20 | 48481.1065 | 208.9992 | 208.1591 | 37228.2159 | 0 | 20 | 47667.8544 | 38093.0414 | 0 | 20 | 48607.6606 |  | -37.7744 | 823.683 |  |  |  | 861.4574 | 863.6793 | 876.138 | 863.5048 | 864.8255
x |  | Pump_FlPri |  | Pump | Condenser Water | TOWERWATERSYS PUMP Flow Rate [gal/min] | US_LO_TOWERWATERSYS PUMP Flow Rate [gal/min] | 2420.9784 | 2158.497 | 81290.7856 | 0 | 20 | 102885.6309 | 75306.4829 | 0 | 20 | 95432.8175 | 2240.6017 | 2018.8557 | 75911.3341 | 0 | 20 | 96370.3167 | 71024.335 | 0 | 20 | 90259.5678 | 1861.779 | 1721.1866 | 65194.5985 | 0 | 20 | 83216.6075 | 63119.6247 | 0 | 20 | 80356.649 | 2221.1058 | 1855.7558 | 75329.8996 | 0 | 20 | 95666.1132 | 66655.7564 | 0 | 20 | 84799.1409 | 2050.0808 | 1870.8136 | 70229.3477 | 0 | 20 | 89488.5877 | 67051.4366 | 0 | 20 | 85296.2396 |  | 5379.4514 | -604.8512 |  |  |  | -5984.3027 | -4886.9991 | -2074.9739 | -8674.1432 | -3177.9111
x |  | Pump_Flow |  | Pump | Hot Water | HEATSYS1 PUMP Flow Rate [gal/min] | US_LO_HEATSYS1 PUMP Flow Rate [gal/min] | 890.4236 | 827.7387 | 61756.6929 | 0 | 20 | 77916.1141 | 61263.8618 | 0 | 20 | 77159.4334 | 1130.0948 | 1046.2719 | 69467.7614 | 0 | 20 | 87218.6698 | 68495.064 | 0 | 20 | 85861.782 | 1044.2843 | 969.886 | 66706.9348 | 0 | 20 | 83888.0363 | 65967.4763 | 0 | 20 | 82819.9712 | 1229.0404 | 1133.0413 | 72651.1926 | 0 | 20 | 91059.1292 | 71366.2404 | 0 | 20 | 89317.0827 | 1315.8368 | 1201.9189 | 75443.7388 | 0 | 20 | 94428.0289 | 73645.3806 | 0 | 20 | 92059.9008 |  | -7711.0685 | -8203.8996 | First cost pipe & pump diff |  |  | -492.8311 | -972.6974 | -739.4585 | -1284.9522 | -1798.3582
x | General Load impact | Chilled and Condenser Water Piping | curve fit from Solarc cost calculations | All systems | COOLSYS1 PUMP SECONDARY | COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | US_LO_COOLSYS1 PUMP SECONDARY Flow Rate [gal/min] | 1377.9463 | 1227.8691 | 157108.9488 | 0 | 30 | 215105.7897 | 143433.6658 | 0 | 30 | 199931.3089 | 1279.9215 | 1147.5238 | 148144.8447 | 0 | 30 | 205138.3649 | 136228.3143 | 0 | 30 | 192010.7958 | 1055.1005 | 975.2656 | 128039.7305 | 0 | 30 | 183074.9683 | 121052.5089 | 0 | 30 | 113927.1921 | 1268.6614 | 1053.869 | 147122.841 | 0 | 30 | 167150.9443 | 127931.3366 | 0 | 30 | 128186.3064 | 1170.5194 | 1068.017 | 138282.308 | 0 | 30 | 149347.3945 | 129177.6841 | 0 | 30 | 130752.8377 |  | 8964.1041 | -4711.1789 | 12889.2278 | 21482.0464 | 8592.8185 | -13675.283 | -11916.5305 | -6987.2216 | -19191.5044 | -9104.6239
x | General Load impact | Hot Water Piping | curve fit from Solarc cost calculations | All reheat coils | ZN_VAV_Box | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | US_LO_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 333.7229 | 308.8504 | 607390.7467 | 0 | 30 | 907925.0822 | 578861.1766 | 0 | 30 | 873265.821 | 438.5215 | 420.6112 | 710189.8061 | 0 | 30 | 1034810.3335 | 694614.7444 | 0 | 30 | 1015318.2414 | 398.3272 | 378.7423 | 674088.8911 | 0 | 30 | 989804.0878 | 654998.6523 | 0 | 30 | 966224.6788 | 468.5349 | 451.3102 | 734447.3224 | 0 | 30 | 1065447.5995 | 720808.1051 | 0 | 30 | 1048175.2587 | 490.0421 | 470.7384 | 750410.5003 | 0 | 30 | 1085840.4809 | 736137.2992 | 0 | 30 | 1067596.865 |  | -102799.0594 | -131328.6295 |  |  |  | -28529.57 | -15575.0617 | -19090.2388 | -13639.2173 | -14273.2011
| 90.1-13by SHW runout insulation | SHW_runout | Additional insulation required on SHW runouts | SHW piping heat loss |  | SHW_runout_Insul | US_LO_SHW_runout_Insul | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | 416 | #N/A | #N/A
[59 empty] | 0 | 0
x | General Load impact Pump speed & control CHW |  | If value is "VFD" lookup cost based on the next motor size hp greater than 1.1 times the hp shown under Power (HP) | Pump | Secondary CHW | COOLSYS1 PUMP SECONDARY VSD | US_LO_COOLSYS1 PUMP SECONDARY VSD | VFD | VFD | 11231.1216 | 0 | 15 | 14738.1817 | 11231.1216 | 0 | 15 | 14738.1817 | VFD | VFD | 11231.1216 | 0 | 15 | 14738.1817 | 11231.1216 | 0 | 15 | 14738.1817 | VFD | VFD | 6130.9687 | 0 | 15 | 8149.686 | 6130.9687 | 0 | 15 | 8149.686 | VFD | VFD | 11231.1216 | 0 | 15 | 14738.1817 | 6130.9687 | 0 | 15 | 8149.686 | VFD | VFD | 11231.1216 | 0 | 15 | 14738.1817 | 6130.9687 | 0 | 15 | 8149.686 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | -5100.1529 | -5100.1529
|  | VFD_Size | cost input item for VFD | Pump | Secondary CHW | COOLSYS1 PUMP SECONDARY Pump Power [hp] | US_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.3006 | 19.675 | 11231.1216 | 0 | 15 | 14738.1817 | 11231.1216 | 0 | 15 | 14738.1817 | 20.7142 | 18.3876 | 11231.1216 | 0 | 15 | 14738.1817 | 11231.1216 | 0 | 15 | 14738.1817 | 17.0757 | 15.6274 | 6130.9687 | 0 | 15 | 8149.686 | 6130.9687 | 0 | 15 | 8149.686 | 20.5319 | 16.8869 | 11231.1216 | 0 | 15 | 14738.1817 | 6130.9687 | 0 | 15 | 8149.686 | 18.9436 | 17.1136 | 11231.1216 | 0 | 15 | 14738.1817 | 6130.9687 | 0 | 15 | 8149.686 |  | 0 | 0
x | General Load impact Pump speed & control HW |  | If value is "VFD" lookup cost based on the next motor size hp greater than 1.1 times the hp shown under Power (HP) | Pump | HW Pump | HEATSYS1 PUMP VSD | US_LO_HEATSYS1 PUMP VSD | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | VFD | 0 | 0 | 0 | 0 | 11231.1216 | 0 | 15 | 14738.1817 | No | VFD | 0 | 0 | 0 | 0 | 11231.1216 | 0 | 15 | 14738.1817 |  | 0 | 0 |  |  |  | 0 | 0 | 0 | 11231.1216 | 11231.1216
|  | VFD_Size | cost input item for VFD | Pump | HW Pump | HEATSYS1 PUMP Pump Power [hp] | US_LO_HEATSYS1 PUMP Pump Power [hp] | 19.247 | 17.7149 | 11231.1216 | 0 | 15 | 14738.1817 | 6130.9687 | 0 | 15 | 8149.686 | 24.4277 | 22.3919 | 11231.1216 | 0 | 15 | 14738.1817 | 11231.1216 | 0 | 15 | 14738.1817 | 22.5728 | 20.7571 | 11231.1216 | 0 | 15 | 14738.1817 | 11231.1216 | 0 | 15 | 14738.1817 | 26.5664 | 24.2489 | 11231.1216 | 0 | 15 | 14738.1817 | 11231.1216 | 0 | 15 | 14738.1817 | 28.4426 | 25.7229 | 11231.1216 | 0 | 15 | 14738.1817 | 11231.1216 | 0 | 15 | 14738.1817 |  | 0 | -5100.1529
x | 90.1-16g occ standby controls | occ_standby | 74 conditioned zones |  |  |  |  | 0 | 74 | 0 | 0 | 0 | 0 | 2230.7797 | 0 | 1110 | 3914.7553 | 0 | 74 | 0 | 0 | 0 | 0 | 2230.7797 | 0 | 1110 | 3914.7553 | 0 | 74 | 0 | 0 | 0 | 0 | 2230.7797 | 0 | 1110 | 3914.7553 | 0 | 74 | 0 | 0 | 0 | 0 | 2230.7797 | 0 | 1110 | 3914.7553 | 0 | 74 | 0 | 0 | 0 | 0 | 2230.7797 | 0 | 1110 | 3914.7553 |  | 0 | 2230.7797 |  |  |  | 2230.7797 | 2230.7797 | 2230.7797 | 2230.7797 | 2230.7797
x | 90.1-16 bq dry cooler efficiency | Dry_Cooler | Manually lookup cost based on capacity, which is hardcoded as 582,060 W, or 48.5 tons. |  |  | each 50 ton cooler |  | 1 | 1 | 53344.4665 | 0 | 20 | 59624.0511 | 55507.0185 | 0 | 20 | 62002.8583 | 1 | 1 | 53344.4665 | 0 | 20 | 59624.0511 | 55507.0185 | 0 | 20 | 62002.8583 | 1 | 1 | 53344.4665 | 0 | 20 | 59624.0511 | 55507.0185 | 0 | 20 | 62002.8583 | 1 | 1 | 53344.4665 | 0 | 20 | 59624.0511 | 55507.0185 | 0 | 20 | 62002.8583 | 1 | 1 | 53344.4665 | 0 | 20 | 59624.0511 | 55507.0185 | 0 | 20 | 62002.8583 |  | 0 | 2162.552 |  |  |  | 2162.552 | 2162.552 | 2162.552 | 2162.552 | 2162.552
x | 90.1-16 be CRAC efficiency | CRAC_Efficiency | Cost based on capacity, which is hardcoded as 20 tons basement. 6 units total |  |  | units are 20 tons |  | 6 | 6 | 444844.932 | 0 | 20 | 517711.3649 | 576233.2968 | 0 | 20 | 662238.5662 | 6 | 6 | 444844.932 | 0 | 20 | 517711.3649 | 576233.2968 | 0 | 20 | 662238.5662 | 6 | 6 | 444844.932 | 0 | 20 | 517711.3649 | 576233.2968 | 0 | 20 | 662238.5662 | 6 | 6 | 444844.932 | 0 | 20 | 517711.3649 | 576233.2968 | 0 | 20 | 662238.5662 | 6 | 6 | 444844.932 | 0 | 20 | 517711.3649 | 576233.2968 | 0 | 20 | 662238.5662 |  | 0 | 131388.3648 |  |  |  | 131388.3648 | 131388.3648 | 131388.3648 | 131388.3648 | 131388.3648
x | 90.1-16 be CRAC efficiency | CRAC_Efficiency_Small | Cost based on capacity, which is hardcoded as 2.5 tons each of bot, mid, top. 12 units total |  |  | units are 2.5 tons |  | 12 | 12 | 422415.5712 | 0 | 20 | 485509.1657 | 359263.128 | 0 | 20 | 416041.4782 | 12 | 12 | 422415.5712 | 0 | 20 | 485509.1657 | 359263.128 | 0 | 20 | 416041.4782 | 12 | 12 | 422415.5712 | 0 | 20 | 485509.1657 | 359263.128 | 0 | 20 | 416041.4782 | 12 | 12 | 422415.5712 | 0 | 20 | 485509.1657 | 359263.128 | 0 | 20 | 416041.4782 | 12 | 12 | 422415.5712 | 0 | 20 | 485509.1657 | 359263.128 | 0 | 20 | 416041.4782 |  | 0 | -63152.4432 |  |  |  | -63152.4432 | -63152.4432 | -63152.4432 | -63152.4432 | -63152.4432
| 90.1-07aj | Motor Efficiency | lookup cost based on the next motor size hp greater than 1.1 times the hp shown in this row. If bhp is between .7 and 1, value = 1. If < 0.7 = 0 - not subject to eff. req)
Not in 2016 |  | Motor_Efficiency |  | VAV_BOT | VAVCHW | VAV_BOT WITH REHEAT Fan Power [hp] | US_LO_VAV_BOT WITH REHEAT Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  |  |  | VAV_MID (estimate based on 5 systems, not 1 as modeled, costs multiplied by 5. Modeled system is too large for real application. Row included to screen out Out of Range * 5 which gives a Value error) | VAVCHW |  |  |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE |  |  | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE | OUT OF RANGE | OUT OF RANGE | #N/A | OUT OF RANGE
|  | Motor_Efficiency |  | VAV_MID | VAVCHW | VAV_MID WITH REHEAT Fan Power [hp] | US_LO_VAV_MID WITH REHEAT Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | VAV_TOP | VAVCHW | VAV_TOP WITH REHEAT Fan Power [hp] | US_LO_VAV_TOP WITH REHEAT Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | CAV_BAS | CAVCHW | CAV_BAS Fan Power [hp] | US_LO_CAV_BAS Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | DATACENTER BASEMENT |  | DATACENTER BASEMENT Fan Power [hp] | US_LO_DATACENTER BASEMENT Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | DATACENTER MID |  | DATACENTER MID Fan Power [hp] | US_LO_DATACENTER MID Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | Pump | Primary CHW | COOLSYS1 PUMP Pump Power [hp] | US_LO_COOLSYS1 PUMP Pump Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2016 |  | Motor_Efficiency |  | Pump | Secondary CHW | COOLSYS1 PUMP SECONDARY Pump Power [hp] | US_LO_COOLSYS1 PUMP SECONDARY Pump Power [hp] | 22.3006 | 19.675 | 6544.6407 | 0 | 18 | 7945.5498 | 6829.1052 | 0 | 18 | 8258.4607 | 20.7142 | 18.3876 | 6544.6407 | 0 | 18 | 7945.5498 | 6829.1052 | 0 | 18 | 8258.4607 | 17.0757 | 15.6274 | 5757.6548 | 0 | 18 | 7063.9411 | 6001.9787 | 0 | 18 | 7332.6974 | 20.5319 | 16.8869 | 6544.6407 | 0 | 18 | 7945.5498 | 6001.9787 | 0 | 18 | 7332.6974 | 18.9436 | 17.1136 | 6544.6407 | 0 | 18 | 7945.5498 | 6001.9787 | 0 | 18 | 7332.6974
Not in 2016 |  | Motor_Efficiency |  | Pump | Condenser Water | TOWERWATERSYS PUMP Pump Power [hp] | US_LO_TOWERWATERSYS PUMP Pump Power [hp] | 43.3467 | 38.2621 | 13102.6346 | 0 | 18 | 15569.8878 | 13699.262 | 0 | 18 | 16226.1779 | 40.1167 | 35.7867 | 13102.6346 | 0 | 18 | 15569.8878 | 9853.691 | 0 | 18 | 11871.6424 | 33.3337 | 30.5124 | 9439.8438 | 0 | 18 | 11416.4104 | 9853.691 | 0 | 18 | 11871.6424 | 39.7662 | 32.898 | 13102.6346 | 0 | 18 | 15569.8878 | 9853.691 | 0 | 18 | 11871.6424 | 36.7052 | 33.165 | 13102.6346 | 0 | 18 | 15569.8878 | 9853.691 | 0 | 18 | 11871.6424
Not in 2016 |  | Motor_Efficiency |  | Pump | Hot Water | HEATSYS1 PUMP Pump Power [hp] | US_LO_HEATSYS1 PUMP Pump Power [hp] | 19.247 | 17.7149 | 6544.6407 | 0 | 18 | 7945.5498 | 6001.9787 | 0 | 18 | 7332.6974 | 24.4277 | 22.3919 | 8592.74 | 0 | 18 | 10360.1888 | 6829.1052 | 0 | 18 | 8258.4607 | 22.5728 | 20.7571 | 6544.6407 | 0 | 18 | 7945.5498 | 6829.1052 | 0 | 18 | 8258.4607 | 26.5664 | 24.2489 | 8592.74 | 0 | 18 | 10360.1888 | 8972.0013 | 0 | 18 | 10777.3762 | 28.4426 | 25.7229 | 9439.8438 | 0 | 18 | 11416.4104 | 8972.0013 | 0 | 18 | 10777.3762
NOTES:
[10 empty] | 9571093.7701 |  |  | 14240952.5243 | 9411207.2739 |  |  | 14016545.279 |  |  | 9675103.5811 |  |  | 14388451.9272 | 9556732.4775 |  |  | 14209853.3536 |  |  | 9326080.4172 |  |  | 14079660.8088 | 9255585.64 |  |  | 13890118.8443 |  |  | 9723286.2462 |  |  | 14419766.7666 | 9546437.8272 |  |  | 14157717.767 |  |  | 9717248.476 |  |  | 14410118.6351 | 9581811.9314 |  |  | 14206035.3544
[9 empty] | 14240952.5243 |  |  |  | 14012630.5237 | [5 empty] | 14388451.9272 |  |  |  | 14205938.5983 | [5 empty] | 14079660.8088 |  |  |  | 13886204.089 | [5 empty] | 14419766.7666 |  |  |  | 14153803.0117 | [5 empty] | 14410118.6351 |  |  |  | 14202120.5991

## HVAC Standalone Retail Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Standalone Retail | [7 empty] | Standalone Retail
[10 empty] | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW | Find Row
|  |  | YES |  |  |  |  | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
[7 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 2 | 3A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 3 | 3B | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 4 | 4A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 5 | 5A | Base Code | 2016 |  |  | Target Code | 2019 |  |  |  | First cost difference |  | 2016 | vs | 2019
Costs row marked x, other rows not marked | [7 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [9 empty] | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameters | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total |  | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
| HVAC System - general load change | CAV_DX | lookup based on cooling tons
x |  | CAV_DX |  | PSZ-AC:1 | CAVDX | PSZ-AC:1 Cooling Capacity [ton] | US_RS_PSZ-AC:1 Cooling Capacity [ton] | 11.3139 | 10.9459 | 15062.666 | 0 | 15 | 19485.4237 | 14682.312 | 0 | 15 | 19043.9287 | 10.5812 | 10.2412 | 14305.3467 | 0 | 15 | 18606.3671 | 13953.9594 | 0 | 15 | 18198.495 | 10.5384 | 9.9057 | 14261.1768 | 0 | 15 | 18555.0969 | 13622.658 | 0 | 15 | 17801.8737 | 10.4557 | 10.0917 | 14175.723 | 0 | 15 | 18455.9067 | 13799.4425 | 0 | 15 | 18019.1399 | 9.5963 | 9.1249 | 13353.5727 | 0 | 15 | 17449.9518 | 12943.6529 | 0 | 15 | 16913.8403 |  | -380.3539 | -351.3874 | -638.5188 | -376.2805 | -409.9198
x |  | CAV_DX | cost estimate based on two smaller units, costs per unit multiplied by two | PSZ-AC:2 | CAVDX | PSZ-AC:2 Cooling Capacity [ton] | US_RS_PSZ-AC:2 Cooling Capacity [ton] | 25.6002 | 24.035 | 25856.6124 | 0 | 15 | 32671.1498 | 24779.0467 | 0 | 15 | 31380.8814 | 24.8879 | 23.8479 | 25366.2376 | 0 | 15 | 32083.9789 | 24650.2679 | 0 | 15 | 31226.6828 | 23.7308 | 22.6941 | 24569.604 | 0 | 15 | 31130.0965 | 23855.8876 | 0 | 15 | 30275.4983 | 24.0046 | 23.1233 | 24758.1199 | 0 | 15 | 31355.8239 | 24151.3501 | 0 | 15 | 30629.2827 | 22.1886 | 21.2441 | 23507.8675 | 0 | 15 | 29858.7818 | 22857.6242 | 0 | 15 | 29080.1859 |  | -1077.5657 | -715.9696 | -713.7164 | -606.7698 | -650.2432
x |  | CAV_DX |  | PSZ-AC:3 | CAVDX | PSZ-AC:3 Cooling Capacity [ton] | US_RS_PSZ-AC:3 Cooling Capacity [ton] | 6.8904 | 6.7656 | 10575.0042 | 0 | 15 | 14036.306 | 10414.3955 | 0 | 15 | 13850.2307 | 6.4722 | 6.314 | 10036.6928 | 0 | 15 | 13412.6384 | 9833.0723 | 0 | 15 | 13176.7313 | 6.6327 | 6.4618 | 10243.2488 | 0 | 15 | 13651.9466 | 10023.267 | 0 | 15 | 13397.0837 | 6.3493 | 6.1924 | 9878.4376 | 0 | 15 | 13229.2898 | 9676.4643 | 0 | 15 | 12995.291 | 5.7425 | 5.5854 | 9210.7878 | 0 | 15 | 12424.5846 | 9077.7323 | 0 | 15 | 12251.3976 |  | -160.6087 | -203.6205 | -219.9819 | -201.9734 | -133.0555
x |  | CAV_DX |  | PSZ-AC:4 | CAVDX | PSZ-AC:4 Cooling Capacity [ton] | US_RS_PSZ-AC:4 Cooling Capacity [ton] | 5.674 | 5.5415 | 9152.8195 | 0 | 15 | 12349.1322 | 9040.5835 | 0 | 15 | 12203.0443 | 5.2462 | 5.0929 | 8790.5199 | 0 | 15 | 11877.5579 | 8660.7124 | 0 | 15 | 11708.5986 | 5.2991 | 5.1178 | 8835.3565 | 0 | 15 | 11935.9179 | 8681.7824 | 0 | 15 | 11736.0236 | 5.1749 | 5.0213 | 8730.1487 | 0 | 15 | 11798.9779 | 8600.0908 | 0 | 15 | 11629.6927 | 4.5449 | 4.3672 | 8203.5903 | 0 | 15 | 11116.7115 | 8055.7962 | 0 | 15 | 10925.555 |  | -112.236 | -129.8075 | -153.5741 | -130.0579 | -147.7941
x |  | Air Distribution | curve fit from Solarc cost calculations - described in HVAC Costs Comp. Material, labor, and project cost adjustments applied in this worksheet. |  |  | sum of PSZ-AC:1 Supply Flow Rate [cfm] to PSZ-AC:4 Supply Flow Rate [cfm] (not the sum of the cooling capacity) |  | 23667.8896 | 22375.3728 | 205485.0746 | 0 | 30 | 264505.3799 | 201421.0263 | 0 | 30 | 259528.3597 | 23625.512 | 22269.4288 | 205351.8271 | 0 | 30 | 264342.1989 | 201087.9076 | 0 | 30 | 259120.4073 | 26761.4544 | 25341.8048 | 215212.1408 | 0 | 30 | 276417.5922 | 210748.3502 | 0 | 30 | 270951.029 | 23307.68 | 22121.1072 | 204352.471 | 0 | 30 | 263118.3415 | 200621.5414 | 0 | 30 | 258549.2738 | 22799.1488 | 21421.8768 | 202753.5012 | 0 | 30 | 261160.1696 | 198422.958 | 0 | 30 | 255856.7875 |  | -4064.0482 | -4263.9195 | -4463.7907 | -3730.9295 | -4330.5432
|  |  | Material |  |  | PSZ-AC:1 Supply Flow Rate [cfm] | US_RS_PSZ-AC:1 Supply Flow Rate [cfm] | 4174.1936 | 3941.1168 | [8 empty] | 4110.6272 | 3856.3616 | [8 empty] | 4746.2912 | 4449.648 | [8 empty] | 3983.4944 | 3729.2288 | [8 empty] | 3771.6064 | 3474.9632
|  |  | y = 1.6479x + 55981 |  |  | PSZ-AC:2 Supply Flow Rate [cfm] | US_RS_PSZ-AC:2 Supply Flow Rate [cfm] | 15361.88 | 14429.5728 | [8 empty] | 15446.6352 | 14514.328 | [8 empty] | 17311.2496 | 16357.7536 | [8 empty] | 15277.1248 | 14471.9504 | [8 empty] | 15192.3696 | 14281.2512
|  |  | Labor |  |  | PSZ-AC:3 Supply Flow Rate [cfm] | US_RS_PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2267.2016 | [8 empty] | 2309.5792 | 2224.824 | [8 empty] | 2648.6 | 2563.8448 | [8 empty] | 2288.3904 | 2224.824 | [8 empty] | 2203.6352 | 2118.88
|  |  | y = 0.2548x + 18981 |  |  | PSZ-AC:4 Supply Flow Rate [cfm] | US_RS_PSZ-AC:4 Supply Flow Rate [cfm] | 1801.048 | 1737.4816 | [8 empty] | 1758.6704 | 1673.9152 | [8 empty] | 2055.3136 | 1970.5584 | [8 empty] | 1758.6704 | 1695.104 | [8 empty] | 1631.5376 | 1546.7824
0 | 90.1-10ca | Vestibule_Control | Lock out vestibule or air curtain heat on outside air temperature |  |  | Vestibule count | US_SR_Vestibule count | 1 | 1 | 354.6123 | 0 | 15 | 469.041 | 583.7669 | 0 | 15 | 588.4701 | 1 | 1 | 354.6123 | 0 | 15 | 469.041 | 583.7669 | 0 | 15 | 588.4701 | 1 | 1 | 354.6123 | 0 | 15 | 469.041 | 583.7669 | 0 | 15 | 588.4701 | 1 | 1 | 354.6123 | 0 | 15 | 469.041 | 583.7669 | 0 | 15 | 588.4701 | 1 | 1 | 354.6123 | 0 | 15 | 469.041 | 583.7669 | 0 | 15 | 588.4701 | 505
0 | 90.1-10aa 90.1-10cb | Optimum_Start_Control | Increase in controls cost to accommodate optimum start through addenda 90.1-10aa and 90.1-10cb | PSZ-AC_2:7 | CAVDX | Unit count | US_SR_Unit count | 5 | 5 | 2447.0074 | 0 | 15 | 3086.5454 | 5625.018 | 0 | 15 | 6434.798 | 5 | 5 | 2447.0074 | 0 | 15 | 3086.5454 | 5625.018 | 0 | 15 | 6434.798 | 5 | 5 | 2447.0074 | 0 | 15 | 3086.5454 | 5625.018 | 0 | 15 | 6434.798 | 5 | 5 | 2447.0074 | 0 | 15 | 3086.5454 | 5625.018 | 0 | 15 | 6434.798 | 5 | 5 | 2447.0074 | 0 | 15 | 3086.5454 | 5625.018 | 0 | 15 | 6434.798 | 508
| 90.1-10aq |  |  |  |  | For 2013, Cost for 2 stage fan and added cooling stage applies if single zone DX system Cooling Capacity [ton] above 5.4167 tons, prototype value shown as "yes" if so, or "no" if not. | If applicable, add the fan and staging cost together for the target code; For units greater than 110 MBH (9.167 tons) include fan control only in the base case per 2010 requirements.
0 |  |  | Capacity check & Select | PSZ-AC:1 | CAVDX |  |  | Yes | Yes | 413.5286 | 0 | 15 | 454.8815 | 1172.0489 | 0 | 15 | 1289.2538 | Yes | Yes | 406.5199 | 0 | 15 | 346.3576 | 1111.9977 | 0 | 15 | 1223.1975 | Yes | Yes | 406.1111 | 0 | 15 | 446.7222 | 1083.4074 | 0 | 15 | 1191.7482 | Yes | Yes | 405.3203 | 0 | 15 | 445.8523 | 1099.2581 | 0 | 15 | 1209.1839 | Yes | Yes | 397.0988 | 0 | 15 | 436.8087 | 1016.8678 | 0 | 15 | 1118.5546
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC:1 | CAVDX | PSZ-AC:1 Cooling Capacity [ton] | US_RS_PSZ-AC:1 Cooling Capacity [ton] | 11.3139 | 10.9459 | 413.5286 | 0 | 15 | 454.8815 | 410.0086 | 0 | 15 | 451.0094 | 10.5812 | 10.2412 | 406.5199 | 0 | 15 | 346.3576 | 403.2679 | 0 | 15 | 443.5947 | 10.5384 | 9.9057 | 406.1111 | 0 | 15 | 446.7222 | 400.0587 | 0 | 15 | 440.0646 | 10.4557 | 10.0917 | 405.3203 | 0 | 15 | 445.8523 | 401.8379 | 0 | 15 | 442.0217 | 9.5963 | 9.1249 | 397.0988 | 0 | 15 | 436.8087 | 392.5897 | 0 | 15 | 431.8487
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC:1 | CAVDX | PSZ-AC:1 Cooling Capacity [ton] | US_RS_PSZ-AC:1 Cooling Capacity [ton] | 11.3139 | 10.9459 | 789.8797 | 0 | 15 | 868.8676 | 762.0403 | 0 | 15 | 838.2443 | 10.5812 | 10.2412 | 734.449 | 0 | 15 | 807.8939 | 708.7298 | 0 | 15 | 779.6028 | 10.5384 | 9.9057 | 731.216 | 0 | 15 | 804.3376 | 683.3487 | 0 | 15 | 751.6836 | 10.4557 | 10.0917 | 724.9614 | 0 | 15 | 797.4575 | 697.4202 | 0 | 15 | 767.1622 | 9.5963 | 9.1249 | 659.9394 | 0 | 15 | 725.9334 | 624.2781 | 0 | 15 | 686.7059
0 |  |  | Capacity check & Select | PSZ-AC:2 | CAVDX |  |  | Yes | Yes | 795.0666 | 0 | 15 | 874.5733 | 4335.6887 | 0 | 15 | 4769.2576 | Yes | Yes | 781.4399 | 0 | 15 | 346.3576 | 4303.8081 | 0 | 15 | 4734.1889 | Yes | Yes | 759.3027 | 0 | 15 | 835.233 | 4107.1503 | 0 | 15 | 4517.8654 | Yes | Yes | 764.5413 | 0 | 15 | 840.9954 | 4180.2954 | 0 | 15 | 4598.3249 | Yes | Yes | 729.7987 | 0 | 15 | 802.7786 | 3860.0191 | 0 | 15 | 4246.021
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC:2 | CAVDX | PSZ-AC:2 Cooling Capacity [ton] | US_RS_PSZ-AC:2 Cooling Capacity [ton] | 51.2004 | 48.07 | 795.0666 | 0 | 15 | 874.5733 | 765.1228 | 0 | 15 | 841.6351 | 49.7758 | 47.6959 | 781.4399 | 0 | 15 | 346.3576 | 761.5442 | 0 | 15 | 837.6987 | 47.4616 | 45.3882 | 759.3027 | 0 | 15 | 835.233 | 739.4697 | 0 | 15 | 813.4166 | 48.0092 | 46.2465 | 764.5413 | 0 | 15 | 840.9954 | 747.6801 | 0 | 15 | 822.4481 | 44.3772 | 42.4882 | 729.7987 | 0 | 15 | 802.7786 | 711.7295 | 0 | 15 | 782.9025
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC:2 | CAVDX | PSZ-AC:2 Cooling Capacity [ton] | US_RS_PSZ-AC:2 Cooling Capacity [ton] | 51.2004 | 48.07 | 3807.3856 | 0 | 15 | 4188.1241 | 3570.5659 | 0 | 15 | 3927.6225 | 49.7758 | 47.6959 | 3699.6145 | 0 | 15 | 4069.576 | 3542.2639 | 0 | 15 | 3896.4903 | 47.4616 | 45.3882 | 3524.5361 | 0 | 15 | 3876.9898 | 3367.6807 | 0 | 15 | 3704.4487 | 48.0092 | 46.2465 | 3565.9668 | 0 | 15 | 3922.5635 | 3432.6153 | 0 | 15 | 3775.8768 | 44.3772 | 42.4882 | 3291.1953 | 0 | 15 | 3620.3148 | 3148.2895 | 0 | 15 | 3463.1185
0 |  |  | Capacity check & Select | PSZ-AC:3 | CAVDX |  |  | No | Yes | 0 | 0 | 0 | 0 | 815.8184 | 0 | 15 | 897.4002 | No | Yes | 0 | 0 | 0 | 0 | 777.3343 | 0 | 15 | 855.0677 | No | Yes | 0 | 0 | 0 | 0 | 789.9253 | 0 | 15 | 868.9179 | No | Yes | 0 | 0 | 0 | 0 | 766.9667 | 0 | 15 | 843.6633 | No | Yes | 0 | 0 | 0 | 0 | 715.2387 | 0 | 15 | 786.7626
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC:3 | CAVDX | PSZ-AC:3 Cooling Capacity [ton] | US_RS_PSZ-AC:3 Cooling Capacity [ton] | 6.8904 | 6.7656 | 371.2157 | 0 | 15 | 408.3372 | 370.0222 | 0 | 15 | 407.0244 | 6.4722 | 6.314 | 367.2155 | 0 | 15 | 346.3576 | 365.7024 | 0 | 15 | 402.2726 | 6.6327 | 6.4618 | 368.7504 | 0 | 15 | 405.6255 | 367.1157 | 0 | 15 | 403.8273 | 6.3493 | 6.1924 | 366.0395 | 0 | 15 | 402.6435 | 364.5387 | 0 | 15 | 400.9925 | 5.7425 | 5.5854 | 360.2353 | 0 | 15 | 396.2589 | 358.7323 | 0 | 15 | 394.6055
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC:3 | CAVDX | PSZ-AC:3 Cooling Capacity [ton] | US_RS_PSZ-AC:3 Cooling Capacity [ton] | 6.8904 | 6.7656 | 455.2352 | 0 | 15 | 500.7587 | 445.7962 | 0 | 15 | 490.3758 | 6.4722 | 6.314 | 423.5986 | 0 | 15 | 465.9585 | 411.6319 | 0 | 15 | 452.795 | 6.6327 | 6.4618 | 435.7379 | 0 | 15 | 479.3117 | 422.8096 | 0 | 15 | 465.0906 | 6.3493 | 6.1924 | 414.298 | 0 | 15 | 455.7278 | 402.428 | 0 | 15 | 442.6708 | 5.7425 | 5.5854 | 368.394 | 0 | 15 | 405.2334 | 356.5064 | 0 | 15 | 392.1571
0 |  |  | Capacity check & Select | PSZ-AC:4 | CAVDX |  |  | No | Yes | 0 | 0 | 0 | 0 | 711.5 | 0 | 15 | 782.65 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC:4 | CAVDX | PSZ-AC:4 Cooling Capacity [ton] | US_RS_PSZ-AC:4 Cooling Capacity [ton] | 5.674 | 5.5415 | 359.5805 | 0 | 15 | 395.5385 | 358.3126 | 0 | 15 | 394.1439 | 5.2462 | 5.0929 | 355.4877 | 0 | 15 | 346.3576 | 354.0213 | 0 | 15 | 389.4234 | 5.2991 | 5.1178 | 355.9942 | 0 | 15 | 391.5936 | 354.2593 | 0 | 15 | 389.6853 | 5.1749 | 5.0213 | 354.8057 | 0 | 15 | 390.2863 | 353.3365 | 0 | 15 | 388.6701 | 4.5449 | 4.3672 | 348.7799 | 0 | 15 | 383.6578 | 347.08 | 0 | 15 | 381.788
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC:4 | CAVDX | PSZ-AC:4 Cooling Capacity [ton] | US_RS_PSZ-AC:4 Cooling Capacity [ton] | 5.674 | 5.5415 | 363.215 | 0 | 15 | 399.5364 | 353.1874 | 0 | 15 | 388.5062 | 5.2462 | 5.0929 | 330.8459 | 0 | 15 | 363.9305 | 319.2485 | 0 | 15 | 351.1734 | 5.2991 | 5.1178 | 334.8518 | 0 | 15 | 368.337 | 321.131 | 0 | 15 | 353.2441 | 5.1749 | 5.0213 | 325.4522 | 0 | 15 | 357.9974 | 313.8324 | 0 | 15 | 345.2156 | 4.5449 | 4.3672 | 277.7948 | 0 | 15 | 305.5743 | 264.3511 | 0 | 15 | 290.7862
| 90.1-10bt and impact of any changes in OA requirements | Energy_Recovery_Packaged | if "Yes" lookup and interpolate costs based on outside airflow, cfm. |  |  | [Yes,No] are parameter values, indicating if expanded ERV requirements apply. Based on 2010 and 2013 standards.
0 |  | Energy_Recovery_Packaged |  | PSZ-AC:2 | CAVDX | PSZ_AC_2 Energy Recovery [yes/no] | US_RS_PSZ_AC_2 Energy Recovery [yes/no] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | Energy_Recovery_Packaged |  | PSZ-AC:2 | CAVDX | PSZ-AC:2 OA Rate [cfm] | US_RS_PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 4005.1282 | 4005.1282 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 4005.1282 | 4005.1282 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 4005.1282 | 4005.1282 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 4005.1282 | 4005.1282 | 27321.5797 | 255.0825 | 15 | 31497.9483 | 27321.5797 | 255.0825 | 15 | 31497.9483
| 90.1-16a | Outdoor_Air_Dampers | Motorized return air damper
|  | Outdoor_Air_Dampers | system cost |  |  |  |  | motorized | motorized | 386.5106 | 0 | 20 | 398.6458 | 451.5617 | 0 | 20 | 519.4937 | motorized | motorized | 386.5106 | 0 | 20 | 398.6458 | 451.5617 | 0 | 20 | 519.4937 | motorized | motorized | 386.5106 | 0 | 20 | 398.6458 | 451.5617 | 0 | 20 | 519.4937 | motorized | motorized | 386.5106 | 0 | 20 | 398.6458 | 451.5617 | 0 | 20 | 519.4937 | motorized | motorized | 386.5106 | 0 | 20 | 398.6458 | 451.5617 | 0 | 20 | 519.4937
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC:1 OA Rate [cfm] | US_RS_PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 292.4834 | 98.8148 | 20 | 317.8374 | 317.066 | 98.8148 | 20 | 379.3281 | 490.669 | 490.669 | 292.4834 | 98.8148 | 20 | 317.8374 | 317.066 | 98.8148 | 20 | 379.3281 | 490.669 | 490.669 | 292.4834 | 98.8148 | 20 | 317.8374 | 317.066 | 98.8148 | 20 | 379.3281 | 490.669 | 490.669 | 292.4834 | 98.8148 | 20 | 317.8374 | 317.066 | 98.8148 | 20 | 379.3281 | 490.669 | 490.669 | 292.4834 | 98.8148 | 20 | 317.8374 | 317.066 | 98.8148 | 20 | 379.3281
x |  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC:1 | CAVDX | PSZ-AC:1 OA Rate [cfm] | US_RS_PSZ-AC:1 OA Rate [cfm] | 490.669 | 490.669 | 678.9941 | 98.8148 | 20 | 716.4832 | 768.6277 | 98.8148 | 20 | 898.8217 | 490.669 | 490.669 | 678.9941 | 98.8148 | 20 | 716.4832 | 768.6277 | 98.8148 | 20 | 898.8217 | 490.669 | 490.669 | 678.9941 | 98.8148 | 20 | 716.4832 | 768.6277 | 98.8148 | 20 | 898.8217 | 490.669 | 490.669 | 678.9941 | 98.8148 | 20 | 716.4832 | 768.6277 | 98.8148 | 20 | 898.8217 | 490.669 | 490.669 | 678.9941 | 98.8148 | 20 | 716.4832 | 768.6277 | 98.8148 | 20 | 898.8217 |  | 89.6336 | 89.6336 | 89.6336 | 89.6336 | 89.6336
|  | Outdoor_Air_Dampers | system cost |  |  |  |  | motorized | motorized | 498.4141 | 0 | 20 | 523.7087 | 589.9958 | 0 | 20 | 686.3108 | motorized | motorized | 498.4141 | 0 | 20 | 523.7087 | 589.9958 | 0 | 20 | 686.3108 | motorized | motorized | 498.4141 | 0 | 20 | 523.7087 | 589.9958 | 0 | 20 | 686.3108 | motorized | motorized | 498.4141 | 0 | 20 | 523.7087 | 589.9958 | 0 | 20 | 686.3108 | motorized | motorized | 498.4141 | 0 | 20 | 523.7087 | 589.9958 | 0 | 20 | 686.3108
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC:2 OA Rate [cfm] | US_RS_PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 630.0802 | 135.9714 | 20 | 702.3763 | 680.8134 | 135.9714 | 20 | 829.2802 | 4005.1282 | 4005.1282 | 630.0802 | 135.9714 | 20 | 702.3763 | 680.8134 | 135.9714 | 20 | 829.2802 | 4005.1282 | 4005.1282 | 630.0802 | 135.9714 | 20 | 702.3763 | 680.8134 | 135.9714 | 20 | 829.2802 | 4005.1282 | 4005.1282 | 630.0802 | 135.9714 | 20 | 702.3763 | 680.8134 | 135.9714 | 20 | 829.2802 | 4005.1282 | 4005.1282 | 630.0802 | 135.9714 | 20 | 702.3763 | 680.8134 | 135.9714 | 20 | 829.2802
x |  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC:2 | CAVDX | PSZ-AC:2 OA Rate [cfm] | US_RS_PSZ-AC:2 OA Rate [cfm] | 4005.1282 | 4005.1282 | 1128.4944 | 135.9714 | 20 | 1226.085 | 1270.8092 | 135.9714 | 20 | 1515.5911 | 4005.1282 | 4005.1282 | 1128.4944 | 135.9714 | 20 | 1226.085 | 1270.8092 | 135.9714 | 20 | 1515.5911 | 4005.1282 | 4005.1282 | 1128.4944 | 135.9714 | 20 | 1226.085 | 1270.8092 | 135.9714 | 20 | 1515.5911 | 4005.1282 | 4005.1282 | 1128.4944 | 135.9714 | 20 | 1226.085 | 1270.8092 | 135.9714 | 20 | 1515.5911 | 4005.1282 | 4005.1282 | 1128.4944 | 135.9714 | 20 | 1226.085 | 1270.8092 | 135.9714 | 20 | 1515.5911 |  | 142.3149 | 142.3149 | 142.3149 | 142.3149 | 142.3149
|  | Outdoor_Air_Dampers | system cost |  |  |  |  | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051 | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051 | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051 | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051 | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC:3 OA Rate [cfm] | US_RS_PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254 | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254 | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254 | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254 | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254
x |  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC:3 | CAVDX | PSZ-AC:3 OA Rate [cfm] | US_RS_PSZ-AC:3 OA Rate [cfm] | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 |  | 88.4327 | 88.4327 | 88.4327 | 88.4327 | 88.4327
|  | Outdoor_Air_Dampers | system cost |  |  |  |  | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051 | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051 | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051 | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051 | motorized | motorized | 375.5635 | 0 | 20 | 385.8004 | 439.4136 | 0 | 20 | 504.2051
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC:4 OA Rate [cfm] | US_RS_PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254 | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254 | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254 | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254 | 377.3937 | 377.3937 | 292.5389 | 97.8989 | 20 | 317.9347 | 317.1215 | 97.8989 | 20 | 379.4254
x |  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC:4 | CAVDX | PSZ-AC:4 OA Rate [cfm] | US_RS_PSZ-AC:4 OA Rate [cfm] | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 | 377.3937 | 377.3937 | 668.1025 | 97.8989 | 20 | 703.7351 | 756.5351 | 97.8989 | 20 | 883.6305 |  | 88.4327 | 88.4327 | 88.4327 | 88.4327 | 88.4327
90.1-16 bo furnace efficiency
x |  | Furnace_eff | 4 units |  |  | Furnace heating capacity [Btuh] | US_RS_Furnace heating capacity [Btuh] | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 |  | 592.48 | 592.48 | 592.48 | 592.48 | 592.48
No diff for 2010-13 so HIDE | 90.1-07cy | DX_Economizer | if any value other than "no" 1ookup cost based on supply air cfm |  |  | economizer parameter value is [No, differntial | economizer parameter value is [No, DifferentialEnthalpy]
Not in 2013 |  | DX_Economizer |  | PSZ-AC:1 | CAVDX | PSZ-AC:1 (economizer) | US_RS_PSZ-AC:1 (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | DX_Economizer |  |  |  | PSZ-AC:1 Supply Flow Rate [cfm] | US_RS_PSZ-AC:1 Supply Flow Rate [cfm] | 4174.1936 | 3941.1168 | 5093.2716 | 181.6477 | 15 | 5666.461 | 4849.9329 | 173.9218 | 15 | 5389.544 | 4110.6272 | 3856.3616 | 5029.7858 | 179.1139 | 15 | 5592.8112 | 4750.0888 | 172.7956 | 15 | 5281.4589 | 4746.2912 | 4449.648 | 5664.6434 | 204.4522 | 15 | 6329.3086 | 5368.3765 | 192.6276 | 15 | 5985.6098 | 3983.4944 | 3729.2288 | 4899.8549 | 174.4849 | 15 | 5443.5866 | 4600.3228 | 171.1064 | 15 | 5119.3312 | 3771.6064 | 3474.9632 | 4650.2448 | 171.6695 | 15 | 5173.3738 | 4300.7907 | 167.728 | 15 | 4795.0758
Not in 2013 |  | DX_Economizer |  | PSZ-AC:2 | CAVDX | PSZ-AC:2 (economizer) | US_RS_PSZ-AC:2 (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | DX_Economizer |  |  |  | PSZ-AC:2 Supply Flow Rate [cfm] | US_RS_PSZ-AC:2 Supply Flow Rate [cfm] | 15361.88 | 14429.5728 | 17787.3851 | 214.5653 | 15 | 20268.552 | 16661.5441 | 214.5653 | 15 | 18957.1556 | 15446.6352 | 14514.328 | 17899.0925 | 214.5653 | 15 | 20404.1924 | 16757.9564 | 214.5653 | 15 | 19065.9549 | 17311.2496 | 16357.7536 | 20356.6554 | 214.5653 | 15 | 23388.2819 | 19099.9471 | 214.5653 | 15 | 21862.3271 | 15277.1248 | 14471.9504 | 17675.6776 | 214.5653 | 15 | 20132.9115 | 16709.7502 | 214.5653 | 15 | 19011.5552 | 15192.3696 | 14281.2512 | 17563.9702 | 214.5653 | 15 | 19997.2711 | 16492.8225 | 214.5653 | 15 | 18766.7567
Not in 2013 |  | DX_Economizer |  | PSZ-AC:3 | CAVDX | PSZ-AC:3 (economizer) | US_RS_PSZ-AC:3 (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | DX_Economizer |  |  |  | PSZ-AC:3 Supply Flow Rate [cfm] | US_RS_PSZ-AC:3 Supply Flow Rate [cfm] | 2330.768 | 2267.2016 | 3353.4739 | 152.525 | 15 | 3756.1959 | 3316.6394 | 151.6804 | 15 | 3715.0509 | 2309.5792 | 2224.824 | 3341.1957 | 152.2435 | 15 | 3742.4809 | 3292.083 | 151.1173 | 15 | 3687.6209 | 2648.6 | 2563.8448 | 3537.6465 | 156.7481 | 15 | 3961.9206 | 3488.5338 | 155.6219 | 15 | 3907.0607 | 2288.3904 | 2224.824 | 3328.9175 | 151.962 | 15 | 3728.7659 | 3292.083 | 151.1173 | 15 | 3687.6209 | 2203.6352 | 2118.88 | 3279.8048 | 150.8358 | 15 | 3673.906 | 3230.6922 | 149.7097 | 15 | 3619.046
Not in 2013 |  | DX_Economizer |  | PSZ-AC:4 | CAVDX | PSZ-AC:4 (economizer) | US_RS_PSZ-AC:4 (economizer) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
|  | DX_Economizer |  |  |  | PSZ-AC:4 Supply Flow Rate [cfm] | US_RS_PSZ-AC:4 Supply Flow Rate [cfm] | 1801.048 | 1737.4816 | 3004.894 | 145.4866 | 15 | 3367.3657 | 2954.7599 | 144.642 | 15 | 3311.5376 | 1758.6704 | 1673.9152 | 2971.4713 | 144.9235 | 15 | 3330.147 | 2904.6258 | 143.7974 | 15 | 3255.7096 | 2055.3136 | 1970.5584 | 3193.8576 | 148.8651 | 15 | 3577.9011 | 3138.5851 | 147.7389 | 15 | 3516.2405 | 1758.6704 | 1695.104 | 2971.4713 | 144.9235 | 15 | 3330.147 | 2921.3372 | 144.0789 | 15 | 3274.3189 | 1631.5376 | 1546.7824 | 2871.203 | 143.2343 | 15 | 3218.4909 | 2804.3575 | 142.1082 | 15 | 3144.0535
No diff for 2010-13 so HIDE | 90.1-07aj | Motor_Efficiency | lookup cost based on the next motor size hp greater than 1.1 times the supply fan motor bhp
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC:1 | CAVDX | PSZ-AC:1 Fan Power [hp] | US_RS_PSZ-AC:1 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC:2 | CAVDX | PSZ-AC:2 Fan Power [hp] | US_RS_PSZ-AC:2 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC:3 | CAVDX | PSZ-AC:3 Fan Power [hp] | US_RS_PSZ-AC:3 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC:4 | CAVDX | PSZ-AC:4 Fan Power [hp] | US_RS_PSZ-AC:4 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | Unit Heater | Unit Heater | FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | US_RS_FRONT_ENTRY UNIT HEATERFAN Fan Power [bhp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| No differences seen in ERV Requirements for national; AC-2 set up above | [8 empty] | 287320.9066 |  |  | 367690.6521 | 282527.3879 |  |  | 362133.0687 |  |  | 285039.3541 |  |  | 364966.0018 | 280375.9435 |  |  | 359557.5388 |  |  | 294310.257 |  |  | 376333.9106 | 289121.9689 |  |  | 370288.1322 |  |  | 283083.6302 |  |  | 362601.6003 | 279038.9129 |  |  | 357949.3039 |  |  | 278218.0493 |  |  | 356653.4599 | 273547.7874 |  |  | 351154.3902

## HVAC Primary School Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Primary School | [7 empty] | Primary School
[6 empty] | $W |  |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW
|  |  | YES |  |  |  |  | 3 | 4 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 5 | 6 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 7 | 8 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 9 | 10 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | 11 | 12 | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
[7 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 2 | 3A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 3 | 3B | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 4 | 4A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 5 | 5A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Using Col C keyword | First cost difference |  | 2016 | vs | 2019
Costs row marked x, other rows not marked | [7 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Base | Target | [8 empty] | Find | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameter | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Row in | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Costs_Comp
| HVAC System - General Load Change |  | Lookup based on cooling tons
x |  | VAV_DX |  | VAV_POD_1 | VAVDX | VAV_POD_1 Cooling Capacity [ton] | US_PS_VAV_POD_1 Cooling Capacity [ton] | 19.3372 | 18.3769 | 38970.7221 | 0 | 15 | 47233.8027 | 37081.334 | 0 | 15 | 45026.1177 | 18.6648 | 18.1241 | 37647.8394 | 0 | 15 | 45688.0598 | 36584.1104 | 0 | 15 | 44445.1291 | 22.3173 | 21.0521 | 43731.6028 | 0 | 15 | 52956.3392 | 41844.1297 | 0 | 15 | 50663.7466 | 18.6852 | 18.1708 | 37687.8645 | 0 | 15 | 45734.8278 | 36675.8858 | 0 | 15 | 44552.3654 | 18.6048 | 18.1705 | 37529.7834 | 0 | 15 | 45550.1154 | 36675.2928 | 0 | 15 | 44551.6726 |  | -1889.3881 | -1063.729 | -1887.4731 | -1011.9788 | -854.4906
x |  | VAV_DX |  | VAV_POD_2 | VAVDX | VAV_POD_2 Cooling Capacity [ton] | US_PS_VAV_POD_2 Cooling Capacity [ton] | 19.3534 | 18.3244 | 39002.4625 | 0 | 15 | 47270.8902 | 36978.2196 | 0 | 15 | 44905.6321 | 18.6162 | 18.0887 | 37552.2881 | 0 | 15 | 45576.4114 | 36514.5321 | 0 | 15 | 44363.8293 | 22.2412 | 20.7718 | 43618.1643 | 0 | 15 | 52818.5527 | 41425.9615 | 0 | 15 | 50155.8245 | 18.4688 | 18.1181 | 37262.2946 | 0 | 15 | 45237.564 | 36572.1784 | 0 | 15 | 44431.1869 | 18.4894 | 18.1201 | 37302.661 | 0 | 15 | 45284.7307 | 36576.2844 | 0 | 15 | 44435.9847 |  | -2024.2429 | -1037.756 | -2192.2028 | -690.1162 | -726.3766
x |  | VAV_DX |  | VAV_POD_3 | VAVDX | VAV_POD_3 Cooling Capacity [ton] | US_PS_VAV_POD_3 Cooling Capacity [ton] | 17.6857 | 16.5968 | 35721.6931 | 0 | 15 | 43437.4241 | 33579.4614 | 0 | 15 | 40934.3001 | 17.0455 | 16.154 | 34462.0787 | 0 | 15 | 41965.608 | 32708.1664 | 0 | 15 | 39916.2218 | 20.3933 | 19.1327 | 40861.3566 | 0 | 15 | 49470.035 | 38568.2554 | 0 | 15 | 46763.5342 | 16.9244 | 16.1545 | 34223.8746 | 0 | 15 | 41687.2747 | 32709.2628 | 0 | 15 | 39917.503 | 16.8958 | 16.0741 | 34167.5764 | 0 | 15 | 41621.4923 | 32551.0474 | 0 | 15 | 39732.6337 |  | -2142.2317 | -1753.9123 | -2293.1011 | -1514.6118 | -1616.529
x |  | VAV_DX |  | VAV_OTHER | VAVDX | VAV_OTHER Cooling Capacity [ton] | US_PS_VAV_OTHER Cooling Capacity [ton] | 26.3715 | 24.6347 | 49869.7833 | 0 | 15 | 60445.334 | 47188.86 | 0 | 15 | 57155.6481 | 25.9969 | 24.3878 | 49286.4981 | 0 | 15 | 59727.7506 | 46820.5179 | 0 | 15 | 56708.2464 | 25.9879 | 23.5162 | 49272.4638 | 0 | 15 | 59710.485 | 45520.1534 | 0 | 15 | 55128.777 | 25.4842 | 23.9792 | 48487.8623 | 0 | 15 | 58745.2332 | 46210.9651 | 0 | 15 | 55967.8618 | 25.5787 | 23.2415 | 48635.1052 | 0 | 15 | 58926.378 | 45110.3757 | 0 | 15 | 54631.0464 |  | -2680.9232 | -2465.9802 | -3752.3104 | -2276.8972 | -3524.7294
x |  | CAV_DX | lookup based on cooling tons | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Cooling Capacity [ton] | US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | 8.3841 | 8.007 | 12279.615 | 0 | 15 | 16057.341 | 11887.3057 | 0 | 15 | 15583.1503 | 8.4249 | 8.1504 | 12322.1467 | 0 | 15 | 16108.7498 | 12036.4847 | 0 | 15 | 15763.4654 | 8.4035 | 8.104 | 12299.8941 | 0 | 15 | 16081.8527 | 11988.2012 | 0 | 15 | 15705.1044 | 8.1363 | 7.8751 | 12021.8124 | 0 | 15 | 15745.7307 | 11750.0209 | 0 | 15 | 15417.2118 | 7.7875 | 7.5294 | 11658.8981 | 0 | 15 | 15307.0701 | 11390.3346 | 0 | 15 | 14982.4529 |  | -392.3092 | -285.662 | -311.6928 | -271.7915 | -268.5635
x |  | CAV_DX |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Cooling Capacity [ton] | US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | 5.284 | 5.1223 | 8822.5812 | 0 | 15 | 11919.2893 | 8685.6348 | 0 | 15 | 11741.0379 | 5.2586 | 5.0915 | 8801.0706 | 0 | 15 | 11891.2908 | 8659.5158 | 0 | 15 | 11707.0411 | 5.8861 | 5.8324 | 9332.373 | 0 | 15 | 12582.8416 | 9286.9104 | 0 | 15 | 12523.6668 | 5.2082 | 5.292 | 8758.3335 | 0 | 15 | 11835.6636 | 8829.3276 | 0 | 15 | 11928.0706 | 5.3411 | 5.318 | 8870.8728 | 0 | 15 | 11982.1464 | 8851.3029 | 0 | 15 | 11956.6739 |  | -136.9464 | -141.5548 | -45.4626 | 70.9941 | -19.57
x |  | CAV_DX |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Cooling Capacity [ton] | US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 14229.092 | 0 | 15 | 18517.8545 | 14229.092 | 0 | 15 | 18517.8545 | 10.5074 | 10.5074 | 14229.092 | 0 | 15 | 18517.8545 | 14229.092 | 0 | 15 | 18517.8545 | 10.5074 | 10.5074 | 14229.092 | 0 | 15 | 18517.8545 | 14229.092 | 0 | 15 | 18517.8545 | 10.5074 | 10.5074 | 14229.092 | 0 | 15 | 18517.8545 | 14229.092 | 0 | 15 | 18517.8545 | 10.5074 | 10.5074 | 14229.092 | 0 | 15 | 18517.8545 | 14229.092 | 0 | 15 | 18517.8545 |  | 0 | 0 | 0 | 0 | 0
x |  | Air Distribution | curve fit from Solarc cost calculations |  |  | sum of PSZ-AC:1 Supply Flow Rate [cfm] to PSZ-AC:4 Supply Flow Rate [cfm] (not the sum of the cooling capacity) |  | 32079.8432 | 30490.6832 | 547649.067 | 0 | 30 | 965832.8844 | 536961.3354 | 0 | 30 | 891462.7663 | 31401.8016 | 30172.8512 | 543088.9682 | 0 | 30 | 901552.8973 | 534823.7891 | 0 | 30 | 887942.9532 | 36508.3025 | 34601.3105 | 577432.2122 | 0 | 30 | 958104.5616 | 564606.9344 | 0 | 30 | 936985.6828 | 31147.536 | 30109.2848 | 541378.9311 | 0 | 30 | 898737.0468 | 534396.2799 | 0 | 30 | 887238.9905 | 31189.9136 | 30109.2848 | 541663.9373 | 0 | 30 | 899206.3552 | 534396.2799 | 0 | 30 | 887238.9905 |  | -10687.7315 | -8265.1791 | -12825.2779 | -6982.6513 | -7267.6575
|  | VAV_DX | Curve Fits | VAV_POD_1 | VAVDX | VAV_POD_1 Supply Flow Rate [cfm] | US_PS_VAV_POD_1 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | [8 empty] | 5593.8432 | 5445.5216 | [8 empty] | 6695.6608 | 6314.2624 | [8 empty] | 5615.032 | 5445.5216 | [8 empty] | 5572.6544 | 5445.5216
| Material | VAV_DX | Material | VAV_POD_2 | VAVDX | VAV_POD_2 Supply Flow Rate [cfm] | US_PS_VAV_POD_2 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | [8 empty] | 5593.8432 | 5424.3328 | [8 empty] | 6674.472 | 6229.5072 | [8 empty] | 5551.4656 | 5445.5216 | [8 empty] | 5551.4656 | 5445.5216
| y = 0.7194x + 28317 | VAV_DX | y = 0.7194x + 28317 | VAV_POD_3 | VAVDX | VAV_POD_3 Supply Flow Rate [cfm] | US_PS_VAV_POD_3 Supply Flow Rate [cfm] | 5297.2 | 4979.368 | [8 empty] | 5106.5008 | 4852.2352 | [8 empty] | 6123.5632 | 5742.1648 | [8 empty] | 5085.312 | 4852.2352 | [8 empty] | 5064.1232 | 4831.0464
| R² = 0.8831 | VAV_DX | R² = 0.8831 | VAV_OTHER | VAVDX | VAV_OTHER Supply Flow Rate [cfm] | US_PS_VAV_OTHER Supply Flow Rate [cfm] | 7903.4224 | 7394.8912 | [8 empty] | 7797.4784 | 7310.136 | [8 empty] | 9174.7504 | 8623.8416 | [8 empty] | 7649.1568 | 7204.192 | [8 empty] | 7670.3456 | 7183.0032
| Labor | CAV_DX | Labor | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Supply Flow Rate [cfm] | US_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | [8 empty] | 2585.0336 | 2457.9008 | [8 empty] | 2881.6768 | 2754.544 | [8 empty] | 2521.4672 | 2415.5232 | [8 empty] | 2563.8448 | 2457.9008
| y = 2.3902x + 122683 | CAV_DX | y = 2.3902x + 122683 | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Supply Flow Rate [cfm] | US_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1546.7824 | [8 empty] | 1567.9712 | 1525.5936 | [8 empty] | 1801.048 | 1779.8592 | [8 empty] | 1567.9712 | 1589.16 | [8 empty] | 1610.3488 | 1589.16
| R² = 0.9806 | CAV_DX | R² = 0.9806 | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Supply Flow Rate [cfm] | US_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | [8 empty] | 3157.1312 | 3157.1312 | [8 empty] | 3157.1312 | 3157.1312 | [8 empty] | 3157.1312 | 3157.1312 | [8 empty] | 3157.1312 | 3157.1312
| 90.1-2016ap SAT reset only 0A, 1A, 3A MZ systems only <3000 cfm design OA is exempt | Material cost = 4E-07x2 + 0.0307x + 1618 Labor hours = 0.0054x + 3.6055 | lookup cost based on supply airflow, cfm new for 2019, thus base code = 0 costs
x |  | SAT_reset_16ap |  | VAV_POD_1 | VAVDX | VAV_POD_1 Supply Flow Rate [cfm] | US_PS_VAV_POD_1 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5593.8432 | 5445.5216 | 0 | 0 |  | 0 | 2853.766 | 0 | 20 | 3189.9193 | 6695.6608 | 6314.2624 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5615.032 | 5445.5216 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5572.6544 | 5445.5216 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
x |  | SAT_reset_16ap |  | VAV_POD_2 | VAVDX | VAV_POD_2 Supply Flow Rate [cfm] | US_PS_VAV_POD_2 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5593.8432 | 5424.3328 | 0 | 0 |  | 0 | 2852.35 | 0 | 20 | 3188.1857 | 6674.472 | 6229.5072 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5551.4656 | 5445.5216 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5551.4656 | 5445.5216 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
x |  | SAT_reset_16ap |  | VAV_POD_3 | VAVDX | VAV_POD_3 Supply Flow Rate [cfm] | US_PS_VAV_POD_3 Supply Flow Rate [cfm] | 5297.2 | 4979.368 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5106.5008 | 4852.2352 | 0 | 0 |  | 0 | 2814.3273 | 0 | 20 | 3141.6088 | 6123.5632 | 5742.1648 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5085.312 | 4852.2352 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 5064.1232 | 4831.0464 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
x |  | SAT_reset_16ap |  | VAV_OTHER | VAVDX | VAV_OTHER Supply Flow Rate [cfm] | US_PS_VAV_OTHER Supply Flow Rate [cfm] | 7903.4224 | 7394.8912 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 7797.4784 | 7310.136 | 0 | 0 |  | 0 | 2980.5485 | 0 | 20 | 3344.8676 | 9174.7504 | 8623.8416 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 7649.1568 | 7204.192 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0 | 7670.3456 | 7183.0032 | 0 | 0 |  | 0 | 0 | 0 | 20 | 0
0 | 90.1-10au | VAV_AHU | If PH coil = NO, then increase | VAV_POD_1 | VAVDX | VAV_POD_1 Preheat Coil | US_PS_VAV_POD_1 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | VAV_AHU | duct cost by | VAV_POD_2 | VAVDX | VAV_POD_2 Preheat Coil | US_PS_VAV_POD_2 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | YES | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | VAV_AHU | 2.75% | VAV_POD_3 | VAVDX | VAV_POD_3 Preheat Coil | US_PS_VAV_POD_3 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | VAV_AHU |  | VAV_OTHER | VAVDX | VAV_OTHER Preheat Coil | US_PS_VAV_OTHER Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | CAV_DX |  | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Preheat Coil | US_PS_PSZ-AC_1:6 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | CAV_DX |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Preheat Coil | US_PS_PSZ-AC_2:5 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
0 |  | CAV_DX |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Preheat Coil | US_PS_PSZ-AC_2:7 Preheat Coil | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | N/A | REF!! | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0
| 90.1-10aq for DX single zone |  |  |  |  | Cost for 2 stage fan and added cooling stage applies if single zone DX system Cooling Capacity [ton] above 5.4167 tons, prototype value shown as "yes" if so, or "no" if not. | If applicable, add the fan and staging cost together for the target code; For units greater than 110 MBH (9.167 tons) include fan control only in the base case.
0 |  |  | Capacity check & Select | PSZ-AC_1:6 | CAVDX |  |  | No | Yes | 0 | 0 | 0 | 0 | 921.6079 | 0 | 15 | 1013.7686 | No | Yes | 0 | 0 | 0 | 0 | 933.8253 | 0 | 15 | 1027.2078 | No | Yes | 0 | 0 | 0 | 0 | 929.871 | 0 | 15 | 1022.8581 | No | Yes | 0 | 0 | 0 | 0 | 910.3645 | 0 | 15 | 1001.401 | No | Yes | 0 | 0 | 0 | 0 | 880.907 | 0 | 15 | 968.9977
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Cooling Capacity [ton] | US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | 8.3841 | 8.007 | 385.5034 | 0 | 15 | 424.0537 | 381.8969 | 0 | 15 | 420.0866 | 8.4249 | 8.1504 | 385.8944 | 0 | 15 | 346.3576 | 383.2683 | 0 | 15 | 421.5951 | 8.4035 | 8.104 | 385.6898 | 0 | 15 | 424.2588 | 382.8244 | 0 | 15 | 421.1069 | 8.1363 | 7.8751 | 383.1334 | 0 | 15 | 421.4468 | 380.6349 | 0 | 15 | 418.6984 | 7.7875 | 7.5294 | 379.7972 | 0 | 15 | 417.7769 | 377.3283 | 0 | 15 | 415.0611
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Cooling Capacity [ton] | US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | 8.3841 | 8.007 | 568.2337 | 0 | 15 | 625.0571 | 539.7109 | 0 | 15 | 593.682 | 8.4249 | 8.1504 | 571.326 | 0 | 15 | 628.4586 | 550.557 | 0 | 15 | 605.6127 | 8.4035 | 8.104 | 569.7081 | 0 | 15 | 626.6789 | 547.0465 | 0 | 15 | 601.7512 | 8.1363 | 7.8751 | 549.4902 | 0 | 15 | 604.4392 | 529.7297 | 0 | 15 | 582.7026 | 7.7875 | 7.5294 | 523.1046 | 0 | 15 | 575.4151 | 503.5787 | 0 | 15 | 553.9366
0 |  |  | Capacity check & Select | PSZ-AC_2:5 | CAVDX |  |  | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Yes | 0 | 0 | 0 | 0 | 736.2903 | 0 | 15 | 809.9194 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Cooling Capacity [ton] | US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | 5.284 | 5.1223 | 355.8499 | 0 | 15 | 391.4349 | 354.3029 | 0 | 15 | 389.7331 | 5.2586 | 5.0915 | 355.6069 | 0 | 15 | 346.3576 | 354.0078 | 0 | 15 | 389.4086 | 5.8861 | 5.8324 | 361.6089 | 0 | 15 | 397.7697 | 361.0953 | 0 | 15 | 397.2048 | 5.2082 | 5.292 | 355.1241 | 0 | 15 | 390.6365 | 355.9261 | 0 | 15 | 391.5187 | 5.3411 | 5.318 | 356.3954 | 0 | 15 | 392.035 | 356.1744 | 0 | 15 | 391.7918
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Cooling Capacity [ton] | US_PS_PSZ-AC_2:5 Cooling Capacity [ton] | 5.284 | 5.1223 | 333.7104 | 0 | 15 | 367.0814 | 321.4752 | 0 | 15 | 353.6227 | 5.2586 | 5.0915 | 331.7886 | 0 | 15 | 364.9674 | 319.1416 | 0 | 15 | 351.0558 | 5.8861 | 5.8324 | 379.2568 | 0 | 15 | 417.1825 | 375.1951 | 0 | 15 | 412.7146 | 5.2082 | 5.292 | 327.9703 | 0 | 15 | 360.7673 | 334.3131 | 0 | 15 | 367.7445 | 5.3411 | 5.318 | 338.0249 | 0 | 15 | 371.8274 | 336.2765 | 0 | 15 | 369.9041
0 |  |  | Capacity check & Select | PSZ-AC_2:7 | CAVDX |  |  | Yes | Yes | 405.8142 | 0 | 15 | 446.3956 | 1134.6818 | 0 | 15 | 1248.15 | Yes | Yes | 405.8142 | 0 | 15 | 346.3576 | 1134.6818 | 0 | 15 | 1248.15 | Yes | Yes | 405.8142 | 0 | 15 | 446.3956 | 1134.6818 | 0 | 15 | 1248.15 | Yes | Yes | 405.8142 | 0 | 15 | 446.3956 | 1134.6818 | 0 | 15 | 1248.15 | Yes | Yes | 405.8142 | 0 | 15 | 446.3956 | 1134.6818 | 0 | 15 | 1248.15
| Upgrade to 2-speed fan |  | curve fit from AHRI cost survey | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Cooling Capacity [ton] | US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 405.8142 | 0 | 15 | 446.3956 | 405.8142 | 0 | 15 | 446.3956 | 10.5074 | 10.5074 | 405.8142 | 0 | 15 | 346.3576 | 405.8142 | 0 | 15 | 446.3956 | 10.5074 | 10.5074 | 405.8142 | 0 | 15 | 446.3956 | 405.8142 | 0 | 15 | 446.3956 | 10.5074 | 10.5074 | 405.8142 | 0 | 15 | 446.3956 | 405.8142 | 0 | 15 | 446.3956 | 10.5074 | 10.5074 | 405.8142 | 0 | 15 | 446.3956 | 405.8142 | 0 | 15 | 446.3956
| Add one stage of cooling |  | curve fit from AHRI cost survey | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Cooling Capacity [ton] | US_PS_PSZ-AC_2:7 Cooling Capacity [ton] | 10.5074 | 10.5074 | 728.8676 | 0 | 15 | 801.7544 | 728.8676 | 0 | 15 | 801.7544 | 10.5074 | 10.5074 | 728.8676 | 0 | 15 | 801.7544 | 728.8676 | 0 | 15 | 801.7544 | 10.5074 | 10.5074 | 728.8676 | 0 | 15 | 801.7544 | 728.8676 | 0 | 15 | 801.7544 | 10.5074 | 10.5074 | 728.8676 | 0 | 15 | 801.7544 | 728.8676 | 0 | 15 | 801.7544 | 10.5074 | 10.5074 | 728.8676 | 0 | 15 | 801.7544 | 728.8676 | 0 | 15 | 801.7544
| 90.1-10aq for multiple zone with variable airflow |  |  |  |  | Cost for added cooling stage applies if DX system with varied airflow and Cooling Capacity [ton] above 5.4167 tons, prototype value shown as "yes" if so, or "no" if not. | If applicable, add staging cost for the target code; Note - these units require variable speed fans and the difference based on fan motor HP is covered in the next item.
0 |  |  | Capacity check | VAV_POD_1 | VAVDX |  |  | NA | Yes | 0 | 0 | 0 | 0 | 1324.212 | 0 | 0 | 1456.6332 | NA | Yes | 0 | 0 | 0 | 0 | 1305.0916 | 0 | 0 | 1435.6008 | NA | Yes | 0 | 0 | 0 | 0 | 1526.599 | 0 | 0 | 1679.2589 | NA | Yes | 0 | 0 | 0 | 0 | 1308.6208 | 0 | 0 | 1439.4828 | NA | Yes | 0 | 0 | 0 | 0 | 1308.598 | 0 | 0 | 1439.4577
| Add one stage of cooling |  | curve fit from AHRI cost survey | VAV_POD_1 | VAVDX | VAV_POD_1 Cooling Capacity [ton] | US_PS_VAV_POD_1 Cooling Capacity [ton] | 19.3372 | 18.3769 | 1396.867 | 0 | 15 | 1536.5537 | 1324.212 | 0 | 15 | 1456.6332 | 18.6648 | 18.1241 | 1345.9965 | 0 | 15 | 1480.5962 | 1305.0916 | 0 | 15 | 1435.6008 | 22.3173 | 21.0521 | 1622.3145 | 0 | 15 | 1784.5459 | 1526.599 | 0 | 15 | 1679.2589 | 18.6852 | 18.1708 | 1347.5357 | 0 | 15 | 1482.2892 | 1308.6208 | 0 | 15 | 1439.4828 | 18.6048 | 18.1705 | 1341.4568 | 0 | 15 | 1475.6024 | 1308.598 | 0 | 15 | 1439.4577
0 |  |  | Capacity check | VAV_POD_2 | VAVDX |  |  | NA | Yes | 0 | 0 | 0 | 0 | 1320.2468 | 0 | 0 | 1452.2715 | NA | Yes | 0 | 0 | 0 | 0 | 1302.416 | 0 | 0 | 1432.6576 | NA | Yes | 0 | 0 | 0 | 0 | 1505.3933 | 0 | 0 | 1655.9327 | NA | Yes | 0 | 0 | 0 | 0 | 1304.6328 | 0 | 0 | 1435.096 | NA | Yes | 0 | 0 | 0 | 0 | 1304.7907 | 0 | 0 | 1435.2697
| Add one stage of cooling |  | curve fit from AHRI cost survey | VAV_POD_2 | VAVDX | VAV_POD_2 Cooling Capacity [ton] | US_PS_VAV_POD_2 Cooling Capacity [ton] | 19.3534 | 18.3244 | 1398.0876 | 0 | 15 | 1537.8963 | 1320.2468 | 0 | 15 | 1452.2715 | 18.6162 | 18.0887 | 1342.3222 | 0 | 15 | 1476.5544 | 1302.416 | 0 | 15 | 1432.6576 | 22.2412 | 20.7718 | 1616.5619 | 0 | 15 | 1778.2181 | 1505.3933 | 0 | 15 | 1655.9327 | 18.4688 | 18.1181 | 1331.1707 | 0 | 15 | 1464.2878 | 1304.6328 | 0 | 15 | 1435.096 | 18.4894 | 18.1201 | 1332.7229 | 0 | 15 | 1465.9952 | 1304.7907 | 0 | 15 | 1435.2697
0 |  |  | Capacity check | VAV_POD_3 | VAVDX |  |  | NA | Yes | 0 | 0 | 0 | 0 | 1189.55 | 0 | 0 | 1308.505 | NA | Yes | 0 | 0 | 0 | 0 | 1156.045 | 0 | 0 | 1271.6495 | NA | Yes | 0 | 0 | 0 | 0 | 1381.3905 | 0 | 0 | 1519.5295 | NA | Yes | 0 | 0 | 0 | 0 | 1156.0871 | 0 | 0 | 1271.6959 | NA | Yes | 0 | 0 | 0 | 0 | 1150.0031 | 0 | 0 | 1265.0034
| Add one stage of cooling |  | curve fit from AHRI cost survey | VAV_POD_3 | VAVDX | VAV_POD_3 Cooling Capacity [ton] | US_PS_VAV_POD_3 Cooling Capacity [ton] | 17.6857 | 16.5968 | 1271.928 | 0 | 15 | 1399.1208 | 1189.55 | 0 | 15 | 1308.505 | 17.0455 | 16.154 | 1223.4904 | 0 | 15 | 1345.8394 | 1156.045 | 0 | 15 | 1271.6495 | 20.3933 | 19.1327 | 1476.7617 | 0 | 15 | 1624.4379 | 1381.3905 | 0 | 15 | 1519.5295 | 16.9244 | 16.1545 | 1214.3304 | 0 | 15 | 1335.7635 | 1156.0871 | 0 | 15 | 1271.6959 | 16.8958 | 16.0741 | 1212.1655 | 0 | 15 | 1333.3821 | 1150.0031 | 0 | 15 | 1265.0034
0 |  |  | Capacity check | VAV_OTHER | VAVDX |  |  | NA | Yes | 0 | 0 | 0 | 0 | 1797.6351 | 0 | 0 | 1977.3986 | NA | Yes | 0 | 0 | 0 | 0 | 1778.9561 | 0 | 0 | 1956.8517 | NA | Yes | 0 | 0 | 0 | 0 | 1713.0135 | 0 | 0 | 1884.3148 | NA | Yes | 0 | 0 | 0 | 0 | 1748.0452 | 0 | 0 | 1922.8497 | NA | Yes | 0 | 0 | 0 | 0 | 1692.2333 | 0 | 0 | 1861.4566
| Add one stage of cooling |  | curve fit from AHRI cost survey | VAV_OTHER | VAVDX | VAV_OTHER Cooling Capacity [ton] | US_PS_VAV_OTHER Cooling Capacity [ton] | 26.3715 | 24.6347 | 1929.0215 | 0 | 15 | 2121.9237 | 1797.6351 | 0 | 15 | 1977.3986 | 25.9969 | 24.3878 | 1900.6893 | 0 | 15 | 2090.7583 | 1778.9561 | 0 | 15 | 1956.8517 | 25.9879 | 23.5162 | 1900.0076 | 0 | 15 | 2090.0084 | 1713.0135 | 0 | 15 | 1884.3148 | 25.4842 | 23.9792 | 1861.8968 | 0 | 15 | 2048.0865 | 1748.0452 | 0 | 15 | 1922.8497 | 25.5787 | 23.2415 | 1869.0489 | 0 | 15 | 2055.9538 | 1692.2333 | 0 | 15 | 1861.4566
| Variation in VFD size and requirements based on load changes | VFD_Size | If VFD required, VFD cost applied, interpolated on VFD_Size costs based on fan bhp *1.1. Note that values in prototype data are 1.1 times the prototype data
x |  | VFD_Size | system cost | VAV_OTHER | VAVDX | VAV_OTHER Fan Power [hp] | US_PS_VAV_OTHER Fan Power [hp] | 12.7452 | 11.9059 | 4468.1965 | 0 | 15 | 5984.9215 | 4275.8215 | 0 | 15 | 5734.4684 | 12.5642 | 11.7865 | 4426.7124 | 0 | 15 | 5930.9134 | 4248.4697 | 0 | 15 | 5698.8591 | 14.769 | 13.8999 | 4932.0399 | 0 | 15 | 6588.7997 | 4732.8558 | 0 | 15 | 6329.4817 | 12.3164 | 11.5891 | 4369.9128 | 0 | 15 | 5856.9659 | 4203.2126 | 0 | 15 | 5639.9388 | 12.3621 | 11.561 | 4380.3835 | 0 | 15 | 5870.5978 | 4196.7753 | 0 | 15 | 5631.5581 |  | -192.375 | -178.2427 | -199.1842 | -166.7002 | -183.6082
x |  | VFD_Size | system cost | VAV_POD_3 | VAVDX | VAV_POD_3 Fan Power [hp] | US_PS_VAV_POD_3 Fan Power [hp] | 8.6127 | 8.0824 | 3596.9197 | 0 | 15 | 4856.9765 | 3504.3863 | 0 | 15 | 4738.9424 | 8.3009 | 7.8667 | 3542.5111 | 0 | 15 | 4787.5739 | 3466.7505 | 0 | 15 | 4690.9349 | 9.9312 | 9.3173 | 3827.0047 | 0 | 15 | 5150.4693 | 3719.8762 | 0 | 15 | 5013.818 | 8.2419 | 7.867 | 3532.2199 | 0 | 15 | 4774.4466 | 3466.7968 | 0 | 15 | 4690.994 | 8.228 | 7.8278 | 3529.79 | 0 | 15 | 4771.347 | 3459.9626 | 0 | 15 | 4682.2764 |  | -92.5334 | -75.7606 | -107.1285 | -65.4231 | -69.8273
x |  | VFD_Size | system cost | VAV_POD_2 | VAVDX | VAV_POD_2 Fan Power [hp] | US_PS_VAV_POD_2 Fan Power [hp] | 9.4248 | 8.9237 | 3738.6311 | 0 | 15 | 5037.7413 | 3651.1944 | 0 | 15 | 4926.2085 | 9.0658 | 8.8089 | 3675.9906 | 0 | 15 | 4957.8381 | 3631.1654 | 0 | 15 | 4900.6598 | 10.8311 | 10.1155 | 4029.5003 | 0 | 15 | 5413.7827 | 3865.4846 | 0 | 15 | 5200.2505 | 8.994 | 8.8232 | 3663.465 | 0 | 15 | 4941.8608 | 3633.6571 | 0 | 15 | 4903.8382 | 9.004 | 8.8242 | 3665.2077 | 0 | 15 | 4944.0837 | 3633.8321 | 0 | 15 | 4904.0615 |  | -87.4367 | -44.8252 | -164.0157 | -29.808 | -31.3756
x |  | VFD_Size | system cost | VAV_POD_1 | VAVDX | VAV_POD_1 Fan Power [hp] | US_PS_VAV_POD_1 Fan Power [hp] | 9.4169 | 8.9493 | 3737.2616 | 0 | 15 | 5035.9945 | 3655.6501 | 0 | 15 | 4931.8922 | 9.0895 | 8.8262 | 3680.1194 | 0 | 15 | 4963.1048 | 3634.1719 | 0 | 15 | 4904.4949 | 10.8682 | 10.252 | 4037.9865 | 0 | 15 | 5424.8308 | 3896.7717 | 0 | 15 | 5240.9833 | 9.0994 | 8.8489 | 3681.8492 | 0 | 15 | 4965.3113 | 3638.136 | 0 | 15 | 4909.5514 | 9.0603 | 8.8487 | 3675.0201 | 0 | 15 | 4956.6003 | 3638.1103 | 0 | 15 | 4909.5186 |  | -81.6115 | -45.9475 | -141.2147 | -43.7132 | -36.9099
No diff for 2010-13 so HIDE | 90.1-07bh | Supply_Air_Temp_Reset | apply cost if "yes" unless check *IF(Base_Code = "2009", "0","1") |  |  | [Yes, No] are parameter values
Not in 2013 |  | Supply_Air_Temp_Reset |  | VAV_POD_1 | VAVDX | Supply Air Temp. Reset Flag | US_PS_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734
Not in 2013 |  | Supply_Air_Temp_Reset |  | VAV_POD_2 | VAVDX | Supply Air Temp. Reset Flag | US_PS_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734
Not in 2013 |  | Supply_Air_Temp_Reset |  | VAV_POD_3 | VAVDX | Supply Air Temp. Reset Flag | US_PS_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734
Not in 2013 |  | Supply_Air_Temp_Reset |  | VAV_OTHER | VAVDX | Supply Air Temp. Reset Flag | US_PS_Supply Air Temp. Reset Flag | No | No |  |  |  |  | 0 | 0 | 0 | 0 | No | No |  |  |  |  | 0 | 0 | 0 | 0 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734 | Yes | Yes |  |  |  |  | 18734 | 0 | 20 | 18734
| 90.1-07ck | Vent_Optimize | apply cost if "Yes", cost value times number of perimeter zones Number of perimeter zones is hard coded |  |  | [Yes, No] are parameter values
Not in 2013 |  | Vent_Optimize |  | VAV_POD_1 | VAVDX | Ventilation Reset Flag add_ck_vav_pod_1 | US_PS_Ventilation Reset Flag add_ck_vav_pod_1 | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  | Vent_Optimize |  | VAV_POD_1 | VAVDX | Number of perimeter zones (hard coded - doesn't change) |  | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0
Not in 2013 |  | Vent_Optimize |  | VAV_POD_2 | VAVDX | Ventilation Reset Flag add_ck_vav_pod_2 | US_PS_Ventilation Reset Flag add_ck_vav_pod_2 | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  | Vent_Optimize |  | VAV_POD_2 | VAVDX | Number of perimeter zones (hard coded - doesn't change) |  | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0
Not in 2013 |  | Vent_Optimize |  | VAV_POD_3 | VAVDX | Ventilation Reset Flag add_ck_vav_pod_3 | US_PS_Ventilation Reset Flag add_ck_vav_pod_3 | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  | Vent_Optimize |  | VAV_POD_3 | VAVDX | Number of perimeter zones (hard coded - doesn't change) |  | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0 | 8 | 8 |  |  |  |  | 982.744 | 0 | 0 | 0
Not in 2013 |  | Vent_Optimize |  | VAV_OTHER | VAVDX | Ventilation Reset Flag add_ck_vav_other | US_PS_Ventilation Reset Flag add_ck_vav_other | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  |  |  |  | #N/A | #N/A | #N/A | #N/A
|  | Vent_Optimize |  | VAV_OTHER | VAVDX | Number of perimeter zones (hard coded - doesn't change) |  | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0 | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0 | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0 | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0 | 4 | 4 |  |  |  |  | 491.372 | 0 | 0 | 0
Not in 2013 | IECC VAV fan control | VAV_fan_control | apply cost if supply fan power is 4.5 to under 6.75 bhp - incremental cost for target code only. Include flag - *=IF(Base_Code = "2009", "0","1") Could just apply cost of 7.5 hp VFD if it applies, no need for interpolation.
|  |  |  | VAV_POD_1 | VAVDX | VAV_POD_1 Fan Power [hp] | US_PS_VAV_POD_1 Fan Power [hp] | 8.5609 | 8.1357 | [8 empty] | 8.2632 | 8.0238 | [8 empty] | 9.8802 | 9.32 | [8 empty] | 8.2722 | 8.0444 | [8 empty] | 8.2366 | 8.0443
|  |  |  | VAV_POD_2 | VAVDX | VAV_POD_2 Fan Power [hp] | US_PS_VAV_POD_2 Fan Power [hp] | 8.568 | 8.1125 | [8 empty] | 8.2417 | 8.0081 | [8 empty] | 9.8465 | 9.1959 | [8 empty] | 8.1764 | 8.0211 | [8 empty] | 8.1855 | 8.022
|  |  |  | VAV_POD_3 | VAVDX | VAV_POD_3 Fan Power [hp] | US_PS_VAV_POD_3 Fan Power [hp] | 7.8297 | 7.3476 | [8 empty] | 7.5463 | 7.1516 | [8 empty] | 9.0284 | 8.4703 | [8 empty] | 7.4927 | 7.1518 | [8 empty] | 7.48 | 7.1162
|  |  |  | VAV_OTHER | VAVDX | VAV_OTHER Fan Power [hp] | US_PS_VAV_OTHER Fan Power [hp] | 11.5866 | 10.8235 | [8 empty] | 11.422 | 10.715 | [8 empty] | 13.4264 | 12.6363 | [8 empty] | 11.1967 | 10.5355 | [8 empty] | 11.2382 | 10.51
HIDE; no diff in 2010-2013 requirement; difference in size not warrant cost adjustment for OA dampers | 90.1-07cb | Outdoor_Air_Dampers | Use the upper rows for gravity dampers if value is "gravity", cost is 0. If "motorized, cost is difference between motorized and gravity. If system has an economizer, then there is no added cost for a motorized damper vs. a gravity damper and value is set to $0,
Not in 2013 |  | Outdoor_Air_Dampers | system cost | VAV_POD_1 | VAVDX | VAV_POD_1 OA Damper [gravity, motorized] | US_PS_VAV_POD_1 OA Damper [gravity, motorized] | motorized | motorized | 431.9197 | 0 | 20 | 420.1868 | 539.1236 | 0 | 20 | 602.8945 | motorized | motorized | 439.4704 | 0 | 20 | 431.9422 | 541.6801 | 0 | 20 | 607.0864 | motorized | motorized | 398.8409 | 0 | 20 | 368.6883 | 513.2515 | 0 | 20 | 560.4714 | motorized | motorized | 439.1577 | 0 | 20 | 431.4554 | 541.2081 | 0 | 20 | 606.3124 | motorized | motorized | 440.088 | 0 | 20 | 432.9038 | 541.2109 | 0 | 20 | 606.3171
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_POD_1 OA Rate [cfm] | US_PS_VAV_POD_1 OA Rate [cfm] | 5802.786 | 5514.5971 | 902.4496 | 144.0463 | 20 | 1046.8808 | 923.6154 | 142.7518 | 20 | 1153.8182 | 5598.6531 | 5438.7412 | 871.5207 | 143.1294 | 20 | 1007.7606 | 911.4137 | 142.4111 | 20 | 1137.5091 | 6697.0593 | 6282.2673 | 1037.9441 | 148.0633 | 20 | 1218.26 | 1047.0971 | 146.2001 | 20 | 1318.8684 | 5607.1074 | 5452.747 | 872.8017 | 143.1674 | 20 | 1009.3808 | 913.6666 | 142.474 | 20 | 1140.5203 | 5581.9563 | 5452.6622 | 868.9909 | 143.0544 | 20 | 1004.5608 | 913.653 | 142.4736 | 20 | 1140.5021
|  | Outdoor_Air_Dampers_Motorized | item cost | VAV_POD_1 | VAVDX | VAV_POD_1 OA Rate [cfm] | US_PS_VAV_POD_1 OA Rate [cfm] | 5802.786 | 5514.5971 | 1334.3693 | 144.0463 | 20 | 1467.0676 | 1462.739 | 142.7518 | 20 | 1756.7127 | 5598.6531 | 5438.7412 | 1310.9912 | 143.1294 | 20 | 1439.7029 | 1453.0938 | 142.4111 | 20 | 1744.5955 | 6697.0593 | 6282.2673 | 1436.785 | 148.0633 | 20 | 1586.9483 | 1560.3486 | 146.2001 | 20 | 1879.3398 | 5607.1074 | 5452.747 | 1311.9594 | 143.1674 | 20 | 1440.8362 | 1454.8747 | 142.474 | 20 | 1746.8328 | 5581.9563 | 5452.6622 | 1309.079 | 143.0544 | 20 | 1437.4646 | 1454.8639 | 142.4736 | 20 | 1746.8192
Not in 2013 |  | Outdoor_Air_Dampers | system cost | VAV_POD_2 | VAVDX | VAV_POD_2 OA Damper [gravity, motorized] | US_PS_VAV_POD_2 OA Damper [gravity, motorized] | motorized | motorized | 431.7417 | 0 | 20 | 419.9098 | 539.6542 | 0 | 20 | 603.7645 | motorized | motorized | 439.9924 | 0 | 20 | 432.7549 | 542.0379 | 0 | 20 | 607.6731 | motorized | motorized | 399.801 | 0 | 20 | 370.183 | 514.9026 | 0 | 20 | 563.1786 | motorized | motorized | 441.5592 | 0 | 20 | 435.1941 | 541.7415 | 0 | 20 | 607.1871 | motorized | motorized | 441.3311 | 0 | 20 | 434.839 | 541.7201 | 0 | 20 | 607.152
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_POD_2 OA Rate [cfm] | US_PS_VAV_POD_2 OA Rate [cfm] | 5807.5958 | 5498.8538 | 903.1784 | 144.0679 | 20 | 1047.8026 | 921.083 | 142.6811 | 20 | 1150.4334 | 5584.5413 | 5428.1256 | 869.3826 | 143.066 | 20 | 1005.0562 | 909.7062 | 142.3634 | 20 | 1135.2267 | 6671.103 | 6233.2788 | 1034.0113 | 147.9467 | 20 | 1213.2857 | 1039.2171 | 145.9801 | 20 | 1308.3358 | 5542.1849 | 5436.919 | 862.965 | 142.8757 | 20 | 996.939 | 911.1206 | 142.4029 | 20 | 1137.1173 | 5548.3509 | 5437.5546 | 863.8993 | 142.9034 | 20 | 998.1207 | 911.2229 | 142.4058 | 20 | 1137.254
|  | Outdoor_Air_Dampers_Motorized | item cost | VAV_POD_2 | VAVDX | VAV_POD_2 OA Rate [cfm] | US_PS_VAV_POD_2 OA Rate [cfm] | 5807.5958 | 5498.8538 | 1334.9201 | 144.0679 | 20 | 1467.7124 | 1460.7372 | 142.6811 | 20 | 1754.1978 | 5584.5413 | 5428.1256 | 1309.375 | 143.066 | 20 | 1437.8111 | 1451.7441 | 142.3634 | 20 | 1742.8998 | 6671.103 | 6233.2788 | 1433.8124 | 147.9467 | 20 | 1583.4687 | 1554.1197 | 145.9801 | 20 | 1871.5144 | 5542.1849 | 5436.919 | 1304.5242 | 142.8757 | 20 | 1432.1331 | 1452.8621 | 142.4029 | 20 | 1744.3044 | 5548.3509 | 5437.5546 | 1305.2303 | 142.9034 | 20 | 1432.9597 | 1452.943 | 142.4058 | 20 | 1744.406
Not in 2013 |  | Outdoor_Air_Dampers | system cost | VAV_POD_3 | VAVDX | VAV_POD_3 OA Damper [gravity, motorized] | US_PS_VAV_POD_3 OA Damper [gravity, motorized] | motorized | motorized | 450.3467 | 0 | 20 | 448.875 | 557.1255 | 0 | 20 | 632.4126 | motorized | motorized | 457.4539 | 0 | 20 | 459.9398 | 561.6051 | 0 | 20 | 639.7579 | motorized | motorized | 420.1969 | 0 | 20 | 401.9363 | 542.2442 | 0 | 20 | 608.0115 | motorized | motorized | 458.7016 | 0 | 20 | 461.8823 | 561.5994 | 0 | 20 | 639.7485 | motorized | motorized | 459.0198 | 0 | 20 | 462.3777 | 562.4127 | 0 | 20 | 641.0822
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_POD_3 OA Rate [cfm] | US_PS_VAV_POD_3 OA Rate [cfm] | 5304.6161 | 4980.4486 | 826.9702 | 141.8086 | 20 | 951.4112 | 837.6962 | 140.3525 | 20 | 1038.9755 | 5112.476 | 4847.5313 | 797.8583 | 140.9455 | 20 | 914.5893 | 816.3161 | 139.7554 | 20 | 1010.3981 | 6119.7068 | 5422.002 | 950.4674 | 145.4699 | 20 | 1107.6158 | 908.7212 | 142.3359 | 20 | 1133.9101 | 5078.7435 | 4847.7008 | 792.7474 | 140.794 | 20 | 908.1248 | 816.3434 | 139.7562 | 20 | 1010.4345 | 5070.1408 | 4823.5668 | 791.444 | 140.7554 | 20 | 906.4761 | 812.4614 | 139.6478 | 20 | 1005.2457
|  | Outdoor_Air_Dampers_Motorized | item cost | VAV_POD_3 | VAVDX | VAV_POD_3 OA Rate [cfm] | US_PS_VAV_POD_3 OA Rate [cfm] | 5304.6161 | 4980.4486 | 1277.3169 | 141.8086 | 20 | 1400.2861 | 1394.8217 | 140.3525 | 20 | 1671.3881 | 5112.476 | 4847.5313 | 1255.3122 | 140.9455 | 20 | 1374.5291 | 1377.9212 | 139.7554 | 20 | 1650.156 | 6119.7068 | 5422.002 | 1370.6643 | 145.4699 | 20 | 1509.552 | 1450.9655 | 142.3359 | 20 | 1741.9216 | 5078.7435 | 4847.7008 | 1251.449 | 140.794 | 20 | 1370.0071 | 1377.9428 | 139.7562 | 20 | 1650.1831 | 5070.1408 | 4823.5668 | 1250.4638 | 140.7554 | 20 | 1368.8539 | 1374.8741 | 139.6478 | 20 | 1646.3279
Not in 2013 |  | Outdoor_Air_Dampers | system cost | VAV_OTHER | VAVDX | VAV_OTHER OA Damper [gravity, motorized] | US_PS_VAV_OTHER OA Damper [gravity, motorized] | motorized | motorized | 504.1965 | 0 | 20 | 535.8315 | 605.3225 | 0 | 20 | 723.1089 | motorized | motorized | 504.1965 | 0 | 20 | 535.8315 | 605.3225 | 0 | 20 | 723.1089 | motorized | motorized | 504.1965 | 0 | 20 | 535.8315 | 605.3225 | 0 | 20 | 723.1089 | motorized | motorized | 504.1965 | 0 | 20 | 535.8315 | 605.3225 | 0 | 20 | 723.1089 | motorized | motorized | 504.1965 | 0 | 20 | 535.8315 | 605.3225 | 0 | 20 | 723.1089
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | VAV_OTHER OA Rate [cfm] | US_PS_VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 597.1902 | 132.3932 | 20 | 660.6816 | 549.3255 | 122.323 | 20 | 653.502 | 3736.1787 | 2988.8921 | 597.1902 | 132.3932 | 20 | 660.6816 | 549.3255 | 122.323 | 20 | 653.502 | 3736.1787 | 2988.8921 | 597.1902 | 132.3932 | 20 | 660.6816 | 549.3255 | 122.323 | 20 | 653.502 | 3736.1787 | 2988.8921 | 597.1902 | 132.3932 | 20 | 660.6816 | 549.3255 | 122.323 | 20 | 653.502 | 3736.1787 | 2988.8921 | 597.1902 | 132.3932 | 20 | 660.6816 | 549.3255 | 122.323 | 20 | 653.502
|  | Outdoor_Air_Dampers_Motorized | item cost | VAV_OTHER | VAVDX | VAV_OTHER OA Rate [cfm] | US_PS_VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 1101.3867 | 132.3932 | 20 | 1196.513 | 1154.6481 | 122.323 | 20 | 1376.611 | 3736.1787 | 2988.8921 | 1101.3867 | 132.3932 | 20 | 1196.513 | 1154.6481 | 122.323 | 20 | 1376.611 | 3736.1787 | 2988.8921 | 1101.3867 | 132.3932 | 20 | 1196.513 | 1154.6481 | 122.323 | 20 | 1376.611 | 3736.1787 | 2988.8921 | 1101.3867 | 132.3932 | 20 | 1196.513 | 1154.6481 | 122.323 | 20 | 1376.611 | 3736.1787 | 2988.8921 | 1101.3867 | 132.3932 | 20 | 1196.513 | 1154.6481 | 122.323 | 20 | 1376.611
Not in 2013 |  | Outdoor_Air_Dampers | system cost | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 OA Damper [gravity, motorized] | US_PS_PSZ-AC_2:5 OA Damper [gravity, motorized] | motorized | motorized | 405.5972 | 0 | 20 | 413.0033 | 475.3854 | 0 | 20 | 542.4353 | motorized | motorized | 405.5972 | 0 | 20 | 413.0033 | 475.3854 | 0 | 20 | 542.4353 | motorized | motorized | 405.5972 | 0 | 20 | 413.0033 | 475.3854 | 0 | 20 | 542.4353 | motorized | motorized | 405.5972 | 0 | 20 | 413.0033 | 475.3854 | 0 | 20 | 542.4353 | motorized | motorized | 405.5972 | 0 | 20 | 413.0033 | 475.3854 | 0 | 20 | 542.4353
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC_2:5 OA Rate [cfm] | US_PS_PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 324.3869 | 103.2883 | 20 | 355.913 | 351.2224 | 103.2883 | 20 | 423.0391 | 1152.7343 | 1152.7343 | 324.3869 | 103.2883 | 20 | 355.913 | 351.2224 | 103.2883 | 20 | 423.0391 | 1152.7343 | 1152.7343 | 324.3869 | 103.2883 | 20 | 355.913 | 351.2224 | 103.2883 | 20 | 423.0391 | 1152.7343 | 1152.7343 | 324.3869 | 103.2883 | 20 | 355.913 | 351.2224 | 103.2883 | 20 | 423.0391 | 1152.7343 | 1152.7343 | 324.3869 | 103.2883 | 20 | 355.913 | 351.2224 | 103.2883 | 20 | 423.0391
|  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 OA Rate [cfm] | US_PS_PSZ-AC_2:5 OA Rate [cfm] | 1152.7343 | 1152.7343 | 729.9841 | 103.2883 | 20 | 768.9163 | 826.6078 | 103.2883 | 20 | 965.4745 | 1152.7343 | 1152.7343 | 729.9841 | 103.2883 | 20 | 768.9163 | 826.6078 | 103.2883 | 20 | 965.4745 | 1152.7343 | 1152.7343 | 729.9841 | 103.2883 | 20 | 768.9163 | 826.6078 | 103.2883 | 20 | 965.4745 | 1152.7343 | 1152.7343 | 729.9841 | 103.2883 | 20 | 768.9163 | 826.6078 | 103.2883 | 20 | 965.4745 | 1152.7343 | 1152.7343 | 729.9841 | 103.2883 | 20 | 768.9163 | 826.6078 | 103.2883 | 20 | 965.4745
Not in 2013 |  | Outdoor_Air_Dampers | system cost | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 OA Damper [gravity, motorized] | US_PS_PSZ-AC_2:7 OA Damper [gravity, motorized] | motorized | motorized | 516.5574 | 0 | 20 | 561.9724 | 603.7448 | 0 | 20 | 718.6085 | motorized | motorized | 1042.7718 | 124.5356 | 20 | 1132.6728 | 1174.3283 | 124.5356 | 20 | 1400.2936 | motorized | motorized | 516.5574 | 0 | 20 | 561.9724 | 603.7448 | 0 | 20 | 718.6085 | motorized | motorized | 516.5574 | 0 | 20 | 561.9724 | 603.7448 | 0 | 20 | 718.6085 | motorized | motorized | 516.5574 | 0 | 20 | 561.9724 | 603.7448 | 0 | 20 | 718.6085
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | PSZ-AC_2:7 OA Rate [cfm] | US_PS_PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 526.2144 | 124.5356 | 20 | 570.7004 | 570.5835 | 124.5356 | 20 | 681.6851 | 3153.0841 | 3153.0841 | 526.2144 | 124.5356 | 20 | 570.7004 | 570.5835 | 124.5356 | 20 | 681.6851 | 3153.0841 | 3153.0841 | 526.2144 | 124.5356 | 20 | 570.7004 | 570.5835 | 124.5356 | 20 | 681.6851 | 3153.0841 | 3153.0841 | 526.2144 | 124.5356 | 20 | 570.7004 | 570.5835 | 124.5356 | 20 | 681.6851 | 3153.0841 | 3153.0841 | 526.2144 | 124.5356 | 20 | 570.7004 | 570.5835 | 124.5356 | 20 | 681.6851
|  | Outdoor_Air_Dampers_Motorized | item cost | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 OA Rate [cfm] | US_PS_PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 1042.7718 | 124.5356 | 20 | 1132.6728 | 1174.3283 | 124.5356 | 20 | 1400.2936 | 3153.0841 | 3153.0841 | 1042.7718 | 124.5356 | 20 | 1132.6728 | 1174.3283 | 124.5356 | 20 | 1400.2936 | 3153.0841 | 3153.0841 | 1042.7718 | 124.5356 | 20 | 1132.6728 | 1174.3283 | 124.5356 | 20 | 1400.2936 | 3153.0841 | 3153.0841 | 1042.7718 | 124.5356 | 20 | 1132.6728 | 1174.3283 | 124.5356 | 20 | 1400.2936 | 3153.0841 | 3153.0841 | 1042.7718 | 124.5356 | 20 | 1132.6728 | 1174.3283 | 124.5356 | 20 | 1400.2936
| 90.1-13 u Transfer air | Transfer_Door_Louvers | item cost | Manual Entry | Q | Number of restrooms |  | 8 | 8 | 2131.2737 | 0 | 30 | 2295.3292 | 1829.8245 | 0 | 30 | 2002.6952 | 8 | 8 | 2131.2737 | 0 | 30 | 2295.3292 | 1829.8245 | 0 | 30 | 2002.6952 | 8 | 8 | 2131.2737 | 0 | 30 | 2295.3292 | 1829.8245 | 0 | 30 | 2002.6952 | 8 | 8 | 2131.2737 | 0 | 30 | 2295.3292 | 1829.8245 | 0 | 30 | 2002.6952 | 8 | 8 | 2131.2737 | 0 | 30 | 2295.3292 | 1829.8245 | 0 | 30 | 2002.6952
| Differences in economizer size and requirements based on load changes | DX_Economizer | If any value other than "no" lookup cost based on supply airflow cfm |  |  | [No, DifferentialEnthalpy] are parameter values
x |  | DX_Economizer |  | VAV_POD_1 | VAVDX | VAV_POD_1 (economizer) | US_PS_VAV_POD_1 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 6903.5269 | 214.5653 | 15 | 7746.4312 | 6540.7002 | 214.5653 | 15 | 7332.9181 | DifferentialEnthalpy | DifferentialEnthalpy | 6644.3649 | 214.5653 | 15 | 7451.0647 | 6462.9516 | 214.5653 | 15 | 7244.3082 | DifferentialDryBulb | DifferentialDryBulb | 7857.4172 | 186.8355 | 15 | 8750.7806 | 7464.7151 | 202.0384 | 15 | 8348.6128 | DifferentialEnthalpy | DifferentialEnthalpy | 6670.2811 | 214.5653 | 15 | 7480.6014 | 6462.9516 | 214.5653 | 15 | 7244.3082 | DifferentialDryBulb | DifferentialDryBulb | 6618.4487 | 214.5653 | 15 | 7421.5281 | 6462.9516 | 214.5653 | 15 | 7244.3082 |  | -362.8268 | -181.4134 | -392.7021 | -207.3296 | -155.4972
|  | DX_Economizer |  | VAV_POD_1 | VAVDX | VAV_POD_1 Supply Flow Rate [cfm] | US_PS_VAV_POD_1 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | 6903.5269 | 214.5653 | 15 | 7746.4312 | 6540.7002 | 214.5653 | 15 | 7332.9181 | 5593.8432 | 5445.5216 | 6644.3649 | 214.5653 | 15 | 7451.0647 | 6462.9516 | 214.5653 | 15 | 7244.3082 | 6695.6608 | 6314.2624 | 7857.4172 | 186.8355 | 15 | 8750.7806 | 7464.7151 | 202.0384 | 15 | 8348.6128 | 5615.032 | 5445.5216 | 6670.2811 | 214.5653 | 15 | 7480.6014 | 6462.9516 | 214.5653 | 15 | 7244.3082 | 5572.6544 | 5445.5216 | 6618.4487 | 214.5653 | 15 | 7421.5281 | 6462.9516 | 214.5653 | 15 | 7244.3082
x |  | DX_Economizer |  | VAV_POD_2 | VAVDX | VAV_POD_2 (economizer) | US_PS_VAV_POD_2 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 6903.5269 | 214.5653 | 15 | 7746.4312 | 6540.7002 | 214.5653 | 15 | 7332.9181 | DifferentialEnthalpy | DifferentialEnthalpy | 6644.3649 | 214.5653 | 15 | 7451.0647 | 6437.0354 | 214.5653 | 15 | 7214.7715 | DifferentialDryBulb | DifferentialDryBulb | 7835.6004 | 187.6801 | 15 | 8728.4379 | 7377.448 | 205.4169 | 15 | 8259.2421 | DifferentialEnthalpy | DifferentialEnthalpy | 6592.5325 | 214.5653 | 15 | 7391.9914 | 6462.9516 | 214.5653 | 15 | 7244.3082 | DifferentialDryBulb | DifferentialDryBulb | 6592.5325 | 214.5653 | 15 | 7391.9914 | 6462.9516 | 214.5653 | 15 | 7244.3082 |  | -362.8268 | -207.3296 | -458.1525 | -129.581 | -129.581
|  | DX_Economizer |  | VAV_POD_2 | VAVDX | VAV_POD_2 Supply Flow Rate [cfm] | US_PS_VAV_POD_2 Supply Flow Rate [cfm] | 5805.7312 | 5509.088 | 6903.5269 | 214.5653 | 15 | 7746.4312 | 6540.7002 | 214.5653 | 15 | 7332.9181 | 5593.8432 | 5424.3328 | 6644.3649 | 214.5653 | 15 | 7451.0647 | 6437.0354 | 214.5653 | 15 | 7214.7715 | 6674.472 | 6229.5072 | 7835.6004 | 187.6801 | 15 | 8728.4379 | 7377.448 | 205.4169 | 15 | 8259.2421 | 5551.4656 | 5445.5216 | 6592.5325 | 214.5653 | 15 | 7391.9914 | 6462.9516 | 214.5653 | 15 | 7244.3082 | 5551.4656 | 5445.5216 | 6592.5325 | 214.5653 | 15 | 7391.9914 | 6462.9516 | 214.5653 | 15 | 7244.3082
x |  | DX_Economizer |  | VAV_POD_3 | VAVDX | VAV_POD_3 (economizer) | US_PS_VAV_POD_3 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 6281.5382 | 214.5653 | 15 | 7037.5517 | 5897.4245 | 213.7429 | 15 | 6599.3577 | DifferentialEnthalpy | DifferentialEnthalpy | 6048.2924 | 214.5653 | 15 | 6771.7219 | 5770.453 | 208.6752 | 15 | 6452.0582 | DifferentialDryBulb | DifferentialDryBulb | 7268.3641 | 209.6399 | 15 | 8147.5289 | 6825.7783 | 214.5653 | 15 | 7657.8212 | DifferentialEnthalpy | DifferentialEnthalpy | 6022.3762 | 214.5653 | 15 | 6742.1852 | 5770.453 | 208.6752 | 15 | 6452.0582 | DifferentialDryBulb | DifferentialDryBulb | 5996.46 | 214.5653 | 15 | 6712.6486 | 5749.2911 | 207.8306 | 15 | 6427.5083 |  | -384.1136 | -277.8394 | -442.5857 | -251.9232 | -247.1689
|  | DX_Economizer |  | VAV_POD_3 | VAVDX | VAV_POD_3 Supply Flow Rate [cfm] | US_PS_VAV_POD_3 Supply Flow Rate [cfm] | 5297.2 | 4979.368 | 6281.5382 | 214.5653 | 15 | 7037.5517 | 5897.4245 | 213.7429 | 15 | 6599.3577 | 5106.5008 | 4852.2352 | 6048.2924 | 214.5653 | 15 | 6771.7219 | 5770.453 | 208.6752 | 15 | 6452.0582 | 6123.5632 | 5742.1648 | 7268.3641 | 209.6399 | 15 | 8147.5289 | 6825.7783 | 214.5653 | 15 | 7657.8212 | 5085.312 | 4852.2352 | 6022.3762 | 214.5653 | 15 | 6742.1852 | 5770.453 | 208.6752 | 15 | 6452.0582 | 5064.1232 | 4831.0464 | 5996.46 | 214.5653 | 15 | 6712.6486 | 5749.2911 | 207.8306 | 15 | 6427.5083
x |  | DX_Economizer |  | VAV_OTHER | VAVDX | VAV_OTHER (economizer) | US_PS_VAV_OTHER (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 9210.3017 | 186.708 | 15 | 10336.2637 | 8625.1589 | 179.9511 | 15 | 9624.4441 | DifferentialEnthalpy | DifferentialEnthalpy | 9088.3969 | 185.3003 | 15 | 10187.9679 | 8527.6351 | 178.825 | 15 | 9505.8075 | DifferentialDryBulb | DifferentialDryBulb | 10673.1586 | 203.6002 | 15 | 12115.8126 | 10039.2539 | 196.2802 | 15 | 11344.6747 | DifferentialEnthalpy | DifferentialEnthalpy | 8917.7303 | 183.3295 | 15 | 9980.3539 | 8405.7304 | 177.4173 | 15 | 9357.5118 | DifferentialDryBulb | DifferentialDryBulb | 8942.1112 | 183.6111 | 15 | 10010.013 | 8381.3494 | 177.1357 | 15 | 9327.8526 |  | -585.1428 | -560.7618 | -633.9047 | -511.9999 | -560.7618
|  | DX_Economizer |  | VAV_OTHER | VAVDX | VAV_OTHER Supply Flow Rate [cfm] | US_PS_VAV_OTHER Supply Flow Rate [cfm] | 7903.4224 | 7394.8912 | 9210.3017 | 186.708 | 15 | 10336.2637 | 8625.1589 | 179.9511 | 15 | 9624.4441 | 7797.4784 | 7310.136 | 9088.3969 | 185.3003 | 15 | 10187.9679 | 8527.6351 | 178.825 | 15 | 9505.8075 | 9174.7504 | 8623.8416 | 10673.1586 | 203.6002 | 15 | 12115.8126 | 10039.2539 | 196.2802 | 15 | 11344.6747 | 7649.1568 | 7204.192 | 8917.7303 | 183.3295 | 15 | 9980.3539 | 8405.7304 | 177.4173 | 15 | 9357.5118 | 7670.3456 | 7183.0032 | 8942.1112 | 183.6111 | 15 | 10010.013 | 8381.3494 | 177.1357 | 15 | 9327.8526
x |  | DX_Economizer |  | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 (economizer) | US_PS_PSZ-AC_1:6 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 3463.9774 | 155.0589 | 15 | 3879.6307 | 3390.3084 | 153.3696 | 15 | 3797.3408 | DifferentialEnthalpy | DifferentialEnthalpy | 3500.8119 | 155.9035 | 15 | 3920.7757 | 3427.1429 | 154.2142 | 15 | 3838.4858 | DifferentialDryBulb | DifferentialDryBulb | 3672.7064 | 159.845 | 15 | 4112.7854 | 3599.0373 | 158.1558 | 15 | 4030.4955 | DifferentialEnthalpy | DifferentialEnthalpy | 3463.9774 | 155.0589 | 15 | 3879.6307 | 3402.5866 | 153.6512 | 15 | 3811.0558 | DifferentialDryBulb | DifferentialDryBulb | 3488.5338 | 155.6219 | 15 | 3907.0607 | 3427.1429 | 154.2142 | 15 | 3838.4858 |  | -73.669 | -73.669 | -73.669 | -61.3909 | -61.3909
|  | DX_Economizer |  | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Supply Flow Rate [cfm] | US_PS_PSZ-AC_1:6 Supply Flow Rate [cfm] | 2521.4672 | 2394.3344 | 3463.9774 | 155.0589 | 15 | 3879.6307 | 3390.3084 | 153.3696 | 15 | 3797.3408 | 2585.0336 | 2457.9008 | 3500.8119 | 155.9035 | 15 | 3920.7757 | 3427.1429 | 154.2142 | 15 | 3838.4858 | 2881.6768 | 2754.544 | 3672.7064 | 159.845 | 15 | 4112.7854 | 3599.0373 | 158.1558 | 15 | 4030.4955 | 2521.4672 | 2415.5232 | 3463.9774 | 155.0589 | 15 | 3879.6307 | 3402.5866 | 153.6512 | 15 | 3811.0558 | 2563.8448 | 2457.9008 | 3488.5338 | 155.6219 | 15 | 3907.0607 | 3427.1429 | 154.2142 | 15 | 3838.4858
x |  | DX_Economizer |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 (economizer) | US_PS_PSZ-AC_2:5 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 2837.7803 | 142.6713 | 15 | 3181.2722 | 2804.3575 | 142.1082 | 15 | 3144.0535 | DifferentialEnthalpy | DifferentialEnthalpy | 2821.0689 | 142.3897 | 15 | 3162.6628 | 2787.6461 | 141.8266 | 15 | 3125.4441 | DifferentialDryBulb | DifferentialDryBulb | 3004.894 | 145.4866 | 15 | 3367.3657 | 2988.1827 | 145.2051 | 15 | 3348.7563 | DifferentialEnthalpy | DifferentialEnthalpy | 2821.0689 | 142.3897 | 15 | 3162.6628 | 2837.7803 | 142.6713 | 15 | 3181.2722 | DifferentialDryBulb | DifferentialDryBulb | 2854.4917 | 142.9528 | 15 | 3199.8815 | 2837.7803 | 142.6713 | 15 | 3181.2722 |  | -33.4228 | -33.4228 | -16.7114 | 16.7114 | -16.7114
|  | DX_Economizer |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Supply Flow Rate [cfm] | US_PS_PSZ-AC_2:5 Supply Flow Rate [cfm] | 1589.16 | 1546.7824 | 2837.7803 | 142.6713 | 15 | 3181.2722 | 2804.3575 | 142.1082 | 15 | 3144.0535 | 1567.9712 | 1525.5936 | 2821.0689 | 142.3897 | 15 | 3162.6628 | 2787.6461 | 141.8266 | 15 | 3125.4441 | 1801.048 | 1779.8592 | 3004.894 | 145.4866 | 15 | 3367.3657 | 2988.1827 | 145.2051 | 15 | 3348.7563 | 1567.9712 | 1589.16 | 2821.0689 | 142.3897 | 15 | 3162.6628 | 2837.7803 | 142.6713 | 15 | 3181.2722 | 1610.3488 | 1589.16 | 2854.4917 | 142.9528 | 15 | 3199.8815 | 2837.7803 | 142.6713 | 15 | 3181.2722
x |  | DX_Economizer |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 (economizer) | US_PS_PSZ-AC_2:7 (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 | DifferentialEnthalpy | DifferentialEnthalpy | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 | DifferentialDryBulb | DifferentialDryBulb | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 | DifferentialEnthalpy | DifferentialEnthalpy | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 | DifferentialDryBulb | DifferentialDryBulb | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 |  | 0 | 0 | 0 | 0 | 0
|  | DX_Economizer |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 Supply Flow Rate [cfm] | US_PS_PSZ-AC_2:7 Supply Flow Rate [cfm] | 3157.1312 | 3157.1312 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3157.1312 | 3157.1312 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3157.1312 | 3157.1312 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3157.1312 | 3157.1312 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3157.1312 | 3157.1312 | 3926.3756 | 163.5049 | 15 | 4389.7566 | 3926.3756 | 163.5049 | 15 | 4389.7566
| Impact of any changes in OA requirements ERV load change from OA reduction from 90.1-16 au, cm, & co | Energy_Recovery_Packaged | if "Yes" lookup and interpolate costs based on outside airflow, cfm. |  |  | [Yes,No] are parameter values, indicating if expanded ERV requirements apply.
x |  | Energy_Recovery_Packaged |  | VAV_POD_1 | VAVDX | VAV_Pod_1_ERV Flag | US_PS_VAV_Pod_1_ERV Flag | Yes | Yes | 38877.7982 | 255.0825 | 15 | 44395.1541 | 37025.18 | 255.0825 | 15 | 42327.5575 | Yes | Yes | 37565.5327 | 255.0825 | 15 | 42930.6128 | 36537.5414 | 255.0825 | 15 | 41783.3331 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 37619.8812 | 255.0825 | 15 | 42991.268 | 36627.5774 | 255.0825 | 15 | 41883.817 | Yes | Yes | 37458.1977 | 255.0825 | 15 | 42810.8226 | 36627.0326 | 255.0825 | 15 | 41883.2089 |  | -1852.6182 | -1027.9913 | 0 | -992.3038 | -831.1651
|  | Energy_Recovery_Packaged |  | VAV_POD_1 | VAVDX | VAV_POD_1 OA Rate [cfm] | US_PS_VAV_POD_1 OA Rate [cfm] | 5802.786 | 5514.5971 | 38877.7982 | 255.0825 | 15 | 44395.1541 | 37025.18 | 255.0825 | 15 | 42327.5575 | 5598.6531 | 5438.7412 | 37565.5327 | 255.0825 | 15 | 42930.6128 | 36537.5414 | 255.0825 | 15 | 41783.3331 | 6697.0593 | 6282.2673 | 44560.776 | 255.0825 | 15 | 50695.5212 | 41933.4739 | 255.0825 | 15 | 47788.3774 | 5607.1074 | 5452.747 | 37619.8812 | 255.0825 | 15 | 42991.268 | 36627.5774 | 255.0825 | 15 | 41883.817 | 5581.9563 | 5452.6622 | 37458.1977 | 255.0825 | 15 | 42810.8226 | 36627.0326 | 255.0825 | 15 | 41883.2089
x |  | Energy_Recovery_Packaged |  | VAV_POD_2 | VAVDX | VAV_Pod_2_ERV Flag | US_PS_VAV_Pod_2_ERV Flag | Yes | Yes | 38908.7183 | 255.0825 | 15 | 44429.6621 | 36923.9746 | 255.0825 | 15 | 42214.6081 | Yes | Yes | 37474.8155 | 255.0825 | 15 | 42829.3688 | 36469.2992 | 255.0825 | 15 | 41707.1721 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 37202.5279 | 255.0825 | 15 | 42525.4849 | 36525.8272 | 255.0825 | 15 | 41770.2595 | Yes | Yes | 37242.1656 | 255.0825 | 15 | 42569.7221 | 36529.9135 | 255.0825 | 15 | 41774.8201 |  | -1984.7437 | -1005.5163 | 0 | -676.7008 | -712.2521
|  | Energy_Recovery_Packaged |  | VAV_POD_2 | VAVDX | VAV_POD_2 OA Rate [cfm] | US_PS_VAV_POD_2 OA Rate [cfm] | 5807.5958 | 5498.8538 | 38908.7183 | 255.0825 | 15 | 44429.6621 | 36923.9746 | 255.0825 | 15 | 42214.6081 | 5584.5413 | 5428.1256 | 37474.8155 | 255.0825 | 15 | 42829.3688 | 36469.2992 | 255.0825 | 15 | 41707.1721 | 6671.103 | 6233.2788 | 44396.3683 | 255.0825 | 15 | 50513.602 | 41623.1795 | 255.0825 | 15 | 47445.0327 | 5542.1849 | 5436.919 | 37202.5279 | 255.0825 | 15 | 42525.4849 | 36525.8272 | 255.0825 | 15 | 41770.2595 | 5548.3509 | 5437.5546 | 37242.1656 | 255.0825 | 15 | 42569.7221 | 36529.9135 | 255.0825 | 15 | 41774.8201
x |  | Energy_Recovery_Packaged |  | VAV_POD_3 | VAVDX | VAV_Pod_3_ERV Flag | US_PS_VAV_Pod_3_ERV Flag | Yes | Yes | 35675.32 | 255.0825 | 15 | 40821.0592 | 33591.414 | 255.0825 | 15 | 38495.3361 | Yes | Yes | 34440.1504 | 255.0825 | 15 | 39442.5601 | 32736.9566 | 255.0825 | 15 | 37541.7273 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 34223.301 | 255.0825 | 15 | 39200.5475 | 32738.0463 | 255.0825 | 15 | 37542.9434 | Yes | Yes | 34167.999 | 255.0825 | 15 | 39138.8282 | 32582.901 | 255.0825 | 15 | 37369.7949 |  | -2083.906 | -1703.1937 | 0 | -1485.2547 | -1585.098
|  | Energy_Recovery_Packaged |  | VAV_POD_3 | VAVDX | VAV_POD_3 OA Rate [cfm] | US_PS_VAV_POD_3 OA Rate [cfm] | 5304.6161 | 4980.4486 | 35675.32 | 255.0825 | 15 | 40821.0592 | 33591.414 | 255.0825 | 15 | 38495.3361 | 5112.476 | 4847.5313 | 34440.1504 | 255.0825 | 15 | 39442.5601 | 32736.9566 | 255.0825 | 15 | 37541.7273 | 6119.7068 | 5422.002 | 40903.812 | 255.0825 | 15 | 46649.0432 | 36429.934 | 255.0825 | 15 | 41663.2389 | 5078.7435 | 4847.7008 | 34223.301 | 255.0825 | 15 | 39200.5475 | 32738.0463 | 255.0825 | 15 | 37542.9434 | 5070.1408 | 4823.5668 | 34167.999 | 255.0825 | 15 | 39138.8282 | 32582.901 | 255.0825 | 15 | 37369.7949
x |  | Energy_Recovery_Packaged |  | VAV_OTHER | VAVDX | VAV_OTHER_ERV Flag | US_PS_VAV_OTHER_ERV Flag | Yes | Yes | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399 | Yes | Yes | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399 | Yes | Yes | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399 |  | -4850.9957 | -4850.9957 | 0 | -4850.9957 | -4850.9957
|  | Energy_Recovery_Packaged |  | VAV_OTHER | VAVDX | VAV_OTHER OA Rate [cfm] | US_PS_VAV_OTHER OA Rate [cfm] | 3736.1787 | 2988.8921 | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399 | 3736.1787 | 2988.8921 | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399 | 3736.1787 | 2988.8921 | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399 | 3736.1787 | 2988.8921 | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399 | 3736.1787 | 2988.8921 | 25576.023 | 255.0825 | 15 | 29539.2196 | 20725.0272 | 255.0825 | 15 | 24095.2399
x |  | Energy_Recovery_Packaged |  | PSZ-AC_2:7 | CAVDX | PSZ_AC_2_7_ERV Flag | US_PS_PSZ_AC_2_7_ERV Flag | Yes | Yes | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378 | Yes | Yes | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Yes | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378 | Yes | Yes | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378 |  | 0 | 0 | 0 | 0 | 0
|  | Energy_Recovery_Packaged |  | PSZ-AC_2:7 | CAVDX | PSZ-AC_2:7 OA Rate [cfm] | US_PS_PSZ-AC_2:7 OA Rate [cfm] | 3153.0841 | 3153.0841 | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378 | 3153.0841 | 3153.0841 | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378 | 3153.0841 | 3153.0841 | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378 | 3153.0841 | 3153.0841 | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378 | 3153.0841 | 3153.0841 | 21790.8763 | 255.0825 | 15 | 25291.378 | 21790.8763 | 255.0825 | 15 | 25291.378
| 90.1-13by SHW runout insulation | SHW_runout | Additional insulation required on SHW runouts | SHW piping heat loss |  | SHW_runout_Insul | US_PS_SHW_runout_Insul | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 0 | #N/A | 0 | 0 | 0 | 0 | #N/A | #N/A | 35 | #N/A | 416
| 90.1-10aj | ECM_Motor | Upgrade from shaded pole or permanent split capicator motor to ECM. No labor as is part of replaced fan equipment. |  |  | Exhaust Fan count | US_PS_Exhaust Fan count
Not in 2016 |  | ECM_Motor_1/3 |  |  |  | Bathroom Exhaust Fan count | US_PS_Bathroom Exhaust Fan count | 1 | 1 | 297.7212 | 0 | 15 | 327.4933 | 477.687 | 0 | 15 | 525.4557 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 17 | 0 | 0 | 15 | 0 | 8120.679 | 0 | 15 | 8932.7469 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 500
0 |  | ECM_Motor_3/4 |  |  |  | Kitchen Exhaust Fan count | US_PS_Kitchen Exhaust Fan count | 1 | 1 | 326.9749 | 0 | 15 | 359.6724 | 599.5157 | 0 | 15 | 659.4673 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 10 | 0 | 0 | 15 | 0 | 5995.157 | 0 | 15 | 6594.6727 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 15 | 0 | 502
x | 90.1-16g occ standby controls | occ_standby | 25 conditioned zones |  |  |  |  | 0 | 25 | 0 | 0 | 0 | 0 | 753.6418 | 0 | 375 | 1322.5525 | 0 | 25 | 0 | 0 | 0 | 0 | 753.6418 | 0 | 375 | 1322.5525 | 0 | 25 | 0 | 0 | 0 | 0 | 753.6418 | 0 | 375 | 1322.5525 | 0 | 25 | 0 | 0 | 0 | 0 | 753.6418 | 0 | 375 | 1322.5525 | 0 | 25 | 0 | 0 | 0 | 0 | 753.6418 | 0 | 375 | 1322.5525 |  | 753.6418 | 753.6418 | 753.6418 | 753.6418 | 753.6418
90.1-16 bo furnace efficiency
x |  | Furnace_eff | 3 units |  |  | Furnace heating capacity [Btuh] | US_PS_Furnace heating capacity [Btuh] | 3 | 3 | 13533.7775 | 0 | 45 | 15969.9166 | 13978.1375 | 0 | 45 | 16458.7126 | 3 | 3 | 13533.7775 | 0 | 45 | 15969.9166 | 13978.1375 | 0 | 45 | 16458.7126 | 3 | 3 | 13533.7775 | 0 | 45 | 15969.9166 | 13978.1375 | 0 | 45 | 16458.7126 | 3 | 3 | 13533.7775 | 0 | 45 | 15969.9166 | 13978.1375 | 0 | 45 | 16458.7126 | 3 | 3 | 13533.7775 | 0 | 45 | 15969.9166 | 13978.1375 | 0 | 45 | 16458.7126 |  | 444.36 | 444.36 | 444.36 | 444.36 | 444.36
x | 90.1-16 br | eff_Refr | Addendum G Commercial Refrigerators for Primary School: 2 refrigerators, 24 cubic feet each, efficiency upgraded. |  |  | ea 24 cu ft refridg | Quantity manually entered in col I,J | 2 | 2 | 12243.5992 | 0 | 15 | 13467.9591 | 21453.7008 | 0 | 15 | 23599.0709 | 2 | 2 | 12243.5992 | 0 | 15 | 13467.9591 | 21453.7008 | 0 | 15 | 23599.0709 | 2 | 2 | 12243.5992 | 0 | 15 | 13467.9591 | 21453.7008 | 0 | 15 | 23599.0709 | 2 | 2 | 12243.5992 | 0 | 15 | 13467.9591 | 21453.7008 | 0 | 15 | 23599.0709 | 2 | 2 | 12243.5992 | 0 | 15 | 13467.9591 | 21453.7008 | 0 | 15 | 23599.0709 | 351 | 9210.1016 | 9210.1016 | 9210.1016 | 9210.1016 | 9210.1016
x | 90.1-16 br | eff_Frzr | Addendum G Commercial Freezer for Primary School8/27/2014 2 freezers, 48 cubic feet each, efficiency upgraded. |  |  | ea 48 cu ft freezer | Quantity manually entered in col I,J | 2 | 2 | 13280.4392 | 0 | 15 | 14608.4831 | 15407.4424 | 0 | 15 | 16948.1866 | 2 | 2 | 13280.4392 | 0 | 15 | 14608.4831 | 15407.4424 | 0 | 15 | 16948.1866 | 2 | 2 | 13280.4392 | 0 | 15 | 14608.4831 | 15407.4424 | 0 | 15 | 16948.1866 | 2 | 2 | 13280.4392 | 0 | 15 | 14608.4831 | 15407.4424 | 0 | 15 | 16948.1866 | 2 | 2 | 13280.4392 | 0 | 15 | 14608.4831 | 15407.4424 | 0 | 15 | 16948.1866 | 352 | 2127.0032 | 2127.0032 | 2127.0032 | 2127.0032 | 2127.0032
x | 90.1-16 cn | eff_WI_Refr | primary school walk-in refrigerator |  |  | 1 ea | Quantity manually entered in col I,J | 1 | 1 | 7803.1292 | 0 | 15 | 8701.8933 | 8478.5564 | 0 | 15 | 9444.8632 | 1 | 1 | 7803.1292 | 0 | 15 | 8701.8933 | 8478.5564 | 0 | 15 | 9444.8632 | 1 | 1 | 7803.1292 | 0 | 15 | 8701.8933 | 8478.5564 | 0 | 15 | 9444.8632 | 1 | 1 | 7803.1292 | 0 | 15 | 8701.8933 | 8478.5564 | 0 | 15 | 9444.8632 | 1 | 1 | 7803.1292 | 0 | 15 | 8701.8933 | 8478.5564 | 0 | 15 | 9444.8632 | 353 | 675.4272 | 675.4272 | 675.4272 | 675.4272 | 675.4272
x | 90.1-16 cn | eff_WI_Frzr | primary school walk-in freezer |  |  | 1 ea | Quantity manually entered in col I,J | 1 | 1 | 9693.1404 | 0 | 15 | 10780.9056 | 10218.9664 | 0 | 15 | 11359.3142 | 1 | 1 | 9693.1404 | 0 | 15 | 10780.9056 | 10218.9664 | 0 | 15 | 11359.3142 | 1 | 1 | 9693.1404 | 0 | 15 | 10780.9056 | 10218.9664 | 0 | 15 | 11359.3142 | 1 | 1 | 9693.1404 | 0 | 15 | 10780.9056 | 10218.9664 | 0 | 15 | 11359.3142 | 1 | 1 | 9693.1404 | 0 | 15 | 10780.9056 | 10218.9664 | 0 | 15 | 11359.3142 | 354 | 525.826 | 525.826 | 525.826 | 525.826 | 525.826
0 |  | WI_Refr_ECM | Addendum AR 1/20 hp motor for primary school walk-in refrigerator evaporator fan: shaded pole motor to ECM |  |  | 1 ea | Quantity manually entered in col I,J | 1 | 1 | 313.4139 | 0 | 15 | 463.2854 | 368.8848 | 0 | 15 | 524.3034 | 1 | 1 | 313.4139 | 0 | 15 | 463.2854 | 368.8848 | 0 | 15 | 524.3034 | 1 | 1 | 313.4139 | 0 | 15 | 463.2854 | 368.8848 | 0 | 15 | 524.3034 | 1 | 1 | 313.4139 | 0 | 15 | 463.2854 | 368.8848 | 0 | 15 | 524.3034 | 1 | 1 | 313.4139 | 0 | 15 | 463.2854 | 368.8848 | 0 | 15 | 524.3034 | 357
0 |  | WI_Frzr_ECM | Addendum AR 1/40 hp motor for primary school walk-in freezer evaporator fan: shaded pole motor to ECM |  |  | 1 ea | Quantity manually entered in col I,J | 1 | 1 | 319.1165 | 0 | 15 | 469.5583 | 348.3406 | 0 | 15 | 501.7048 | 1 | 1 | 319.1165 | 0 | 15 | 469.5583 | 348.3406 | 0 | 15 | 501.7048 | 1 | 1 | 319.1165 | 0 | 15 | 469.5583 | 348.3406 | 0 | 15 | 501.7048 | 1 | 1 | 319.1165 | 0 | 15 | 469.5583 | 348.3406 | 0 | 15 | 501.7048 | 1 | 1 | 319.1165 | 0 | 15 | 469.5583 | 348.3406 | 0 | 15 | 501.7048 | 358
0 |  | WI_OccSnsr | Addendum AR: From No walk-in lighting controls required required in base to low temperature occupancy sensors in both freezer and refrigerator walk ins |  |  | 1 ea | Quantity manually entered in col I,J | 0 | 2 | 0 | 0 | 15 | 0 | 1090.312 | 0 | 15 | 1379.8628 | 0 | 2 | 0 | 0 | 15 | 0 | 1090.312 | 0 | 15 | 1379.8628 | 0 | 2 | 0 | 0 | 15 | 0 | 1090.312 | 0 | 15 | 1379.8628 | 0 | 2 | 0 | 0 | 15 | 0 | 1090.312 | 0 | 15 | 1379.8628 | 0 | 2 | 0 | 0 | 15 | 0 | 1090.312 | 0 | 15 | 1379.8628 | 359
| 90.1-07ax | Kitchen Exhaust two items
|  | CAV_DX | lookup based on cooling tons (note - CAV_DX key word appears under the general load changes, not under 90.1-07ax, but change is primarily due to 90.1-07ax in this case) | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Cooling Capacity [ton] | US_PS_PSZ-AC_1:6 Cooling Capacity [ton] | 8.3841 | 8.007 | 12279.615 | 0 | 15 | 16057.341 | 11887.3057 | 0 | 15 | 15583.1503 | 8.4249 | 8.1504 | 12322.1467 | 0 | 15 | 16108.7498 | 12036.4847 | 0 | 15 | 15763.4654 | 8.4035 | 8.104 | 12299.8941 | 0 | 15 | 16081.8527 | 11988.2012 | 0 | 15 | 15705.1044 | 8.1363 | 7.8751 | 12021.8124 | 0 | 15 | 15745.7307 | 11750.0209 | 0 | 15 | 15417.2118 | 7.7875 | 7.5294 | 11658.8981 | 0 | 15 | 15307.0701 | 11390.3346 | 0 | 15 | 14982.4529
Not in 2013 |  | Kitchen_Hood | lookup cost based on code. Multiply by flag, *IF (Target_Code = 2012, 0, 1) | Kitchen_Hood |  | Exhaust airflow, cfm - values are hard coded, don't vary with location |  |  |  | 4988.3688 | 0 | 25 | 7403.7432 | 4030.5792 | 0 | 25 | 6044.009 |  |  | 4988.3688 | 0 | 25 | 7403.7432 | 4030.5792 | 0 | 25 | 6044.009 |  |  | 4988.3688 | 0 | 25 | 7403.7432 | 4030.5792 | 0 | 25 | 6044.009 |  |  | 4988.3688 | 0 | 25 | 7403.7432 | 4030.5792 | 0 | 25 | 6044.009 |  |  | 4988.3688 | 0 | 25 | 7403.7432 | 4030.5792 | 0 | 25 | 6044.009
| HVAC Plant - General Load Change |  | lookup cost based on boiler millions of Btu/h
x |  | Boiler_Capacity |  | Boiler |  | HEATSYS1 Capacity [MMBTU/h] | US_PS_HEATSYS1 Capacity [MMBTU/h] | 0.64826 | 0.6009 | 21622.7856 | 0 | 35 | 28273.4863 | 20750.0919 | 0 | 35 | 27115.7923 | 0.90587 | 0.86434 | 26370.2894 | 0 | 35 | 34571.4086 | 25604.9201 | 0 | 35 | 33556.0884 | 0.86403 | 0.80043 | 25599.196 | 0 | 35 | 33548.495 | 24427.0515 | 0 | 35 | 31993.5568 | 1.015 | 0.97432 | 28381.9699 | 0 | 35 | 37240.0547 | 27631.7146 | 0 | 35 | 36244.7844 | 1.1154 | 1.0753 | 30231.6255 | 0 | 35 | 39693.7625 | 29491.9977 | 0 | 35 | 38712.5904 |  | -872.6936 | -765.3693 | -1172.1446 | -750.2553 | -739.6278
|  | Pump_Flow | lookup based on GPM
x | 90.1-16 an - clean water pump & general load change | Pump_FlPri |  | HW Pump | HEATSYS1 PUMP | HEATSYS1 Flow Rate [gal/min] | US_PS_HEATSYS1 Flow Rate [gal/min] | 66.5317 | 61.6715 | 19557.064 | 0 | 20 | 26059.7564 | 19711.1759 | 0 | 20 | 26149.8859 | 92.9713 | 88.7089 | 20962.4415 | 0 | 20 | 28007.4059 | 21239.6669 | 0 | 20 | 28272.8943 | 88.677 | 82.1491 | 20785.9928 | 0 | 20 | 27773.3324 | 20868.8233 | 0 | 20 | 27757.8085 | 104.1747 | 99.9964 | 21350.9153 | 0 | 20 | 28503.9842 | 21667.8573 | 0 | 20 | 28826.7908 | 114.4758 | 110.3566 | 21708.1055 | 0 | 20 | 28960.5732 | 22035.9865 | 0 | 20 | 29295.7782 |  | 154.1119 | 277.2254 | 82.8305 | 316.9419 | 327.8811
| 90.1-13 dd expands requirement to heating pumps |  | If value is "VFD" lookup cost based on the next motor size hp greater than 1.1 times the hp shown under Power (HP) | Pump | HW Pump | HEATSYS1 PUMP VSD | US_PS_HEATSYS1 PUMP VSD | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
x | General Load Change - HW | VFD_Size | cost input item for VFD | Pump | HW Pump | HEATSYS1 Pump Power [hp] | US_PS_HEATSYS1 Pump Power [hp] | 1.4381 | 1.3199 | 2285.4884 | 0 | 15 | 3303.7116 | 2285.4884 | 0 | 15 | 3303.7116 | 2.0096 | 1.8985 | 2578.9348 | 0 | 15 | 3626.5027 | 2578.9348 | 0 | 15 | 3626.5027 | 1.9168 | 1.7581 | 2578.9348 | 0 | 15 | 3626.5027 | 2285.4884 | 0 | 15 | 3303.7116 | 2.2518 | 2.1401 | 2578.9348 | 0 | 15 | 3626.5027 | 2578.9348 | 0 | 15 | 3626.5027 | 2.4745 | 2.3618 | 2578.9348 | 0 | 15 | 3626.5027 | 2578.9348 | 0 | 15 | 3626.5027 |  | 0 | 0 | -293.4465 | 0 | 0
x | General Load Change - HW | Heating Water Piping | curve fit from Solarc cost calculations | All reheat coils | ZN_VAV_Box | ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | US_PS_ZN_VAV_BOXes_Max_Reheat_Water_Flow_GPM | 94.3097 | 93.4261 | 104471.4539 | 0 | 30 | 148262.4672 | 104215.2643 | 0 | 30 | 147929.4502 | 93.0721 | 92.1725 | 104117.3074 | 0 | 30 | 147802.047 | 103880.5771 | 0 | 30 | 147493.9641 | 85.0563 | 84.1331 | 102621.6963 | 0 | 30 | 145845.5264 | 102538.2439 | 0 | 30 | 145734.2913 | 95.9294 | 95.578 | 104984.7615 | 0 | 30 | 148929.0551 | 104868.6039 | 0 | 30 | 148778.2769 | 94.7918 | 93.9035 | 104618.3528 | 0 | 30 | 148453.3128 | 104351.5998 | 0 | 30 | 148106.7018 |  | -256.1896 | -236.7303 | -83.4524 | -116.1576 | -266.753
No diff for 2010-13 so HIDE | 90.1-07aj | Motor_Efficiency | lookup cost based on the next motor size hp greater than 1.1 times the hp shown in this row
Not in 2013 |  | Motor_Efficiency |  | VAV_POD_1 | VAVDX | VAV_POD_1 Fan Power [hp] | US_PS_VAV_POD_1 Fan Power [hp] | 8.5609 | 8.1357 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 8.2632 | 8.0238 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 9.8802 | 9.32 | 4515.148 | 0 | 18 | 5647.4206 | 4698.0762 | 0 | 18 | 5848.6416 | 8.2722 | 8.0444 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 8.2366 | 8.0443 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966
Not in 2013 |  | Motor_Efficiency |  | VAV_POD_2 | VAVDX | VAV_POD_2 Fan Power [hp] | US_PS_VAV_POD_2 Fan Power [hp] | 8.568 | 8.1125 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 8.2417 | 8.0081 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 9.8465 | 9.1959 | 4515.148 | 0 | 18 | 5647.4206 | 4698.0762 | 0 | 18 | 5848.6416 | 8.1764 | 8.0211 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 8.1855 | 8.022 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966
Not in 2013 |  | Motor_Efficiency |  | VAV_POD_3 | VAVDX | VAV_POD_3 Fan Power [hp] | US_PS_VAV_POD_3 Fan Power [hp] | 7.8297 | 7.3476 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 7.5463 | 7.1516 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 9.0284 | 8.4703 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 7.4927 | 7.1518 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966 | 7.48 | 7.1162 | 3829.8686 | 0 | 18 | 4843.8503 | 3980.7288 | 0 | 18 | 5009.7966
Not in 2013 |  | Motor_Efficiency |  | VAV_OTHER | VAVDX | VAV_OTHER Fan Power [hp] | US_PS_VAV_OTHER Fan Power [hp] | 11.5866 | 10.8235 | 4515.148 | 0 | 18 | 5647.4206 | 4698.0762 | 0 | 18 | 5848.6416 | 11.422 | 10.715 | 4515.148 | 0 | 18 | 5647.4206 | 4698.0762 | 0 | 18 | 5848.6416 | 13.4264 | 12.6363 | 4515.148 | 0 | 18 | 5647.4206 | 4698.0762 | 0 | 18 | 5848.6416 | 11.1967 | 10.5355 | 4515.148 | 0 | 18 | 5647.4206 | 4698.0762 | 0 | 18 | 5848.6416 | 11.2382 | 10.51 | 4515.148 | 0 | 18 | 5647.4206 | 4698.0762 | 0 | 18 | 5848.6416
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC_1:6 | CAVDX | PSZ-AC_1:6 Fan Power [hp] | US_PS_PSZ-AC_1:6 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | PSZ-AC_2:5 | CAVDX | PSZ-AC_2:5 Fan Power [hp] | US_PS_PSZ-AC_2:5 Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | HW Pump |  | HEATSYS1 Pump Power [hp] | US_PS_HEATSYS1 Pump Power [hp] | 1.4381 | 1.3199 | 2100.1765 | 0 | 18 | 2770.502 | 1961.7025 | 0 | 18 | 2593.7967 | 2.0096 | 1.8985 | 2132.5408 | 0 | 18 | 2806.1026 | 2207.7857 | 0 | 18 | 2888.872 | 1.9168 | 1.7581 | 2132.5408 | 0 | 18 | 2806.1026 | 2173.7181 | 0 | 18 | 2851.3977 | 2.2518 | 2.1401 | 2132.5408 | 0 | 18 | 2806.1026 | 2207.7857 | 0 | 18 | 2888.872 | 2.4745 | 2.3618 | 2132.5408 | 0 | 18 | 2806.1026 | 2207.7857 | 0 | 18 | 2888.872
[10 empty] | 1166932.6649 |  |  | 1729852.8437 | 1146712.2582 |  |  | 1643934.4671 |  |  | 1158819.4473 |  |  | 1662572.7283 | 1158051.2424 |  |  | 1656695.9029 |  |  | 1059982.112 |  |  | 1566755.887 | 1046315.4697 |  |  | 1543530.1517 |  |  | 1157975.1305 |  |  | 1661183.6145 | 1149028.5542 |  |  | 1646988.3306 |  |  | 1159653.6467 |  |  | 1663584.9309 | 1148961.247 |  |  | 1647116.9306
[9 empty] | 1713882.9272 |  |  |  | 1626153.202 | [5 empty] | 1646602.8118 |  |  |  | 1638914.6379 | [5 empty] | 1550785.9704 |  |  |  | 1525748.8867 | [5 empty] | 1645213.6979 |  |  |  | 1629207.0656 | [5 empty] | 1647615.0143 |  |  |  | 1629335.6656

## HVAC Small Hotel Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Small Hotel | [7 empty] | Small Hotel
[10 empty] | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW | Find Row
|  |  | YES |  |  |  |  | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
[7 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
[7 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22
[8 empty] | Climate Zone 1 | 2A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 2 | 3A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 3 | 3B | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 4 | 4A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 5 | 5A | Base Code | 2016 |  |  | Target Code | 2019 |  |  |  | First cost difference |  | 2016 | vs | 2019
Costs row marked x, other rows not marked | [7 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [8 empty] | Bzse | Target | [8 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [9 empty] | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameters | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total |  | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
| HVAC System - General load change | Supply air units | lookup based on cooling tons |  |  | HVAC System - General Load Change
x |  | CAV_DX |  | SAC_MEETINGROOM | CAVDX | SAC_FRONTOFFICE Cooling Capacity [ton] | US_SH_SAC_FRONTOFFICE Cooling Capacity [ton] | 2.5999 | 2.4575 | 6061.0049 | 0 | 15 | 8295.1689 | 5894.1462 | 0 | 15 | 8073.2924 | 2.4415 | 2.3156 | 5868.8349 | 0 | 15 | 8041.1451 | 5669.4147 | 0 | 15 | 7787.8661 | 2.3849 | 2.2422 | 5779.1827 | 0 | 15 | 7927.2799 | 5553.1816 | 0 | 15 | 7640.2411 | 2.2772 | 2.1613 | 5608.6711 | 0 | 15 | 7710.717 | 5425.1977 | 0 | 15 | 7477.6917 | 2.1107 | 2 | 5345.0362 | 0 | 15 | 7375.8803 | 5169.7458 | 0 | 15 | 7153.2481 |  | -166.8587 | -199.4202 | -226.0011 | -183.4734 | -175.2903
x |  | CAV_DX |  | SAC_FRONTLOUNGE | CAVDX | SAC_FRONTLOUNGE Cooling Capacity [ton] | US_SH_SAC_FRONTLOUNGE Cooling Capacity [ton] | 6.2508 | 5.928 | 9751.712 | 0 | 15 | 13082.4702 | 9367.8459 | 0 | 15 | 12629.0137 | 6.3213 | 5.9999 | 9842.3657 | 0 | 15 | 13187.4983 | 9428.7493 | 0 | 15 | 12708.2863 | 6.1359 | 5.8857 | 9603.819 | 0 | 15 | 12911.1269 | 9332.0768 | 0 | 15 | 12582.4561 | 6.027 | 5.7233 | 9463.5979 | 0 | 15 | 12748.672 | 9194.4972 | 0 | 15 | 12403.3805 | 5.7399 | 5.5082 | 9208.5486 | 0 | 15 | 12421.6701 | 9012.3602 | 0 | 15 | 12166.3084 |  | -383.866 | -413.6165 | -271.7422 | -269.1008 | -196.1884
x |  | CAV_DX |  | SAC_FRONTOFFICE | CAVDX | SAC_MEETINGROOM Cooling Capacity [ton] | US_SH_SAC_MEETINGROOM Cooling Capacity [ton] | 2.9807 | 2.8761 | 6440.8412 | 0 | 15 | 8815.5548 | 6336.4867 | 0 | 15 | 8672.5863 | 2.9994 | 2.9144 | 6459.4833 | 0 | 15 | 8841.0948 | 6374.7065 | 0 | 15 | 8724.9485 | 3.1725 | 3.0992 | 6682.675 | 0 | 15 | 9133.2221 | 6588.0012 | 0 | 15 | 9009.3223 | 2.8701 | 2.7771 | 6330.5061 | 0 | 15 | 8664.3928 | 6237.744 | 0 | 15 | 8537.3062 | 2.8701 | 2.7798 | 6330.5317 | 0 | 15 | 8664.4277 | 6240.4947 | 0 | 15 | 8541.0747 |  | -104.3545 | -84.7767 | -94.6738 | -92.7621 | -90.037
x |  | CAV_DX |  | SAC_EXC_EMPLGE_RESTRM | CAVDX | SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | US_SH_SAC_EXC_EMPLGE_RESTRM Cooling Capacity [ton] | 6.1652 | 6.1259 | 9641.5234 | 0 | 15 | 12954.8098 | 9590.8397 | 0 | 15 | 12896.0896 | 6.0419 | 6.0006 | 9482.7741 | 0 | 15 | 12770.8887 | 9429.5465 | 0 | 15 | 12709.2213 | 6.1247 | 6.0801 | 9589.3024 | 0 | 15 | 12894.3085 | 9531.8765 | 0 | 15 | 12827.777 | 5.7874 | 5.7466 | 9248.8395 | 0 | 15 | 12474.1132 | 9214.2501 | 0 | 15 | 12429.0912 | 5.5467 | 5.5007 | 9045.0065 | 0 | 15 | 12208.8013 | 9006.0327 | 0 | 15 | 12158.0725 |  | -50.6837 | -53.2276 | -57.4259 | -34.5893 | -38.9738
x |  | Air Distribution | curve fit from Solarc cost calculations |  |  | sum of 4 system Supply Flow Rate [cfm] values from HVAC data (not the sum of the cooling capacity) |  | 5805.7312 | 5593.8432 | 94454.6316 | 0 | 30 | 155443.3725 | 92751.3479 | 0 | 30 | 152605.957 | 5848.1088 | 5636.2208 | 94795.2883 | 0 | 30 | 156010.8556 | 93092.0046 | 0 | 30 | 153173.4401 | 6632.0944 | 6420.2064 | 101097.4381 | 0 | 30 | 166509.2928 | 99394.1544 | 0 | 30 | 163671.8774 | 5572.6544 | 5403.144 | 92581.0195 | 0 | 30 | 152322.2155 | 91218.3925 | 0 | 30 | 150052.2831 | 5615.032 | 5381.9552 | 92921.6762 | 0 | 30 | 152889.6986 | 91048.0642 | 0 | 30 | 149768.5416 |  | -1703.2837 | -1703.2837 | -1703.2837 | -1362.627 | -1873.6121
|  |  |  | Material |  | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 783.9856 | [8 empty] | 826.3632 | 762.7968 | [8 empty] | 953.496 | 889.9296 | [8 empty] | 762.7968 | 720.4192 | [8 empty] | 762.7968 | 699.2304
|  |  |  | y = 0.7074x + 6086.9 |  | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1779.8592 | [8 empty] | 1906.992 | 1801.048 | [8 empty] | 2161.2576 | 2055.3136 | [8 empty] | 1801.048 | 1716.2928 | [8 empty] | 1801.048 | 1695.104
|  |  |  | Labor |  | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | [8 empty] | 889.9296 | 868.7408 | [8 empty] | 1017.0624 | 995.8736 | [8 empty] | 868.7408 | 826.3632 | [8 empty] | 868.7408 | 826.3632
|  |  |  | y = 2.9572x + 16341 |  | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | [8 empty] | 2224.824 | 2203.6352 | [8 empty] | 2500.2784 | 2479.0896 | [8 empty] | 2140.0688 | 2140.0688 | [8 empty] | 2182.4464 | 2161.2576
| 90.1-13 d | Hotel Room Controls: setback & ventilation | Increase in controls cost to shut off ventilation & setback unrented rooms; Basis: 50% central systems | Basis: 90.1 cost effectiveness analysis; adjusted to 2018 $. Cost curve fit: |  | Number_of_Rooms | US_SH_Number_of_Rooms | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A | #N/A | 0 | 0 | 15 | 0 | #N/A | 0 | 15 | #N/A | #N/A
|  |  |  | Material x | 280.6
|  |  |  | Material intercept | 2497.5
|  |  |  | Labor x | 49.056
|  |  |  | Labor intercept | 688.68
| 90.1-10bk | PTAC_Efficiency | lookup cost values times quantity |  |  | Quantities are the same for all climates and are hard-coded, no lookup needed
|  | PTAC_Efficiency |  | PTAC |  | Type (PTAC, PTHP) |  | PTAC | PTAC | [8 empty] | PTAC | PTAC | [8 empty] | PTAC | PTAC | [8 empty] | PTAC | PTAC | [8 empty] | PTAC | PTAC
0 |  | PTAC_Efficiency |  |  |  | Quantity |  | 85 | 85 | 120177.1594 | 0 | 15 | 152851.264 | 124583.7294 | 0 | 15 | 157698.491 | 85 | 85 | 120177.1594 | 0 | 15 | 152851.264 | 124583.7294 | 0 | 15 | 157698.491 | 85 | 85 | 120177.1594 | 0 | 15 | 152851.264 | 124583.7294 | 0 | 15 | 157698.491 | 85 | 85 | 120177.1594 | 0 | 15 | 152851.264 | 124583.7294 | 0 | 15 | 157698.491 | 85 | 85 | 120177.1594 | 0 | 15 | 152851.264 | 124583.7294 | 0 | 15 | 157698.491
| 90.1-13by SHW runout insulation | SHW_runout | Additional insulation required on SHW runouts | SHW piping heat loss |  | SHW_runout_Insul | US_SH_SHW_runout_Insul | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | 35 | #N/A | 416
0 |  | Door_Switch_Control | Increase in controls cost to accommodate door switch through addenda 90.1-10ba |  |  | Door count: Basis: 0.7% of small hotel guest rooms have exterior sliding doors which translates to (1) door for the prototype analyzed | US_SH_Door count: Basis: 0.7% of small hotel guest rooms have exterior sliding doors which translates to (1) door for the prototype analyzed | 1 | 1 | 489.4015 | 0 | 15 | 636.0599 | 735.6519 | 0 | 15 | 821.864 | 1 | 1 | 489.4015 | 0 | 15 | 636.0599 | 735.6519 | 0 | 15 | 821.864 | 1 | 1 | 489.4015 | 0 | 15 | 636.0599 | 735.6519 | 0 | 15 | 821.864 | 1 | 1 | 489.4015 | 0 | 15 | 636.0599 | 735.6519 | 0 | 15 | 821.864 | 1 | 1 | 489.4015 | 0 | 15 | 636.0599 | 735.6519 | 0 | 15 | 821.864 | 511
No diff for 2010-13 so HIDE | N. Carolina hotel room HVAC control amendment |  | include cost lookup in all base code fields with *IF(State_Abb = "NC",1,0), only included for NC. Cost is a credit so will show as a negative value in the base code case
Not in 2013 |  | NC_hotel_HVAC | no data needed - conditional on state per above |  |  |  |  | 81 | 81 | [8 empty] | 81 | 81 | [8 empty] | 81 | 81 | [8 empty] | 81 | 81 | [8 empty] | 81 | 81
90.1-16 bo furnace efficiency
x |  | Furnace_eff | 4 units |  |  | Furnace heating capacity [Btuh] | US_SH_Furnace heating capacity [Btuh] | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 | 4 | 4 | 18045.0366 | 0 | 60 | 21293.2221 | 18637.5166 | 0 | 60 | 21944.9501 |  | 592.48 | 592.48 | 592.48 | 592.48 | 592.48
| 90.1-16a low leak RA damper | Outdoor_Air_Dampers | Motorized return air damper
|  | Outdoor_Air_Dampers | system cost | SAC_FRONTLOUNGE | CAVDX | SAC_FrontLounge OA Damper [gravity, motorized] | US_SH_SAC_FrontLounge OA Damper [gravity, motorized] | motorized | motorized | 387.4126 | 0 | 20 | 399.7041 | 452.5628 | 0 | 20 | 520.7533 | motorized | motorized | 387.4126 | 0 | 20 | 399.7041 | 452.5628 | 0 | 20 | 520.7533 | motorized | motorized | 387.4126 | 0 | 20 | 399.7041 | 452.5628 | 0 | 20 | 520.7533 | motorized | motorized | 387.4126 | 0 | 20 | 399.7041 | 452.5628 | 0 | 20 | 520.7533 | motorized | motorized | 387.4126 | 0 | 20 | 399.7041 | 452.5628 | 0 | 20 | 520.7533
|  | Outdoor_Air_Dampers_Gravity | item cost |  |  | SAC_FRONTLOUNGE OA Rate [cfm] | US_SH_SAC_FRONTLOUNGE OA Rate [cfm] | 500.0133 | 500.0133 | 292.4794 | 98.8903 | 20 | 317.8301 | 317.062 | 98.8903 | 20 | 379.3208 | 500.0133 | 500.0133 | 292.4794 | 98.8903 | 20 | 317.8301 | 317.062 | 98.8903 | 20 | 379.3208 | 500.0133 | 500.0133 | 292.4794 | 98.8903 | 20 | 317.8301 | 317.062 | 98.8903 | 20 | 379.3208 | 500.0133 | 500.0133 | 292.4794 | 98.8903 | 20 | 317.8301 | 317.062 | 98.8903 | 20 | 379.3208 | 500.0133 | 500.0133 | 292.4794 | 98.8903 | 20 | 317.8301 | 317.062 | 98.8903 | 20 | 379.3208
x |  | Outdoor_Air_Dampers_Motorized | item cost |  | CAVDX | SAC_FrontLounge OA Rate [cfm] | US_SH_SAC_FrontLounge OA Rate [cfm] | 500.0133 | 500.0133 | 679.8921 | 98.8903 | 20 | 717.5341 | 769.6248 | 98.8903 | 20 | 900.0741 | 500.0133 | 500.0133 | 679.8921 | 98.8903 | 20 | 717.5341 | 769.6248 | 98.8903 | 20 | 900.0741 | 500.0133 | 500.0133 | 679.8921 | 98.8903 | 20 | 717.5341 | 769.6248 | 98.8903 | 20 | 900.0741 | 500.0133 | 500.0133 | 679.8921 | 98.8903 | 20 | 717.5341 | 769.6248 | 98.8903 | 20 | 900.0741 | 500.0133 | 500.0133 | 679.8921 | 98.8903 | 20 | 717.5341 | 769.6248 | 98.8903 | 20 | 900.0741 |  | 89.7327 | 89.7327 | 89.7327 | 89.7327 | 89.7327
x | 90.1-16g occ standby controls | occ_standby | 54 conditioned zones |  |  |  |  | 0 | 54 | 0 | 0 | 0 | 0 | 1627.8663 | 0 | 810 | 2856.7133 | 0 | 54 | 0 | 0 | 0 | 0 | 1627.8663 | 0 | 810 | 2856.7133 | 0 | 54 | 0 | 0 | 0 | 0 | 1627.8663 | 0 | 810 | 2856.7133 | 0 | 54 | 0 | 0 | 0 | 0 | 1627.8663 | 0 | 810 | 2856.7133 | 0 | 54 | 0 | 0 | 0 | 0 | 1627.8663 | 0 | 810 | 2856.7133 |  | 1627.8663 | 1627.8663 | 1627.8663 | 1627.8663 | 1627.8663
| Differences in economizer size and requirements based on load changes | DX_Economizer | cost applied if any value other than "No" 1ookup cost based on outside air cfm
x |  | DX_Economizer |  | SAC_MEETINGROOM | CAVDX | SAC_MeetingRoom (economizer) | US_SH_SAC_MeetingRoom (economizer) | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DX_Economizer |  |  | CAVDX | SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_MR_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 889.9296 | 868.7408 | 2221.0971 | 134.8431 | 15 | 2494.9453 | 2191.8331 | 134.8431 | 15 | 2462.4338 | 889.9296 | 868.7408 | 2221.0971 | 134.8431 | 15 | 2494.9453 | 2191.8331 | 134.8431 | 15 | 2462.4338 | 1017.0624 | 995.8736 | 2386.5731 | 135.0698 | 15 | 2678.8198 | 2367.4172 | 134.8431 | 15 | 2657.503 | 868.7408 | 826.3632 | 2191.8331 | 134.8431 | 15 | 2462.4338 | 2133.3051 | 134.8431 | 15 | 2397.4107 | 868.7408 | 826.3632 | 2191.8331 | 134.8431 | 15 | 2462.4338 | 2133.3051 | 134.8431 | 15 | 2397.4107
x |  | DX_Economizer |  | SAC_FRONTLOUNGE | CAVDX | SAC_FrontLounge (economizer) | US_SH_SAC_FrontLounge (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 3071.7396 | 146.6128 | 15 | 3441.8031 | 2988.1827 | 145.2051 | 15 | 3348.7563 | DifferentialEnthalpy | DifferentialEnthalpy | 3088.4509 | 146.8943 | 15 | 3460.4124 | 3004.894 | 145.4866 | 15 | 3367.3657 | DifferentialDryBulb | DifferentialDryBulb | 3255.2485 | 150.2727 | 15 | 3646.476 | 3193.8576 | 148.8651 | 15 | 3577.9011 | DifferentialEnthalpy | DifferentialEnthalpy | 3004.894 | 145.4866 | 15 | 3367.3657 | 2938.0485 | 144.3605 | 15 | 3292.9283 | DifferentialDryBulb | DifferentialDryBulb | 3004.894 | 145.4866 | 15 | 3367.3657 | 2921.3372 | 144.0789 | 15 | 3274.3189
|  | DX_Economizer |  |  | CAVDX | SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_FL_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 1885.8032 | 1779.8592 | 3071.7396 | 146.6128 | 15 | 3441.8031 | 2988.1827 | 145.2051 | 15 | 3348.7563 | 1906.992 | 1801.048 | 3088.4509 | 146.8943 | 15 | 3460.4124 | 3004.894 | 145.4866 | 15 | 3367.3657 | 2161.2576 | 2055.3136 | 3255.2485 | 150.2727 | 15 | 3646.476 | 3193.8576 | 148.8651 | 15 | 3577.9011 | 1801.048 | 1716.2928 | 3004.894 | 145.4866 | 15 | 3367.3657 | 2938.0485 | 144.3605 | 15 | 3292.9283 | 1801.048 | 1695.104 | 3004.894 | 145.4866 | 15 | 3367.3657 | 2921.3372 | 144.0789 | 15 | 3274.3189
x |  | DX_Economizer |  | SAC_FRONTOFFICE | CAVDX | SAC_FrontOffice (economizer) | US_SH_SAC_FrontOffice (economizer) | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DX_Economizer |  |  | CAVDX | SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_FO_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 847.552 | 783.9856 | 2162.5691 | 134.8431 | 15 | 2429.9222 | 2074.7771 | 134.8431 | 15 | 2332.3876 | 826.3632 | 762.7968 | 2133.3051 | 134.8431 | 15 | 2397.4107 | 2045.5131 | 134.8431 | 15 | 2299.8761 | 953.496 | 889.9296 | 2308.8891 | 134.8431 | 15 | 2592.48 | 2221.0971 | 134.8431 | 15 | 2494.9453 | 762.7968 | 720.4192 | 2045.5131 | 134.8431 | 15 | 2299.8761 | 1986.9851 | 134.8431 | 15 | 2234.853 | 762.7968 | 699.2304 | 2045.5131 | 134.8431 | 15 | 2299.8761 | 1957.7211 | 134.8431 | 15 | 2202.3415
x |  | DX_Economizer |  | SAC_EXC_EMPLGE_RESTRM | CAVDX | SAC_Exc_EmpLge_RestRm (economizer) | US_SH_SAC_Exc_EmpLge_RestRm (economizer) | DifferentialEnthalpy | DifferentialEnthalpy | 3267.5267 | 150.5543 | 15 | 3660.191 | 3255.2485 | 150.2727 | 15 | 3646.476 | DifferentialEnthalpy | DifferentialEnthalpy | 3292.083 | 151.1173 | 15 | 3687.6209 | 3279.8048 | 150.8358 | 15 | 3673.906 | DifferentialDryBulb | DifferentialDryBulb | 3451.6993 | 154.7773 | 15 | 3865.9157 | 3439.4211 | 154.4958 | 15 | 3852.2007 | DifferentialEnthalpy | DifferentialEnthalpy | 3242.9703 | 149.9912 | 15 | 3632.761 | 3242.9703 | 149.9912 | 15 | 3632.761 | DifferentialDryBulb | DifferentialDryBulb | 3267.5267 | 150.5543 | 15 | 3660.191 | 3255.2485 | 150.2727 | 15 | 3646.476
|  | DX_Economizer |  |  | CAVDX | SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | US_SH_SAC_EXC_ADDAQ SUPPLY FAN Supply Flow Rate [cfm] | 2182.4464 | 2161.2576 | 3267.5267 | 150.5543 | 15 | 3660.191 | 3255.2485 | 150.2727 | 15 | 3646.476 | 2224.824 | 2203.6352 | 3292.083 | 151.1173 | 15 | 3687.6209 | 3279.8048 | 150.8358 | 15 | 3673.906 | 2500.2784 | 2479.0896 | 3451.6993 | 154.7773 | 15 | 3865.9157 | 3439.4211 | 154.4958 | 15 | 3852.2007 | 2140.0688 | 2140.0688 | 3242.9703 | 149.9912 | 15 | 3632.761 | 3242.9703 | 149.9912 | 15 | 3632.761 | 2182.4464 | 2161.2576 | 3267.5267 | 150.5543 | 15 | 3660.191 | 3255.2485 | 150.2727 | 15 | 3646.476
No diff for 2010-13 so HIDE | 90.1-07aj | Motor_Efficiency | lookup cost based on the next motor size hp greater than 1.1 times the supply fan motor hp
Not in 2013 |  | Motor_Efficiency |  | SAC_FRONTLOUNGE | CAVDX | SAC_FRONTLOUNGE Fan Power [hp] | US_SH_SAC_FRONTLOUNGE Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Not in 2013 |  | Motor_Efficiency |  | SAC_EXC_EMPLGE_RESTRM | CAVDX | SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | US_SH_SAC_EXC_EMPLGE_RESTRM Fan Power [hp] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
[10 empty] | 151413.908 |  |  | 227704.1264 | 151219.1053 |  |  | 227573.9089 |  |  | 151554.2089 |  |  | 228010.2721 | 151314.1282 |  |  | 227846.7715 |  |  | 158184.2937 |  |  | 238898.3781 | 158067.577 |  |  | 238863.5132 |  |  | 148205.4273 |  |  | 222930.9934 | 148506.1082 |  |  | 223527.1796 |  |  | 147848.1487 |  |  | 222598.7909 | 147688.291 |  |  | 222409.7777
[9 empty] | 206410.9043 |  |  |  | 202772.2455 | [5 empty] | 206717.05 |  |  |  | 203045.1081 | [5 empty] | 217605.156 |  |  |  | 214061.8497 | [5 empty] | 201637.7713 |  |  |  | 198725.5161 | [5 empty] | 201305.5688 |  |  |  | 197608.1143

## HVAC Mid-rise Apartment Proto
90.1 Cost Effectiveness - Cost Estimate - HVAC - Mid-rise Apartment |  |  |  | Split system Inflation adjustment for 2012 to 2018 (M/L): | 1.032 | 1.185 |  | Mid-rise Apartment |  | Note: For mid-rise apartment, material, labor and project cost adjustments made on tis sheet for total new construction rather than on HVAC Comp sheet.
[10 empty] | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW |  |  | $AP | $AQ | $AR | $BA | $BK | $BL | $BM | $BW | Find Row
|  |  | YES |  |  |  |  | 3 | 4 | [8 empty] | 5 | 6 | [8 empty] | 7 | 8 | [8 empty] | 9 | 10 | [8 empty] | 11 | 12
This is all new, now have lookup for mid-rise apartment cooling capacity change | [6 empty] | City-year parameter column |  |  | I | I | I | I | J | J | J | J |  |  | S | S | S | S | T | T | T | T |  |  | AC | AC | AC | AC | AD | AD | AD | AD |  |  | AM | AM | AM | AM | AN | AN | AN | AN |  |  | AW | AW | AW | AW | AX | AX | AX | AX
[7 empty] | Parameter range lookup extension |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par |  |  | _2007Par | _2007Par | _2007Par | _2007Par | _2010Par | _2010Par | _2010Par | _2010Par
All "SPLIT MXX" named cooling capacities are divided by 2 and resulting costs multiplied by 2. These zones include 2 apartments | [6 empty] | Cost range lookup extension |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs |  |  | _2007Costs | _2007Costs | _2007Costs | _2007Costs | _2010Costs | _2010Costs | _2010Costs | _2010Costs
[7 empty] | Cost range column index values |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 |  |  | 9 | 10 | 11 | 20 | 10 | 11 | 12 | 22 | Unit
[8 empty] | Climate Zone 1 | 2A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 2 | 3A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 3 | 3B | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 4 | 4A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Climate Zone 5 | 5A | Base Code | 2016 |  |  | Target Code | 2019 |  |  | Mult | First cost difference |  | 2016 | vs | 2019
Costs row marked x, other rows not marked | [7 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [8 empty] | 2016 | 2019 | [9 empty] | Total new construction (added cost)
| Addendum or general | Key Word | Description | Model | Type | Parameters | Lookup Value in HVAC Data, Current_HVAC_Data | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total | Prototype | Prototype | Total New | Maintenance | Replacement Life | Total | Total New | Maintenance | Replacement Life | Total |  | 2A | 3A | 3B | 4A | 5A
| load change |  |  | Object |  |  |  | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost | Data | Data | Construction |  |  | Replacement Cost | Construction |  |  | Replacement Cost
0 |  | Door_Switch_Control | Increase in controls cost to accommodate door switch through addenda 90.1-10ba |  |  | Door count: Basis: 11.6% of apartments have exterior sliding doors which translates to (4) doors for the prototype analyzed | US_SH_Door count: Basis: 11.6% of apartments have exterior sliding doors which translates to (4) doors for the prototype analyzed | 4 | 4 | 1957.606 | 0 | 15 | 2544.2398 | 2942.6076 | 0 | 15 | 3287.4562 | 4 | 4 | 1957.606 | 0 | 15 | 2544.2398 | 2942.6076 | 0 | 15 | 3287.4562 | 4 | 4 | 1957.606 | 0 | 15 | 2544.2398 | 2942.6076 | 0 | 15 | 3287.4562 | 4 | 4 | 1957.606 | 0 | 15 | 2544.2398 | 2942.6076 | 0 | 15 | 3287.4562 | 4 | 4 | 1957.606 | 0 | 15 | 2544.2398 | 2942.6076 | 0 | 15 | 3287.4562 | 511
| HVAC System - General load change |  | curve fits for labor and material | [54 empty] | unit count
x |  | Split-System_W_Furnace |  | SPLIT GN1 COOLING COIL | Split System | SPLIT GN1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GN1 COOLING COIL Cooling Capacity [ton] | 0.72462 | 0.71657 | 6456.0619 | 0 | 15 | 9480.7503 | 6386.8746 | 0 | 15 | 9378.8038 | 0.65014 | 0.64124 | 5813.4756 | 0 | 15 | 8534.1959 | 5736.3614 | 0 | 15 | 8420.647 | 0.60991 | 0.59896 | 5464.5515 | 0 | 15 | 8020.4868 | 5369.2819 | 0 | 15 | 7880.2576 | 0.59683 | 0.58765 | 5350.7257 | 0 | 15 | 7852.9461 | 5270.8167 | 0 | 15 | 7735.3397 | 0.50669 | 0.49714 | 4562.9504 | 0 | 15 | 6693.9703 | 4479.0695 | 0 | 15 | 6570.6219 | 1 | -69.1873 | -77.1142 | -95.2696 | -79.909 | -83.8808
x |  | Split-System_W_Furnace |  | SPLIT GN2 COOLING COIL | Split System | SPLIT GN2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GN2 COOLING COIL Cooling Capacity [ton] | 0.72294 | 0.71491 | 6441.6613 | 0 | 15 | 9459.5306 | 6372.5856 | 0 | 15 | 9357.7501 | 0.64857 | 0.63967 | 5799.885 | 0 | 15 | 8514.1833 | 5722.8333 | 0 | 15 | 8400.728 | 0.60819 | 0.59725 | 5449.5494 | 0 | 15 | 7998.404 | 5354.4125 | 0 | 15 | 7858.3724 | 0.59496 | 0.58583 | 5334.5169 | 0 | 15 | 7829.0899 | 5254.9652 | 0 | 15 | 7712.0113 | 0.50447 | 0.49498 | 4543.4792 | 0 | 15 | 6665.3366 | 4460.08 | 0 | 15 | 6542.6989 | 1 | -69.0758 | -77.0517 | -95.1369 | -79.5517 | -83.3992
x |  | Split-System_W_Furnace |  | SPLIT GNE COOLING COIL | Split System | SPLIT GNE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GNE COOLING COIL Cooling Capacity [ton] | 0.84983 | 0.84053 | 7526.4481 | 0 | 15 | 11058.8952 | 7447.3142 | 0 | 15 | 10942.1618 | 0.75301 | 0.74161 | 6699.8705 | 0 | 15 | 9840.0579 | 6602.019 | 0 | 15 | 9695.8403 | 0.73287 | 0.72042 | 6526.9562 | 0 | 15 | 9585.2197 | 6419.9707 | 0 | 15 | 9427.5694 | 0.69822 | 0.68633 | 6228.838 | 0 | 15 | 9145.9672 | 6126.3144 | 0 | 15 | 8994.9391 | 0.59725 | 0.58515 | 5354.4373 | 0 | 15 | 7858.4088 | 5249.0449 | 0 | 15 | 7703.2987 | 1 | -79.1339 | -97.8515 | -106.9856 | -102.5236 | -105.3923
x |  | Split-System_W_Furnace |  | SPLIT GNW COOLING COIL | Split System | SPLIT GNW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GNW COOLING COIL Cooling Capacity [ton] | 0.94819 | 0.93774 | 8358.7441 | 0 | 15 | 12287.2316 | 8270.6663 | 0 | 15 | 12157.1924 | 0.84441 | 0.83404 | 7480.3008 | 0 | 15 | 10990.8205 | 7392.1251 | 0 | 15 | 10860.756 | 0.82609 | 0.81272 | 7324.4553 | 0 | 15 | 10760.9472 | 7210.5045 | 0 | 15 | 10592.8927 | 0.79432 | 0.78088 | 7053.4548 | 0 | 15 | 10361.3092 | 6938.5397 | 0 | 15 | 10191.881 | 0.70314 | 0.68933 | 6271.2509 | 0 | 15 | 9208.4507 | 6152.1706 | 0 | 15 | 9033.0266 | 1 | -88.0778 | -88.1757 | -113.9508 | -114.9151 | -119.0803
x |  | Split-System_W_Furnace |  | SPLIT GS1 COOLING COIL | Split System | SPLIT GS1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GS1 COOLING COIL Cooling Capacity [ton] | 0.76065 | 0.75025 | 6765.3154 | 0 | 15 | 9936.5217 | 6676.216 | 0 | 15 | 9805.1936 | 0.67117 | 0.66065 | 5995.4251 | 0 | 15 | 8802.1492 | 5904.4709 | 0 | 15 | 8668.1964 | 0.61633 | 0.604 | 5520.2627 | 0 | 15 | 8102.4957 | 5413.1336 | 0 | 15 | 7944.8021 | 0.63623 | 0.62578 | 5692.9854 | 0 | 15 | 8356.7807 | 5602.3714 | 0 | 15 | 8223.3717 | 0.55883 | 0.54822 | 5019.492 | 0 | 15 | 7365.5166 | 4926.7371 | 0 | 15 | 7229.0532 | 1 | -89.0994 | -90.9541 | -107.129 | -90.614 | -92.7549
x |  | Split-System_W_Furnace |  | SPLIT GS2 COOLING COIL | Split System | SPLIT GS2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GS2 COOLING COIL Cooling Capacity [ton] | 0.79438 | 0.78111 | 7053.8921 | 0 | 15 | 10361.9539 | 6940.534 | 0 | 15 | 10194.8211 | 0.70484 | 0.69203 | 6285.8741 | 0 | 15 | 9229.9945 | 6175.4694 | 0 | 15 | 9067.3476 | 0.66283 | 0.64704 | 5923.3083 | 0 | 15 | 8695.9381 | 5786.6371 | 0 | 15 | 8494.6757 | 0.67013 | 0.6531 | 5986.4074 | 0 | 15 | 8788.8679 | 5839.1495 | 0 | 15 | 8572.0022 | 0.59321 | 0.5778 | 5319.2458 | 0 | 15 | 7806.6142 | 5185.0368 | 0 | 15 | 7609.104 | 1 | -113.3581 | -110.4047 | -136.6712 | -147.2579 | -134.209
x |  | Split-System_W_Furnace |  | SPLIT GSW COOLING COIL | Split System | SPLIT GSW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT GSW COOLING COIL Cooling Capacity [ton] | 0.98423 | 0.97375 | 8661.8757 | 0 | 15 | 12734.8702 | 8573.8624 | 0 | 15 | 12604.8853 | 0.86899 | 0.85871 | 7689.1484 | 0 | 15 | 11298.9309 | 7601.8449 | 0 | 15 | 11170.1249 | 0.83268 | 0.81943 | 7380.5557 | 0 | 15 | 10843.6914 | 7267.6427 | 0 | 15 | 10677.1575 | 0.83162 | 0.81763 | 7371.5025 | 0 | 15 | 10830.3382 | 7252.301 | 0 | 15 | 10654.5318 | 0.74751 | 0.73308 | 6652.6532 | 0 | 15 | 9770.4652 | 6528.8128 | 0 | 15 | 9587.9556 | 1 | -88.0133 | -87.3035 | -112.913 | -119.2015 | -123.8404
x |  | Split-System_W_Furnace |  | SPLIT MN1 COOLING COIL | Split System | SPLIT MN1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MN1 COOLING COIL Cooling Capacity [ton] | 0.70501 | 0.69631 | 12574.5893 | 0 | 15 | 18464.1747 | 12424.6857 | 0 | 15 | 18243.3341 | 0.68651 | 0.6779 | 12255.6711 | 0 | 15 | 17994.3597 | 12107.0541 | 0 | 15 | 17775.4512 | 0.63025 | 0.6194 | 11282.1591 | 0 | 15 | 16560.7186 | 11093.8406 | 0 | 15 | 16283.4769 | 0.66526 | 0.65639 | 11888.5367 | 0 | 15 | 17453.6129 | 11735.1192 | 0 | 15 | 17227.6777 | 0.59193 | 0.58281 | 10616.1386 | 0 | 15 | 15580.3301 | 10457.2861 | 0 | 15 | 15346.549 | 2 | -149.9036 | -148.617 | -188.3185 | -153.4175 | -158.8525
x |  | Split-System_W_Furnace | All "SPLIT MXX" named cooling | SPLIT MN2 COOLING COIL | Split System | SPLIT MN2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MN2 COOLING COIL Cooling Capacity [ton] | 0.70285 | 0.69417 | 12537.5291 | 0 | 15 | 18409.5753 | 12387.8404 | 0 | 15 | 18189.0556 | 0.68451 | 0.67591 | 12221.1477 | 0 | 15 | 17943.5062 | 12072.65 | 0 | 15 | 17724.7776 | 0.62805 | 0.61722 | 11244.1212 | 0 | 15 | 16504.7171 | 11056.0351 | 0 | 15 | 16227.8231 | 0.66264 | 0.65384 | 11843.3216 | 0 | 15 | 17387.0236 | 11690.9983 | 0 | 15 | 17162.7051 | 0.58882 | 0.57978 | 10562.0393 | 0 | 15 | 15500.7107 | 10404.5275 | 0 | 15 | 15268.9091 | 2 | -149.6886 | -148.4976 | -188.0861 | -152.3233 | -157.5118
x |  | Split-System_W_Furnace | capacities are divided by 2 and | SPLIT MNE COOLING COIL | Split System | SPLIT MNE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MNE COOLING COIL Cooling Capacity [ton] | 0.8507 | 0.84002 | 15067.5895 | 0 | 15 | 22139.4662 | 14886.0656 | 0 | 15 | 21871.6929 | 0.82736 | 0.81784 | 14670.4892 | 0 | 15 | 21553.7206 | 14508.1892 | 0 | 15 | 21314.354 | 0.78763 | 0.77517 | 13992.4919 | 0 | 15 | 20553.9183 | 13779.4324 | 0 | 15 | 20239.8057 | 0.80625 | 0.79154 | 14310.5448 | 0 | 15 | 21022.8876 | 14059.3434 | 0 | 15 | 20652.4844 | 0.73128 | 0.7167 | 13026.746 | 0 | 15 | 19130.4059 | 12775.9022 | 0 | 15 | 18760.7799 | 2 | -181.5239 | -162.3 | -213.0595 | -251.2014 | -250.8438
x |  | Split-System_W_Furnace | resulting costs multiplied by 2. | SPLIT MNW COOLING COIL | Split System | SPLIT MNW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MNW COOLING COIL Cooling Capacity [ton] | 0.9774 | 0.96608 | 17209.0707 | 0 | 15 | 25300.3682 | 17018.6361 | 0 | 15 | 25019.1373 | 0.95587 | 0.94547 | 16846.8527 | 0 | 15 | 24765.4739 | 16671.6316 | 0 | 15 | 24506.7576 | 0.92064 | 0.90685 | 16252.756 | 0 | 15 | 23888.3778 | 16019.6978 | 0 | 15 | 23544.3758 | 0.9633 | 0.9484 | 16971.8471 | 0 | 15 | 24950.0442 | 16721.0815 | 0 | 15 | 24579.7687 | 0.90318 | 0.88788 | 15957.51 | 0 | 15 | 23452.5916 | 15698.5352 | 0 | 15 | 23070.3974 | 2 | -190.4345 | -175.2211 | -233.0582 | -250.7656 | -258.9748
x |  | Split-System_W_Furnace | These zones include 2 apts. | SPLIT MS1 COOLING COIL | Split System | SPLIT MS1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MS1 COOLING COIL Cooling Capacity [ton] | 0.74143 | 0.73239 | 13201.0113 | 0 | 15 | 19387.2199 | 13045.8264 | 0 | 15 | 19158.5235 | 0.70879 | 0.70028 | 12639.7267 | 0 | 15 | 18560.1418 | 12493.2086 | 0 | 15 | 18344.2811 | 0.6342 | 0.62383 | 11350.6913 | 0 | 15 | 16661.6182 | 11170.8351 | 0 | 15 | 16396.8245 | 0.70013 | 0.69031 | 12490.5133 | 0 | 15 | 18340.3103 | 12321.2649 | 0 | 15 | 18090.9828 | 0.63872 | 0.62888 | 11429.1302 | 0 | 15 | 16777.108 | 11258.5035 | 0 | 15 | 16525.8914 | 2 | -155.1848 | -146.5181 | -179.8562 | -169.2484 | -170.6267
x |  | Split-System_W_Furnace |  | SPLIT MS2 COOLING COIL | Split System | SPLIT MS2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MS2 COOLING COIL Cooling Capacity [ton] | 0.7394 | 0.73038 | 13166.0786 | 0 | 15 | 19335.7379 | 13011.1576 | 0 | 15 | 19107.4345 | 0.70705 | 0.69856 | 12609.879 | 0 | 15 | 18516.1667 | 12463.5087 | 0 | 15 | 18300.5271 | 0.63203 | 0.62195 | 11313.0622 | 0 | 15 | 16606.2166 | 11138.2047 | 0 | 15 | 16348.787 | 0.69748 | 0.68774 | 12444.9316 | 0 | 15 | 18273.1596 | 12276.8432 | 0 | 15 | 18025.547 | 0.63594 | 0.62618 | 11380.8679 | 0 | 15 | 16706.0483 | 11211.5532 | 0 | 15 | 16456.7697 | 2 | -154.921 | -146.3703 | -174.8575 | -168.0883 | -169.3147
x |  | Split-System_W_Furnace | see unit mult in col BH | SPLIT MSE COOLING COIL | Split System | SPLIT MSE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MSE COOLING COIL Cooling Capacity [ton] | 0.90012 | 0.88843 | 15905.7916 | 0 | 15 | 23376.2616 | 15707.7836 | 0 | 15 | 23084.0452 | 0.84498 | 0.83551 | 14970.3457 | 0 | 15 | 21996.0147 | 14809.1768 | 0 | 15 | 21758.2789 | 0.82514 | 0.77981 | 14632.5857 | 0 | 15 | 21497.8173 | 13858.7168 | 0 | 15 | 20356.6902 | 0.87757 | 0.86383 | 15523.7431 | 0 | 15 | 22812.4688 | 15290.6032 | 0 | 15 | 22468.4774 | 0.80957 | 0.79503 | 14367.1919 | 0 | 15 | 21106.4221 | 14119.0544 | 0 | 15 | 20740.5255 | 2 | -198.008 | -161.1689 | -773.8689 | -233.1399 | -248.1375
x |  | Split-System_W_Furnace |  | SPLIT MSW COOLING COIL | Split System | SPLIT MSW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT MSW COOLING COIL Cooling Capacity [ton] | 1.011 | 0.99937 | 17772.5938 | 0 | 15 | 26132.7334 | 17577.83 | 0 | 15 | 25845.0255 | 0.97352 | 0.96316 | 17143.7094 | 0 | 15 | 25203.8405 | 16969.4547 | 0 | 15 | 24946.5114 | 0.93212 | 0.91807 | 16446.4766 | 0 | 15 | 24174.3479 | 16209.237 | 0 | 15 | 23824.1391 | 0.99954 | 0.98386 | 17580.6918 | 0 | 15 | 25849.2527 | 17317.6142 | 0 | 15 | 25460.6762 | 0.94325 | 0.92729 | 16634.2002 | 0 | 15 | 24451.4926 | 16365.0377 | 0 | 15 | 24054.1244 | 2 | -194.7637 | -174.2546 | -237.2396 | -263.0775 | -269.1624
x |  | Split-System_W_Furnace |  | SPLIT OFFICE COOLING C | Split System | SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT OFFICE COOLING COIL Cooling Capacity [ton] | 1.832 | 1.7461 | 15542.3439 | 0 | 15 | 22931.9511 | 14864.9822 | 0 | 15 | 21925.1027 | 1.694 | 1.5722 | 14451.9845 | 0 | 15 | 21311.5147 | 13480.7554 | 0 | 15 | 19869.4901 | 1.8067 | 1.7039 | 15343.0668 | 0 | 15 | 22635.6769 | 14530.1851 | 0 | 15 | 21427.679 | 1.6468 | 1.5121 | 14076.6697 | 0 | 15 | 20754.1141 | 12998.8089 | 0 | 15 | 19154.414 | 1.5311 | 1.445 | 13151.1183 | 0 | 15 | 19380.3637 | 12457.1047 | 0 | 15 | 18351.0687 | 1 | -677.3616 | -971.2291 | -812.8817 | -1077.8608 | -694.0136
x |  | Split-System_W_Furnace | curve fits for labor and material | SPLIT TN1 COOLING COIL | Split System | SPLIT TN1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TN1 COOLING COIL Cooling Capacity [ton] | 0.86648 | 0.85784 | 7667.8187 | 0 | 15 | 11267.4605 | 7594.4311 | 0 | 15 | 11159.1873 | 0.86073 | 0.85225 | 7619.0127 | 0 | 15 | 11195.453 | 7547.0125 | 0 | 15 | 11089.2321 | 0.8259 | 0.81499 | 7322.7841 | 0 | 15 | 10758.4824 | 7229.8534 | 0 | 15 | 10621.4271 | 0.82875 | 0.81934 | 7347.098 | 0 | 15 | 10794.3431 | 7266.8914 | 0 | 15 | 10676.0496 | 0.75307 | 0.74377 | 6700.3337 | 0 | 15 | 9840.7407 | 6620.5677 | 0 | 15 | 9723.1771 | 1 | -73.3876 | -72.0002 | -92.9307 | -80.2067 | -79.766
x |  | Split-System_W_Furnace | Material (2012 estimate) | SPLIT TN2 COOLING COIL | Split System | SPLIT TN2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TN2 COOLING COIL Cooling Capacity [ton] | 0.86163 | 0.85301 | 7626.6177 | 0 | 15 | 11206.673 | 7553.4394 | 0 | 15 | 11098.7134 | 0.85645 | 0.84799 | 7582.6693 | 0 | 15 | 11141.8351 | 7510.762 | 0 | 15 | 11035.7553 | 0.84338 | 0.80979 | 7471.5716 | 0 | 15 | 10977.9438 | 7185.5 | 0 | 15 | 10556.019 | 0.84963 | 0.83979 | 7524.7322 | 0 | 15 | 11056.3639 | 7441.0251 | 0 | 15 | 10932.8849 | 0.74635 | 0.73722 | 6642.7481 | 0 | 15 | 9755.8668 | 6564.3731 | 0 | 15 | 9640.3602 | 1 | -73.1782 | -71.9072 | -286.0716 | -83.7071 | -78.375
x |  | Split-System_W_Furnace | y = 17.693x2 - 208.45x + 2690.6 | SPLIT TNE COOLING COIL | Split System | SPLIT TNE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TNE COOLING COIL Cooling Capacity [ton] | 1.0592 | 1.0483 | 9289.1263 | 0 | 15 | 13661.5859 | 9198.4793 | 0 | 15 | 13527.6247 | 1.0473 | 1.0372 | 9190.31 | 0 | 15 | 13515.5525 | 9106.0596 | 0 | 15 | 13391.0567 | 1.0393 | 1.0271 | 9123.5762 | 0 | 15 | 13416.9399 | 9021.0458 | 0 | 15 | 13265.4437 | 1.0417 | 1.03 | 9143.5133 | 0 | 15 | 13446.4002 | 9045.4043 | 0 | 15 | 13301.4336 | 0.94186 | 0.92925 | 8305.3799 | 0 | 15 | 12208.4426 | 8199.0175 | 0 | 15 | 12051.4179 | 1 | -90.647 | -84.2504 | -102.5305 | -98.109 | -106.3624
x |  | Split-System_W_Furnace | Labor | SPLIT TNW COOLING COIL | Split System | SPLIT TNW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TNW COOLING COIL Cooling Capacity [ton] | 1.1912 | 1.1797 | 10384.6639 | 0 | 15 | 15281.5928 | 10289.5302 | 0 | 15 | 15140.8438 | 1.1706 | 1.1603 | 10214.8239 | 0 | 15 | 15030.3264 | 10129.077 | 0 | 15 | 14903.4864 | 1.1877 | 1.1733 | 10356.0372 | 0 | 15 | 15239.2385 | 10236.9127 | 0 | 15 | 15063.0028 | 1.195 | 1.1788 | 10415.8858 | 0 | 15 | 15327.7882 | 10282.6492 | 0 | 15 | 15130.664 | 1.119 | 1.1026 | 9787.3006 | 0 | 15 | 14398.0277 | 9650.5632 | 0 | 15 | 14195.854 | 1 | -95.1337 | -85.7468 | -119.1244 | -133.2366 | -136.7373
x |  | Split-System_W_Furnace | y = 6.1014x2 - 73.657x + 2202.7 | SPLIT TS1 COOLING COIL | Split System | SPLIT TS1 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TS1 COOLING COIL Cooling Capacity [ton] | 0.94614 | 0.93602 | 8341.4945 | 0 | 15 | 12261.7631 | 8256.1107 | 0 | 15 | 12135.7034 | 0.90692 | 0.89812 | 8010.4139 | 0 | 15 | 11773.0219 | 7935.9451 | 0 | 15 | 11663.1143 | 0.88 | 0.86952 | 7782.4929 | 0 | 15 | 11436.6629 | 7693.6598 | 0 | 15 | 11305.5873 | 0.92679 | 0.91561 | 8178.2347 | 0 | 15 | 12020.738 | 8083.8631 | 0 | 15 | 11881.433 | 0.85356 | 0.84165 | 7558.1506 | 0 | 15 | 11105.6636 | 7456.8438 | 0 | 15 | 10956.2187 | 1 | -85.3838 | -74.4688 | -88.8332 | -94.3716 | -101.3069
x |  | Split-System_W_Furnace | Updated to 2018 with labor and | SPLIT TS2 COOLING COIL | Split System | SPLIT TS2 COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TS2 COOLING COIL Cooling Capacity [ton] | 0.94818 | 0.93801 | 8358.6722 | 0 | 15 | 12287.1255 | 8272.9682 | 0 | 15 | 12160.5907 | 0.90913 | 0.90029 | 8029.046 | 0 | 15 | 11800.522 | 7954.3513 | 0 | 15 | 11690.2789 | 0.88505 | 0.87455 | 7825.2641 | 0 | 15 | 11499.7771 | 7736.2542 | 0 | 15 | 11368.435 | 0.9289 | 0.91764 | 8196.066 | 0 | 15 | 12047.0607 | 8100.9674 | 0 | 15 | 11906.6802 | 0.85674 | 0.84455 | 7585.157 | 0 | 15 | 11145.5052 | 7481.534 | 0 | 15 | 10992.6395 | 1 | -85.7041 | -74.6947 | -89.0098 | -95.0985 | -103.623
x |  | Split-System_W_Furnace | material inflation multipliers. | SPLIT TSE COOLING COIL | Split System | SPLIT TSE COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TSE COOLING COIL Cooling Capacity [ton] | 1.1276 | 1.116 | 9858.6522 | 0 | 15 | 14503.5362 | 9762.2539 | 0 | 15 | 14360.9926 | 1.0953 | 1.0852 | 9590.4838 | 0 | 15 | 14107.0322 | 9505.7518 | 0 | 15 | 13981.7732 | 1.0764 | 1.0641 | 9432.5546 | 0 | 15 | 13873.5748 | 9330.683 | 0 | 15 | 13723.0041 | 1.1238 | 1.1094 | 9826.8288 | 0 | 15 | 14456.4776 | 9707.6293 | 0 | 15 | 14280.2258 | 1.0384 | 1.0241 | 9115.8284 | 0 | 15 | 13405.4914 | 8996.0862 | 0 | 15 | 13228.5665 | 1 | -96.3984 | -84.732 | -101.8716 | -119.1996 | -119.7422
x |  | Split-System_W_Furnace | See cells F1:G1 | SPLIT TSW COOLING COIL | Split System | SPLIT TSW COOLING COIL Cooling Capacity [ton] | US_MA_SPLIT TSW COOLING COIL Cooling Capacity [ton] | 1.23 | 1.2184 | 10704.6523 | 0 | 15 | 15755.1106 | 10608.5365 | 0 | 15 | 15612.8626 | 1.1977 | 1.1872 | 10438.3755 | 0 | 15 | 15361.0643 | 10351.8832 | 0 | 15 | 15233.0927 | 1.2097 | 1.1951 | 10536.9511 | 0 | 15 | 15506.9277 | 10417.1289 | 0 | 15 | 15329.6274 | 1.2457 | 1.2288 | 10833.6833 | 0 | 15 | 15946.0934 | 10694.3619 | 0 | 15 | 15739.8806 | 1.1693 | 1.1503 | 10203.9421 | 0 | 15 | 15014.229 | 10046.3161 | 0 | 15 | 14781.0737 | 1 | -96.1158 | -86.4923 | -119.8222 | -139.3213 | -157.626
x | 90.1-16g occ standby controls | occ_standby | 32 conditioned zones |  |  |  |  | 0 | 32 | 0 | 0 | 0 | 0 | 964.6615 | 0 | 15 | 1692.8672 | 0 | 32 | 0 | 0 | 0 | 0 | 964.6615 | 0 | 15 | 1692.8672 | 0 | 32 | 0 | 0 | 0 | 0 | 964.6615 | 0 | 15 | 1692.8672 | 0 | 32 | 0 | 0 | 0 | 0 | 964.6615 | 0 | 15 | 1692.8672 | 0 | 32 | 0 | 0 | 0 | 0 | 964.6615 | 0 | 15 | 1692.8672 |  | 964.6615 | 964.6615 | 964.6615 | 964.6615 | 964.6615
90.1-16 bo furnace efficiency
x |  | Furnace_eff_apt | 32 units |  |  | Furnace heating capacity [Btuh] | US_MA_Furnace heating capacity [Btuh] | 32 | 32 | 48065.7035 | 0 | 15 | 64421.7283 | 49203.2651 | 0 | 15 | 65673.046 | 32 | 32 | 48065.7035 | 0 | 15 | 64421.7283 | 49203.2651 | 0 | 15 | 65673.046 | 32 | 32 | 48065.7035 | 0 | 15 | 64421.7283 | 49203.2651 | 0 | 15 | 65673.046 | 32 | 32 | 48065.7035 | 0 | 15 | 64421.7283 | 49203.2651 | 0 | 15 | 65673.046 | 32 | 32 | 48065.7035 | 0 | 15 | 64421.7283 | 49203.2651 | 0 | 15 | 65673.046 |  | 1137.5616 | 1137.5616 | 1137.5616 | 1137.5616 | 1137.5616
90.1-16 ay & h - ERV
x |  | ERV_multifamily | [5 empty] | 32 | 32 | 65099.0234 | 0 | 15 | 70211.0438 | 75357.7682 | 480 | 15 | 81892.1116 | 32 | 32 | 65099.0234 | 0 | 15 | 70211.0438 | 75357.7682 | 480 | 15 | 81892.1116 | 32 | 32 | 65099.0234 | 0 | 15 | 70211.0438 | 75357.7682 | 480 | 15 | 81892.1116 | 32 | 32 | 65099.0234 | 0 | 15 | 70211.0438 | 78720 | 480 | 15 | 85600 | 32 | 32 | 65099.0234 | 0 | 15 | 70211.0438 | 78720 | 480 | 15 | 85600 |  | 10258.7448 | 10258.7448 | 10258.7448 | 13620.9766 | 13620.9766
[8 empty] | 86.4752 | 118.1554 | 369637.0211 |  |  |  | 378654.305 |  |  |  | 85.268 | 116.9233 | 357413.6473 |  |  |  | 366277.2907
[10 empty] | 369637.0211 |  |  | 511654.8615 | 378654.305 |  |  | 521338.7028 |  |  | 357413.6473 |  |  | 493612.6503 | 366277.2907 |  |  | 503069.8836 |  |  | 348463.0086 |  |  | 480432.9109 | 356054.5001 |  |  | 488015.9 |  |  | 354779.9994 |  |  | 489736.2103 | 366206.8531 |  |  | 501721.975 |  |  | 333912.0184 |  |  | 458960.9745 | 345631.6847 |  |  | 471385.9948
The regressions for bare costs + 10% (subcontractor cost level) are:
|  | material | labor
| C | 2690.6 | 2202.7
| x | -208.45 | -73.657
| x^2 | 17.693 | 6.1014

## Int Ltg LPD Methodology
90. 1 Cost Effectiveness - Interior Lighting Power Density Allowance Cost Calculation – Methodology
90.1-2019, Chapter 9, includes requirements for maximum lighting power density (LPD). There are both mandatory and prescriptive requirements. A total of three compliance paths exist, but the primary compliance paths are Table 9.5.1, which includes LPDs that are applied to an entire building area and Table 9.6.1, which allows assignment of maximum LPDs to specific space types.
Addenda to 90.1-16 updated the values in both Tables 9.5.1 and 9.6.1 of the standard. The maximum allowed LPD values decrease generally with some exceptions.
Part of the basis for the cost development is the use of the existing set of building space models that are used by the 90.1 lighting subcommittee to develop the LPD values in the Standard.
The models incorporate the various interior lighting design elements including:
• IES recommended light levels
• More surface reflectance options
• Light fixture efficacy
• Light loss factors
• Fixture coefficient of utilization (CU) related to expected room geometry
• Committee design expertise
In the development of LPD values for Standard 90.1-2019, the IES light level recommendations set the amount of light needed for the each space type. 90.1 Lighting Subcommittee design experts then determine an appropriate application mix of fixture types and lighting sources and what portion of the recommended light level(s) is provided by each combination. The mix of lighting technology for each space type is defined for both the baseline 90.1-2016 and the 90.1-2019 which is an aggressive yet achievable and realistic design model for typical spaces that strives to implement the 90.1 required LPD (W/ft2) maximum achievable energy efficiency while retaining reasonable and necessary design flexibility.
Finally, the combined fixture efficacy, loss factors, and CU values for the various fixtures and sources is used to calculate the wattage needed to provide the recommended level of lighting based on the efficacy of the sources and efficiency of fixtures involved. Each space type in the model has a total footcandle requirement to meet recommended light levels. There are up to four lighting systems that can be used in each space type and each system provides an assigned percentage of the overall total footcandles for that space. These percentages determine the amount of each luminaire type and its wattage needed to provide the required light levels. Note the worksheets that define the 90.1 lighting model are not included. Worksheets shown begin with the fixture costs by fixture ID, and the Int Lighting LPD Cost Detail contains the information on how these fixtures are applied to the different space types based on the LPD levels determined in the lighting models.
For cost development, the same basic modeling process is used but modified to produce realistic cost data that parallels the LPD development and therefore most effectively represents costs directly related to energy code requirements. To implement this, the LPD model process is first modified to calculate quantities of complete luminaires (fixture plus lighting source or lamp) needed to provide the recommended light levels. Then, costs for the specified luminaires are applied to generate a cost per square foot value for each space type within each Standard for comparison. The resulting calculations provide a $/ft2 value that is considered directly relatable to the LPD requirements in each standard.
The development of the costs for the luminaires used in the models first involved extracting a list of all the unique products used within both the 2016 and 2019 90.1 sets of lighting building models. Reputable sources, easily accessible to the general public, were used to cost these lighting components and appropriate installation labor. RS Means, an accepted authority within the construction industry, was used for labor costs (RS Means 2020). Fixture and lamp costs were determined using Grainger’s on-line catalog (Grainger 2020). The cost, lamp life, and complete luminaire wattage were noted. Fixture Cost per Watt ($/W) was calculated by dividing the fixture wattage by total luminaire cost (lamp, fixture, labor).
Modifying the LPD model process to calculate costs per square foot involved changing the wattage portion of the calculation explained above to cost. In this cost analysis, these same percentages are applied to the luminaire cost data to determine the total space cost associated with meeting the requirements in the Standard.
The basic cost calculation for each luminaire type within a space takes the form of:
Cost per square foot = (total space footcandles x percent of footcandles provided by lighting system x Fixture Cost per Watt)/ (efficacy of the lighting system in Lumens per Watt)
Costs are developed for each fixture including fixture cost, lamp cost, installation cost, replacement lamp cost and installation cost, and hours of lamp life for each lamp type. When the costs are combined by space type for each prototype, the replacement cycle is determined by dividing the annual full load equivalent hours from the corresponding energy model schedule, which include fractions of full load operation during each hour of the day.
The database of real building details available for development of the LPDs includes approximately 250 buildings. However, for this cost estimate, only those buildings that are classified as one of the 16 prototypes were used to calculate average whole building $/sqft for both Standard years.
Once the costs are assigned to each prototype and its corresponding space types, these are summed up for each prototype. The cost for each prototype is totaled and the incremental cost is the difference between the 90.1-2016 and 90.1-2019 costs. Replacement cost incremental costs have to be kept separated into the replacement lives, e.g. year 5 replacement if any for 90.1-2016 and 90.1-2019.
Cost estimation for the IECC models - methodology
The 2006, 2009 and the high efficiency lighting option in the 2012 IECC (modeled option for this case) include only whole building LPDs. In order to implement these LPDs, the following procedure was used:
- whole building LPDs were calculated for the 90.1-2004 cases from the space-by-space LPDs and zones areas
- Scaling factors were then calculated based on the 90.1-2004 calculated whole building LPDs, to match the IECC requirements
- The scaling factors were then used to scale each space-by-space LPD such that it yielded the correct whole building level LPD
For cost estimation, a similar strategy is used, in that the space-by-space LPDs are scaled to match the modeled space-by-space LPD from above. Because different prototypes have different IECC scaling factors, the IECC LPD for the same space type is different in different prototypes. Hence, the costs for the same space type also vary by prototype.
Once the required space-by-sapce LPDs are calculated, the methodology for determining the fixture type and counts remains the same as 90.1.
Note about Apartments:
- The 2009 and 2012 IECC require 50% and 75% respectively of all permanently installed fixtures to have high efficacy lamps. These requirements do not exist in 90.1.
- The baseline 2006 IECC in simulation is kept the same as 90.1-2004. 90.1-2004 uses Building America Benchmark definition for the LPD (refer 90.1 LPD Requirement spreadsheet under _p.require). This baseline includes an assumption of % flourescent. These fractions are adjusted to match the 2009 and 2012 IECC requirements. The LPD is used in conjunction with a lighting usage profile to yield lighting energy.
- While this approach results in an accurate representation of the energy profile, it is not very useful in determining incremental costs due to the normalization of the LPD for modeling purposes. In reality, home have many more connected fixtures (higher connected LPD) and only a subset operates at any given time.
- Thus, in order to cost out lighting requirements, a detailed lighting fixture sheet is derived from the NC3 data. The fixtures are then changed to high efficacy fixtures to meet the IECC requirements. The calculations are detailed in the dwelling_units tab in this workbook.
- NC3 data had two apartments - one a basic low-end apartment with minimal fixtures and another high-end apartment with more detailed fixtures. This sheet includes costs for the high-end apartment.
Note about changes since the 90.1 cost estimate: (Per Eric's note - email dtd. 5/6/2013)
The initial 90.1-2007 to 90.1-2010 cost effectiveness analysis considered slightly different equipment options for costing based on the fact that current federal rulemakings have eliminated some specific incandescent products. In the 2007 timeframe, the standard incandescent lamps were available (60, 75, 100) but for a timeframe where 90.1-2010 would typically be adopted, these would effectively be replaced with more efficient and therefore lower wattage and different cost options. The costs associated with these equipment were used for costing the 90.1-2010 option.
However, for cost comparison of options, the costs for applicable equipment should be the same for any and all options for the same equipment. Therefore, for the current analysis, the costs associated with the newer technologies available in the 2010 adoption timeframe were applied to both options.
Internal Instructions for LPD tabs:
[Int Lighting Comp]
Fixture and lamp cost, life and wattage information
Note that the NEW table reads from the BASE table, so fixture IDs are identical
Each line in BASE table is assigned a lookup fixture ID
[Int Ltg LPD Space Type Comp]
The BASE code information is entered it the top table, the NEW code information in the lower table
Each line is assigned a lookup space name (first line) plus fixture ID [col B]
Unused lines must have ID 0
ASHRAE LSC model # entered in [col D] space LPD [col E] - first line of space
and W/sf in [col O] for each fixture ID [col F]
The rest of the cost factors/sf are calculated.
A current quirk is that BASE allows 3 fixt ID/space, and NEW allows 4
[Int Ltg LPD Proto]
Aligned in groups of 4, BASE and NEW space/fixture codes are entered [col B/C]
Prototypes affected marked [col H-M]; climates not necessary.
BASE descriptive comments may be added [Col V]
EFLH in [col X] for BASE and [col AD] for NEW for each building
Note - this is not by space type as noted, but by building type except for small hotel where it is by space
Area in protototypes BASE in first line each space [col Z]
Area in protototypes NEW in first line each space [col AE]
Remainder of cells appear to be calculated

## Int Ltg LPD Summary
Commercial Energy Code Cost Effectiveness - Interior Lighting LPD - Cost Summary Depending on Choice of Base Code and Target Code
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
Base Code | 2016 |  | Target Code | 2019 |  | Incremental Cost |  | Base Code | 2016 |  | Target Code | 2019 |  | Incremental Cost |  | Base Code | 2016 |  | Target Code | 2019 |  | Incremental Cost |  | Base Code | 2016 |  | Target Code | 2019 |  | Incremental Cost |  | Base Code | 2016 |  | Target Code | 2019 |  | Incremental Cost |  | Base Code | 2016 |  | Target Code | 2019 |  | Incremental Cost
Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
New Construction | 127729.4835 | 127729.4835 | New Construction | 117687.4475 | 117687.4475 | -10042.036 | -10042.036 | New Construction | 11579260.8433 | 11579260.8433 | New Construction | 10668902.0566 | 10668902.0566 | -910358.7867 | -910358.7867 | New Construction | 358532.6129 | 358532.6129 | New Construction | 328325.5382 | 328325.5382 | -30207.0748 | -30207.0748 | New Construction | 916122.7479 | 916122.7479 | New Construction | 770565.3464 | 770565.3464 | -145557.4015 | -145557.4015 | New Construction | 377768.7015 | 377768.7015 | New Construction | 406437.254 | 406437.254 | 28668.5525 | 28668.5525 | New Construction | 69144.7631 | 69144.7631 | New Construction | 47156.228 | 47156.228 | -21988.5351 | -21988.5351
Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0 | Replacement - Year |  |  | Replacement - Year | 0 | 0 | 0 | 0
1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 20884.6319 | 20884.6319 | 1 | 0 | 0 | -20884.6319 | -20884.6319 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 20884.6319 | 2 | 0 | 0 | -20884.6319 | -20884.6319 | 2 | 528.8638 | 528.8638 | 2 | 68.2405 | 68.2405 | -460.6233 | -460.6233
3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 37857.1874 | 58741.8193 | 3 | 0 | 0 | -58741.8193 | -58741.8193 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 20884.6319 | 4 | 0 | 0 | -20884.6319 | -20884.6319 | 4 | 0 | 528.8638 | 4 | 0 | 68.2405 | -460.6233 | -460.6233
5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 232.7298 | 21117.3617 | 5 | 0 | 0 | -21117.3617 | -21117.3617 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 135670.3716 | 194412.1909 | 6 | 94347.8392 | 94347.8392 | -100064.3517 | -100064.3517 | 6 | 63156.8524 | 63685.7162 | 6 | 43715.9604 | 43784.2009 | -19901.5153 | -19901.5153
7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 7673.9739 | 28558.6057 | 7 | 17024.6528 | 17024.6528 | -11533.953 | -11533.953 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 20884.6319 | 8 | 0 | 0 | -20884.6319 | -20884.6319 | 8 | 0 | 528.8638 | 8 | 0 | 68.2405 | -460.6233 | -460.6233
9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 28420.2502 | 87162.0695 | 9 | 21396.1611 | 21396.1611 | -65765.9084 | -65765.9084 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 17.3674 | 17.3674 | 10 | 0 | 0 | -17.3674 | -17.3674 | 10 | 2290.3509 | 2290.3509 | 10 | 0 | 0 | -2290.3509 | -2290.3509 | 10 | 0 | 21117.3617 | 10 | 0 | 0 | -21117.3617 | -21117.3617 | 10 | 0 | 528.8638 | 10 | 0 | 68.2405 | -460.6233 | -460.6233
11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 20884.6319 | 11 | 0 | 0 | -20884.6319 | -20884.6319 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 12354.5122 | 206766.7031 | 12 | 14000.1555 | 108347.9947 | -98418.7083 | -98418.7083 | 12 | 0 | 63685.7162 | 12 | 0 | 43784.2009 | -19901.5153 | -19901.5153
13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 4533.0008 | 25417.6326 | 13 | 8659.795 | 8659.795 | -16757.8377 | -16757.8377 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
14 | 124443.0313 | 124443.0313 | 14 | 114685.1443 | 114685.1443 | -9757.887 | -9757.887 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 421205.0681 | 421205.0681 | 14 | 375158.7975 | 375158.7975 | -46046.2706 | -46046.2706 | 14 | 1029845.9836 | 1029845.9836 | 14 | 885684.5554 | 885684.5554 | -144161.4282 | -144161.4282 | 14 | 42932.2072 | 71490.8129 | 14 | 252954.6848 | 269979.3376 | 198488.5247 | 198488.5247 | 14 | 0 | 528.8638 | 14 | 0 | 68.2405 | -460.6233 | -460.6233
15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 58974.5491 | 15 | 0 | 0 | -58974.5491 | -58974.5491 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 5280.2353 | 26164.8672 | 16 | 6409.7483 | 6409.7483 | -19755.1188 | -19755.1188 | 16 | 15690.9328 | 16219.7966 | 16 | 8708.5897 | 8776.8302 | -7442.9664 | -7442.9664
17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 20884.6319 | 17 | 0 | 0 | -20884.6319 | -20884.6319 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 11700825.0465 | 11700825.0465 | 18 | 10783334.3055 | 10783334.3055 | -917490.7411 | -917490.7411 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 222832.4411 | 18 | 0 | 115744.0002 | -107088.4408 | -107088.4408 | 18 | 0 | 63685.7162 | 18 | 0 | 43784.2009 | -19901.5153 | -19901.5153
19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 20884.6319 | 19 | 0 | 0 | -20884.6319 | -20884.6319 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 17.3674 | 20 | 0 | 0 | -17.3674 | -17.3674 | 20 | 0 | 2290.3509 | 20 | 0 | 0 | -2290.3509 | -2290.3509 | 20 | 0 | 21117.3617 | 20 | 0 | 0 | -21117.3617 | -21117.3617 | 20 | 386.4405 | 915.3043 | 20 | 1380.1447 | 1448.3852 | 533.0809 | 533.0809
21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 66415.7932 | 21 | 0 | 17024.6528 | -49391.1404 | -49391.1404 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 20884.6319 | 22 | 0 | 0 | -20884.6319 | -20884.6319 | 22 | 0 | 528.8638 | 22 | 0 | 68.2405 | -460.6233 | -460.6233
23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 20884.6319 | 23 | 0 | 0 | -20884.6319 | -20884.6319 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 11912.5628 | 218679.2659 | 24 | 8940.9575 | 117288.9522 | -101390.3136 | -101390.3136 | 24 | 0 | 63685.7162 | 24 | 0 | 43784.2009 | -19901.5153 | -19901.5153
25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 21117.3617 | 25 | 0 | 0 | -21117.3617 | -21117.3617 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 25417.6326 | 26 | 0 | 8659.795 | -16757.8377 | -16757.8377 | 26 | 0 | 528.8638 | 26 | 0 | 68.2405 | -460.6233 | -460.6233
27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 87162.0695 | 27 | 0 | 21396.1611 | -65765.9084 | -65765.9084 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
28 | 0 | 124443.0313 | 28 | 0 | 114685.1443 | -9757.887 | -9757.887 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 421205.0681 | 28 | 0 | 375158.7975 | -46046.2706 | -46046.2706 | 28 | 0 | 1029845.9836 | 28 | 0 | 885684.5554 | -144161.4282 | -144161.4282 | 28 | 0 | 71490.8129 | 28 | 0 | 269979.3376 | 198488.5247 | 198488.5247 | 28 | 0 | 528.8638 | 28 | 0 | 68.2405 | -460.6233 | -460.6233
29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 20884.6319 | 29 | 0 | 0 | -20884.6319 | -20884.6319 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
30 | 0 | 0 | 30 | 0 | 0 | 8363.9032 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 305830.247 | 0 | 30 | 0 | 17.3674 | 30 | 0 | 0 | 39468.232 | -17.3674 | 30 | 0 | 2290.3509 | 30 | 0 | 0 | 123566.9385 | -2290.3509 | 30 | 0 | 194644.9207 | 30 | 0 | 94347.8392 | -183607.915 | -100297.0815 | 30 | 0 | 63685.7162 | 30 | 0 | 43784.2009 | 375.9408 | -19901.5153
31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 20884.6319 | 31 | 0 | 0 |  | -20884.6319 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 26164.8672 | 32 | 0 | 6409.7483 |  | -19755.1188 | 32 | 0 | 16219.7966 | 32 | 0 | 8776.8302 |  | -7442.9664
33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 58741.8193 | 33 | 0 | 0 |  | -58741.8193 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 20884.6319 | 34 | 0 | 0 |  | -20884.6319 | 34 | 0 | 528.8638 | 34 | 0 | 68.2405 |  | -460.6233
35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 28791.3355 | 35 | 0 | 17024.6528 |  | -11766.6827 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 11700825.0465 | 36 | 0 | 10783334.3055 |  | -917490.7411 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 235186.9532 | 36 | 0 | 129744.1558 |  | -105442.7974 | 36 | 0 | 63685.7162 | 36 | 0 | 43784.2009 |  | -19901.5153
37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 20884.6319 | 37 | 0 | 0 |  | -20884.6319 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 20884.6319 | 38 | 0 | 0 |  | -20884.6319 | 38 | 0 | 528.8638 | 38 | 0 | 68.2405 |  | -460.6233
39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 63274.82 | 39 | 0 | 8659.795 |  | -54615.0251 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
40 | 0 | 0 | 40 | 0 | 0 |  | 1393.9839 | 40 | 0 | 0 | 40 | 0 | 0 |  | 713603.9097 | 40 | 0 | 0 | 40 | 0 | 0 |  | 6578.0387 | 40 | 0 | 0 | 40 | 0 | 0 |  | 20594.4897 | 40 | 0 | 0 | 40 | 0 | 0 |  | 5759.075 | 40 | 0 | 0 | 40 | 0 | 0 |  | 9971.4689
Residual Year 30 |  | -106665.4554 | Residual Year 30 | 0 | -98301.5523 |  | 8363.9032 | Residual Year 30 |  | -3900275.0155 | Residual Year 30 | 0 | -3594444.7685 |  | 305830.247 | Residual Year 30 |  | -361032.9155 | Residual Year 30 | 0 | -321564.6836 |  | 39468.232 | Residual Year 30 |  | -882725.1288 | Residual Year 30 | 0 | -759158.1903 |  | 123566.9385 | Residual Year 30 |  | -80137.217 | Residual Year 30 | 0 | -263745.132 |  | -183607.915 | Residual Year 30 |  | -2154.5869 | Residual Year 30 | 0 | -1778.6461 |  | 375.9408
Residual Year 40 |  | -17777.5759 | Residual Year 40 | 0 | -16383.592 |  | 1393.9839 | Residual Year 40 |  | -9100641.7028 | Residual Year 40 | 0 | -8387037.7931 |  | 713603.9097 | Residual Year 40 |  | -60172.1526 | Residual Year 40 | 0 | -53594.1139 |  | 6578.0387 | Residual Year 40 |  | -147120.8548 | Residual Year 40 | 0 | -126526.3651 |  | 20594.4897 | Residual Year 40 |  | -113607.9682 | Residual Year 40 | 0 | -107848.8932 |  | 5759.075 | Residual Year 40 |  | -28897.7506 | Residual Year 40 | 0 | -18926.2817 |  | 9971.4689

## Int Ltg LPD Proto 90_1
[16 empty] | Commercial Energy Code Cost Effectiveness - Interior Lighting Power Density - 90.1 2016 and 2019 - Costs Totals for Each Prototype | [20 empty] | Warning! Formulas below are different in greyed areas for ballast replacements | [23 empty] | Warning! Formulas below are different in greyed areas for ballast replacements | [23 empty] | 90.1 Cost Effectiveness - Interior Lighting Power Density 90.1-07by and 90.1-07de Costs - Prototype
Summary
Addenda 90.1-10bh, co, cr, dj, and dl change the interior lighting power allowances in Tables 9.5.1 for the building area method and Table 9.6.1 for the space by space method.
The cost of interior lighting for the prototypes that meets the lighting power allowances for 90.1-2016 and 90.1-2019 are shown below.
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
[16 empty] | Col22 | LPD2013 | Fixture ID Numbers | Col25 | area2013 | Col27 | LPD2016 | Col29 | Col30 | area2016 | Col32 | Col33 | Col34 | Col35 | Col36 | Mat2013 | Col38 | Col39 | Lab2013 | Col41 | Col42 | Col43 | Col44 | Tot2013 | Col46 | Col47 | Col48 | Col49 | Col50 | Col51 | Col52 | Col53 | Col54 | Col55 | Col56 | Rep2010 | Col58 | Mat2016 | Col60 | Col61 | Lab2016 | Col63 | Col64 | Col65 | Col66 | Tot2016 | Col68 | Col69 | Col70 | Col71 | Col72 | Col73 | Col74 | Col75 | Col76 | Col77 | Col78 | Repl2016 | Incremental | Repl | Col82 | Proto | Space | Col85 | Col86 | Col87 | Col88 | Col89 | Col90
[16 empty] | 90.1-2016 |  |  |  |  | 90.1-2019 | [8 empty] | 90.1-2016 Baseline Costs - without implementation of the addenda. | [21 empty] | 90.1-2019 - costs with addendum | [21 empty] | Incremental Costs | Incremental Costs | [9 empty] | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
|  | Prototypes Affected (X) | [5 empty] | Not Used | [5 empty] | Name of Item | [11 empty] | LPA |  |  |  | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | New Construction Costs | [9 empty] | Replacement Costs | [22 empty] | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost |  | 90.1-2016 |  |  | 90.1-2019 |  |  | Incremental Cost
90.1-2016 Lookup | 90.1-2019 Lookup | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | [5 empty] | Not Used | Interior Lighting Power Density | Not Used | Costs to provide lighting fixtures, lamps and ballasts to meet space by space lighting power density (LPD) maximum allowed LPD values under 90.1-2016. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs are for equipment etc. at today's prices that just meet the 90.1-2016 requirements. Costs by 90.1-2016 Prototype and Lighting Space Type | 90.1-2016 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent Operating Hours for Space Type Lamp Life for Fixtures (Used to Calculate Replacement Life) | Area of Space Type In Prototype Models | Costs to provide lighting fixtures, lamps and ballasts to meet space by space maximum allowed LPD values under 90.1-2019 Table 9.6.1. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs by 90.1-2019 Prototype and Lighting Space Type | 90.1-2019 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent (BLE) Operating Hours | Area of Space Type, ft2 | Baseline # of fixtures | Baseline Sq. Ft. per fixture | NEW # of fixtures | Baseline Sq. Ft. per fixture | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments (with added replacement labor hours) | Not Used | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments (with added replacement labor hours) | Incremental Added Design with OH&P | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | New Construction Costs 90.1-2019 minus 90.1-2016 | Replacement Costs 90.1-2019 minus 90.1-2016 | line item repl costs |  | Space Name |  |  | 2013 Fixture in Space | 2016 Fixture in Space |  |  | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[85 empty] | New Construction | 127729.4835 | 127729.4835 | New Construction | 117687.4475 | 117687.4475 | -10042.036 | -10042.036 | New Construction | 11579260.8433 | 11579260.8433 | New Construction | 10668902.0566 | 10668902.0566 | -910358.7867 | -910358.7867 | New Construction | 358532.6129 | 358532.6129 | New Construction | 328325.5382 | 328325.5382 | -30207.0748 | -30207.0748 | New Construction | 916122.7479 | 916122.7479 | New Construction | 770565.3464 | 770565.3464 | -145557.4015 | -145557.4015 | New Construction | 377768.7015 | 377768.7015 | New Construction | 406437.254 | 406437.254 | 28668.5525 | 28668.5525 | New Construction | 69144.7631 | 69144.7631 | New Construction | 47156.228 | 47156.228 | -21988.5351 | -21988.5351
[85 empty] | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
[85 empty] | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 20884.6319 | 20884.6319 | 1 | 0 | 0 | -20884.6319 | -20884.6319 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
[85 empty] | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 20884.6319 | 2 | 0 | 0 | -20884.6319 | -20884.6319 | 2 | 528.8638 | 528.8638 | 2 | 68.2405 | 68.2405 | -460.6233 | -460.6233
[16 empty] | Scroll down to row 60 for space by space analysis; scroll right for 40 year cost tabulations by building type | [68 empty] | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 37857.1874 | 58741.8193 | 3 | 0 | 0 | -58741.8193 | -58741.8193 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
[85 empty] | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 20884.6319 | 4 | 0 | 0 | -20884.6319 | -20884.6319 | 4 | 0 | 528.8638 | 4 | 0 | 68.2405 | -460.6233 | -460.6233
[85 empty] | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 232.7298 | 21117.3617 | 5 | 0 | 0 | -21117.3617 | -21117.3617 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
[85 empty] | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 135670.3716 | 194412.1909 | 6 | 94347.8392 | 94347.8392 | -100064.3517 | -100064.3517 | 6 | 63156.8524 | 63685.7162 | 6 | 43715.9604 | 43784.2009 | -19901.5153 | -19901.5153
[85 empty] | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 7673.9739 | 28558.6057 | 7 | 17024.6528 | 17024.6528 | -11533.953 | -11533.953 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
[85 empty] | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 20884.6319 | 8 | 0 | 0 | -20884.6319 | -20884.6319 | 8 | 0 | 528.8638 | 8 | 0 | 68.2405 | -460.6233 | -460.6233
[85 empty] | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 28420.2502 | 87162.0695 | 9 | 21396.1611 | 21396.1611 | -65765.9084 | -65765.9084 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
[85 empty] | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 17.3674 | 17.3674 | 10 | 0 | 0 | -17.3674 | -17.3674 | 10 | 2290.3509 | 2290.3509 | 10 | 0 | 0 | -2290.3509 | -2290.3509 | 10 | 0 | 21117.3617 | 10 | 0 | 0 | -21117.3617 | -21117.3617 | 10 | 0 | 528.8638 | 10 | 0 | 68.2405 | -460.6233 | -460.6233
[85 empty] | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 20884.6319 | 11 | 0 | 0 | -20884.6319 | -20884.6319 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
[85 empty] | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 12354.5122 | 206766.7031 | 12 | 14000.1555 | 108347.9947 | -98418.7083 | -98418.7083 | 12 | 0 | 63685.7162 | 12 | 0 | 43784.2009 | -19901.5153 | -19901.5153
[85 empty] | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 4533.0008 | 25417.6326 | 13 | 8659.795 | 8659.795 | -16757.8377 | -16757.8377 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
[85 empty] | 14 | 124443.0313 | 124443.0313 | 14 | 114685.1443 | 114685.1443 | -9757.887 | -9757.887 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 421205.0681 | 421205.0681 | 14 | 375158.7975 | 375158.7975 | -46046.2706 | -46046.2706 | 14 | 1029845.9836 | 1029845.9836 | 14 | 885684.5554 | 885684.5554 | -144161.4282 | -144161.4282 | 14 | 42932.2072 | 71490.8129 | 14 | 252954.6848 | 269979.3376 | 198488.5247 | 198488.5247 | 14 | 0 | 528.8638 | 14 | 0 | 68.2405 | -460.6233 | -460.6233
[85 empty] | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 58974.5491 | 15 | 0 | 0 | -58974.5491 | -58974.5491 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
[85 empty] | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 5280.2353 | 26164.8672 | 16 | 6409.7483 | 6409.7483 | -19755.1188 | -19755.1188 | 16 | 15690.9328 | 16219.7966 | 16 | 8708.5897 | 8776.8302 | -7442.9664 | -7442.9664
[85 empty] | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 20884.6319 | 17 | 0 | 0 | -20884.6319 | -20884.6319 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
[16 empty] | Scroll down to row 60 for space by space analysis; scroll right for 40 year cost tabulations by building type | [68 empty] | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 11700825.0465 | 11700825.0465 | 18 | 10783334.3055 | 10783334.3055 | -917490.7411 | -917490.7411 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 222832.4411 | 18 | 0 | 115744.0002 | -107088.4408 | -107088.4408 | 18 | 0 | 63685.7162 | 18 | 0 | 43784.2009 | -19901.5153 | -19901.5153
[85 empty] | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 20884.6319 | 19 | 0 | 0 | -20884.6319 | -20884.6319 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
[85 empty] | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 17.3674 | 20 | 0 | 0 | -17.3674 | -17.3674 | 20 | 0 | 2290.3509 | 20 | 0 | 0 | -2290.3509 | -2290.3509 | 20 | 0 | 21117.3617 | 20 | 0 | 0 | -21117.3617 | -21117.3617 | 20 | 386.4405 | 915.3043 | 20 | 1380.1447 | 1448.3852 | 533.0809 | 533.0809
[85 empty] | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 66415.7932 | 21 | 0 | 17024.6528 | -49391.1404 | -49391.1404 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
[85 empty] | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 20884.6319 | 22 | 0 | 0 | -20884.6319 | -20884.6319 | 22 | 0 | 528.8638 | 22 | 0 | 68.2405 | -460.6233 | -460.6233
[85 empty] | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 20884.6319 | 23 | 0 | 0 | -20884.6319 | -20884.6319 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
[85 empty] | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 11912.5628 | 218679.2659 | 24 | 8940.9575 | 117288.9522 | -101390.3136 | -101390.3136 | 24 | 0 | 63685.7162 | 24 | 0 | 43784.2009 | -19901.5153 | -19901.5153
[85 empty] | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 21117.3617 | 25 | 0 | 0 | -21117.3617 | -21117.3617 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
[85 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 25417.6326 | 26 | 0 | 8659.795 | -16757.8377 | -16757.8377 | 26 | 0 | 528.8638 | 26 | 0 | 68.2405 | -460.6233 | -460.6233
[85 empty] | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 87162.0695 | 27 | 0 | 21396.1611 | -65765.9084 | -65765.9084 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
[85 empty] | 28 | 0 | 124443.0313 | 28 | 0 | 114685.1443 | -9757.887 | -9757.887 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 421205.0681 | 28 | 0 | 375158.7975 | -46046.2706 | -46046.2706 | 28 | 0 | 1029845.9836 | 28 | 0 | 885684.5554 | -144161.4282 | -144161.4282 | 28 | 0 | 71490.8129 | 28 | 0 | 269979.3376 | 198488.5247 | 198488.5247 | 28 | 0 | 528.8638 | 28 | 0 | 68.2405 | -460.6233 | -460.6233
[85 empty] | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 20884.6319 | 29 | 0 | 0 | -20884.6319 | -20884.6319 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
[16 empty] | Scroll down to row 60 for space by space analysis; scroll right for 40 year cost tabulations by building type | [68 empty] | 30 | 0 | 0 | 30 | 0 | 0 | 8363.9032 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 305830.247 | 0 | 30 | 0 | 17.3674 | 30 | 0 | 0 | 39468.232 | -17.3674 | 30 | 0 | 2290.3509 | 30 | 0 | 0 | 123566.9385 | -2290.3509 | 30 | 0 | 194644.9207 | 30 | 0 | 94347.8392 | -183607.915 | -100297.0815 | 30 | 0 | 63685.7162 | 30 | 0 | 43784.2009 | 375.9408 | -19901.5153
[85 empty] | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 20884.6319 | 31 | 0 | 0 |  | -20884.6319 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
[85 empty] | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 26164.8672 | 32 | 0 | 6409.7483 |  | -19755.1188 | 32 | 0 | 16219.7966 | 32 | 0 | 8776.8302 |  | -7442.9664
[85 empty] | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 58741.8193 | 33 | 0 | 0 |  | -58741.8193 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
[85 empty] | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 20884.6319 | 34 | 0 | 0 |  | -20884.6319 | 34 | 0 | 528.8638 | 34 | 0 | 68.2405 |  | -460.6233
[85 empty] | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 28791.3355 | 35 | 0 | 17024.6528 |  | -11766.6827 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
[85 empty] | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 11700825.0465 | 36 | 0 | 10783334.3055 |  | -917490.7411 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 235186.9532 | 36 | 0 | 129744.1558 |  | -105442.7974 | 36 | 0 | 63685.7162 | 36 | 0 | 43784.2009 |  | -19901.5153
[85 empty] | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 20884.6319 | 37 | 0 | 0 |  | -20884.6319 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
[85 empty] | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 20884.6319 | 38 | 0 | 0 |  | -20884.6319 | 38 | 0 | 528.8638 | 38 | 0 | 68.2405 |  | -460.6233
[85 empty] | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 63274.82 | 39 | 0 | 8659.795 |  | -54615.0251 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
[85 empty] | 40 | 0 | 0 | 40 | 0 | 0 |  | 1393.9839 | 40 | 0 | 0 | 40 | 0 | 0 |  | 713603.9097 | 40 | 0 | 0 | 40 | 0 | 0 |  | 6578.0387 | 40 | 0 | 0 | 40 | 0 | 0 |  | 20594.4897 | 40 | 0 | 0 | 40 | 0 | 0 |  | 5759.075 | 40 | 0 | 0 | 40 | 0 | 0 |  | 9971.4689
[85 empty] | Residual Year 30 |  | -106665.4554 | Residual Year 30 |  | -98301.5523 |  | 8363.9032 | Residual Year 30 |  | -3900275.0155 | Residual Year 30 |  | -3594444.7685 |  | 305830.247 | Residual Year 30 |  | -361032.9155 | Residual Year 30 |  | -321564.6836 |  | 39468.232 | Residual Year 30 |  | -882725.1288 | Residual Year 30 |  | -759158.1903 |  | 123566.9385 | Residual Year 30 |  | -80137.217 | Residual Year 30 |  | -263745.132 |  | -183607.915 | Residual Year 30 |  | -2154.5869 | Residual Year 30 |  | -1778.6461 |  | 375.9408
[85 empty] | Residual Year 40 |  | -17777.5759 | Residual Year 40 |  | -16383.592 |  | 1393.9839 | Residual Year 40 |  | -9100641.7028 | Residual Year 40 |  | -8387037.7931 |  | 713603.9097 | Residual Year 40 |  | -60172.1526 | Residual Year 40 |  | -53594.1139 |  | 6578.0387 | Residual Year 40 |  | -147120.8548 | Residual Year 40 |  | -126526.3651 |  | 20594.4897 | Residual Year 40 |  | -113607.9682 | Residual Year 40 |  | -107848.8932 |  | 5759.075 | Residual Year 40 |  | -28897.7506 | Residual Year 40 |  | -18926.2817 |  | 9971.4689
Scroll down to row 60 for space by space analysis; scroll right for 40 year cost tabulations by building type
[16 empty] | Col22 | LPD2010 | Fixture ID Numbers | Col25 | area2010 | Col27 | LPD2013 | Col29 | Col30 | area2013 | Col32 | Col33 | Col34 | Col35 | Col36 | Mat2010 | Col38 | Col39 | Lab2010 | Col41 | Col42 | Col43 | Col44 | Tot2010 | Col46 | Col47 | Col48 | Col49 | Col50 | Col51 | Col52 | Col53 | Col54 | Col55 | Col56 | Rep2010 | Col58 | Mat2013 | Col60 | Col61 | Lab2013 | Col63 | Col64 | Col65 | Col66 | Tot2013 | Col68 | Col69 | Col70 | Col71 | Col72 | Col73 | Col74 | Col75 | Col76 | Col77 | Col78 | Repl2013 | Incremental | Repl | Col82 | Proto | Space | Col85 | Col86 | Col87 | Col88 | Col89 | Col90
[16 empty] | 90.1-2016 |  |  |  |  | 90.1-2019 | [8 empty] | 90.1-2016 Baseline Costs - without implementation of the addenda. | [21 empty] | 90.1-2019 - costs with addendum | [21 empty] | Incremental Costs | Incremental Costs
|  | Prototypes Affected (X) | [5 empty] | Not Used | [5 empty] | Name of Item | [11 empty] | 4510 | 4345 |  |  | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | New Construction Costs | [9 empty] | Replacement Costs
90.1-2016 Lookup | 90.1-2019 Lookup | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | [5 empty] | Not Used | Interior Lighting Power Density | Not Used | Costs to provide lighting fixtures, lamps and ballasts to meet space by space lighting power density (LPD) maximum allowed LPD values under 90.1-2016. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs are for equipment etc. at today's prices that just meet the 90.1-2016 requirements. Costs by 90.1-2016 Prototype and Lighting Space Type | 90.1-2016 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent Operating Hours for Space Type Lamp Life for Fixtures (Used to Calculate Replacement Life) | Area of Space Type In Prototype Models | Costs to provide lighting fixtures, lamps and ballasts to meet space by space maximum allowed LPD values under 90.1-2019 Table 9.6.1. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs by 90.1-2019 Prototype and Lighting Space Type | 90.1-2019 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent (BLE) Operating Hours | Area of Space Type, ft2 | LPA |  |  |  | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments (with added replacement labor hours) | Not Used | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments (with added replacement labor hours) | Incremental Added Design with OH&P | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | New Construction Costs 90.1-2019 minus 90.1-2016 | Replacement Costs 90.1-2019 minus 90.1-2016
Small Office |  | X | [5 empty] | X | X | X | X | X |  | Small _Office_Interior_Lighting_LPD |  | Small Office |  |  | 3642 |  | Small Office |  |  | 3642
Office-BLDG-SO | Office-BLDG-SO | X | [13 empty] | Office-BLDG-SO | 0.79 |  | 3642 | 5500 | Office-BLDG-SO | 0.64 |  | 3642 | 5500 | 110.2926 |  | 101.1494 | [45 empty] | -10042.036 | -33.7781 |  | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO | Office-BLDG-SO
Office-BLDG-SO735 | Office-BLDG-SOID701 | X | [13 empty] | replacement costs shown are for lamps |  | 735 |  | 5500 |  |  | ID701 |  | 5500 | 105.6579 | 52.0548 | 93.8666 | 58.5938 | 12.8649 | 70756.9789 |  | 1.5489 | 8518.8263 |  | 42273.0828 |  |  | 121548.888 | 13.7287 | 14 | 0.0073 | 40.15 |  | 0.011814 | 64.9796 |  | 184.4152 |  | 289.5448 | 295.2662 | 11.4284 | 62855.936 |  | 1.376 | 7568.1408 |  | 37553.2255 |  |  | 107977.3023 | 13.7287 | 14 | 0.005632 | 30.976 |  | 0.010496 | 57.728 |  | 160.8812 |  | 249.5852 | 254.517 | -13571.5857 |  | -40.7492 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO735 | Office-BLDG-SOID701
Office-BLDG-SO0 | Office-BLDG-SO0 | X | [15 empty] | 0 |  | 5500 |  |  | 0 |  | 5500 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO0 | Office-BLDG-SO0
Office-BLDG-SO0 | Office-BLDG-SO0 | X | [15 empty] | 0 |  | 5500 |  |  | 0 |  | 5500 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO0 | Office-BLDG-SO0
Office-BLDG-SO703 | Office-BLDG-SOWW714 | X | [15 empty] | 703 |  | 5500 |  |  | WW714 |  | 5500 | 4.6347 | 1186.7089 | 7.2828 | 755.2085 | 0.64864 | 3567.5347 |  | 0.082918 | 456.0512 |  | 2157.0096 |  |  | 6180.5955 | 13.7287 | 14 | 0.000632 | 3.476 |  | 0.00051824 | 2.8503 |  | 9.1685 |  | 15.4948 | 15.801 | 1.019 | 5604.6654 |  | 0.1303 | 716.6234 |  | 3388.8563 |  |  | 9710.1451 | 13.7287 | 14 | 0.000768 | 4.224 |  | 0.00081434 | 4.4789 |  | 13.628 |  | 22.3309 | 22.7721 | 3529.5496 |  | 6.9711 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO703 | Office-BLDG-SOWW714
Office-BLDG-SO735 | Office-BLDG-SOID701 | X | [13 empty] | ballast replacement |  | 735 |  | 5500 |  |  | ID701 |  | 5500 | 65.7 |  | 55.7568 | [11 empty] | 13.7287 | 14 | 9.6432 | 53037.6217 |  | 1.5489 | 8518.8263 |  | 54241.9419 |  | 115798.3899 | 118086.5661 | [10 empty] | 13.7287 | 14 | 8.567 | 47118.72 |  | 1.376 | 7568.1408 |  | 48188.6403 |  | 102875.5011 | 104908.321 | 0 | -9724.1089 | -13178.2451 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO735 | Office-BLDG-SOID701
Office-BLDG-SO0 | Office-BLDG-SO0 | X | [15 empty] | 0 |  | 5500 |  |  | 0 |  | 5500 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO0 | Office-BLDG-SO0
Office-BLDG-SO0 | Office-BLDG-SO0 | X | [15 empty] | 0 |  | 5500 |  |  | 0 |  | 5500 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO0 | Office-BLDG-SO0
Office-BLDG-SO703 | Office-BLDG-SOWW714 | X | [15 empty] | 703 |  | 5500 |  |  | WW714 |  | 5500 | 3.9816 |  | 6.2899 | [11 empty] | 13.7287 | 14 | 0.48601 | 2673.044 |  | 0.082918 | 456.0512 |  | 2799.1605 |  | 5928.2557 | 6045.398 | [10 empty] | 13.7287 | 14 | 0.7637 | 4200.331 |  | 0.1303 | 716.6234 |  | 4398.5062 |  | 9315.4607 | 9499.5342 | 0 |  | 3454.1362 | SmOfc | Office-BLDG-SO |  |  | Office-BLDG-SO703 | Office-BLDG-SOWW714
Office - Open Plan (Including Other)-whole | Office - Open Plan (Including Other)-whole | 0 | [13 empty] | Office - Open Plan (Including Other)-whole-small | 0.81 |  | 3642 | 1100 | Office - Open Plan (Including Other)-whole | 0.61 |  | 3642 | 1100 | 33.3204 |  | 19.6149 | [45 empty] | -1150.8803 | -33.3025 |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small | Office - Open Plan (Including Other)-whole-small
Office - Open Plan (Including Other)735-whole-Small | Office - Open Plan (Including Other)id701-whole-Small | 0 | [13 empty] | replacement costs shown are for lamps |  | 735 |  | 1100 |  |  | ID701 |  | 1100 | 14.4737 | 76 | 18.6667 | 58.9286 | 8.8116 | 9692.7368 |  | 1.0609 | 1166.9625 |  | 5790.8333 |  |  | 16650.5326 | 13.7287 | 14 | 0.005 | 5.5 |  | 0.0080921 | 8.9013 |  | 25.2624 |  | 39.6637 | 40.4474 | 11.3634 | 12499.76 |  | 1.3682 | 1505.028 |  | 7467.971 |  |  | 21472.759 | 13.7287 | 14 | 0.0056 | 6.16 |  | 0.010436 | 11.48 |  | 31.9934 |  | 49.6334 | 50.6142 | 4822.2264 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small735 | Office - Open Plan (Including Other)-whole-smallID701
Office - Open Plan (Including Other)739-whole-Small | Office - Open Plan (Including Other)0-whole-Small | 0 | [15 empty] | 739 |  | 1100 |  |  | 0 |  | 1100 | 16.5 | 66.6667 | 0 | 0 | 1.9215 | 2113.65 |  | 0.45203 | 497.2275 |  | 1497.1556 |  |  | 4108.0331 | 13.7287 | 14 | 0.0015 | 1.65 |  | 0.009225 | 10.1475 |  | 25.8916 |  | 37.6891 | 38.4339 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -4108.0331 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small739 | Office - Open Plan (Including Other)-whole-small0
Office - Open Plan (Including Other)0-whole-Small | Office - Open Plan (Including Other)0-whole-Small | 0 | [15 empty] | 0 |  | 1100 |  |  | 0 |  | 1100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small0 | Office - Open Plan (Including Other)-whole-small0
Office - Open Plan (Including Other)703-whole-Small | Office - Open Plan (Including Other)ww714-whole-Small | 0 | [15 empty] | 703 |  | 1100 |  |  | WW714 |  | 1100 | 2.3467 | 468.75 | 0.94828 | 1160.0002 | 1.6421 | 1806.3467 |  | 0.20992 | 230.912 |  | 1092.1568 |  |  | 3129.4154 | 13.7287 | 14 | 0.0016 | 1.76 |  | 0.001312 | 1.4432 |  | 4.6423 |  | 7.8455 | 8.0005 | 0.66343 | 729.7741 |  | 0.084828 | 93.3103 |  | 441.2573 |  |  | 1264.3418 | 13.7287 | 14 | 0.0005 | 0.55 |  | 0.00053017 | 0.58319 |  | 1.7745 |  | 2.9077 | 2.9651 | -1865.0736 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small703 | Office - Open Plan (Including Other)-whole-smallWW714
Office - Open Plan (Including Other)735-whole-Small | Office - Open Plan (Including Other)id701-whole-Small | 0 | [13 empty] | ballast replacement |  | 735 |  | 1100 |  |  | ID701 |  | 1100 | 45 |  | 55.44 | [11 empty] | 13.7287 | 14 | 6.6049 | 7265.4276 |  | 1.0609 | 1166.9625 |  | 7430.403 |  | 15862.7931 | 16176.2419 | [10 empty] | 13.7287 | 14 | 8.5184 | 9370.2 |  | 1.3682 | 1505.028 |  | 9582.9682 |  | 20458.1962 | 20862.4502 | 0 | -1518.6006 |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small735 | Office - Open Plan (Including Other)-whole-smallID701
Office - Open Plan (Including Other)739-whole-Small | Office - Open Plan (Including Other)0-whole-Small | 0 | [15 empty] | 739 |  | 1100 |  |  | 0 |  | 1100 | 9.18 |  | 1e-05 | [11 empty] | 13.7287 | 14 | 1.44 | 1584 |  | 0.45203 | 497.2275 |  | 2214.6523 |  | 4295.8798 | 4380.7664 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small739 | Office - Open Plan (Including Other)-whole-small0
Office - Open Plan (Including Other)0-whole-Small | Office - Open Plan (Including Other)0-whole-Small | 0 | [15 empty] | 0 |  | 1100 |  |  | 0 |  | 1100 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small0 | Office - Open Plan (Including Other)-whole-small0
Office - Open Plan (Including Other)703-whole-Small | Office - Open Plan (Including Other)ww714-whole-Small | 0 | [15 empty] | 703 |  | 1100 |  |  | WW714 |  | 1100 | 10.08 |  | 4.095 | [11 empty] | 13.7287 | 14 | 1.2304 | 1353.44 |  | 0.20992 | 230.912 |  | 1417.2964 |  | 3001.6484 | 3060.961 | [10 empty] | 13.7287 | 14 | 0.4972 | 546.9181 |  | 0.084828 | 93.3103 |  | 572.7222 |  | 1212.9506 | 1236.9185 | 0 |  |  |  | Office - Open Plan (Including Other)-whole-small |  |  | Office - Open Plan (Including Other)-whole-small703 | Office - Open Plan (Including Other)-whole-smallWW714
Office-Enclosed-whole | Office-Enclosed-whole-small | 0 | [13 empty] | Office-Enclosed-whole-small | 0.878 |  | 3642 | 1595 | Office-Enclosed-whole | 0.74 |  | 3642 | 1595 | 66.6356 |  | 36.8844 | [45 empty] | -8498.6157 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small | Office-Enclosed-whole-small
Office-Enclosed700-whole-Small | Office-Enclosed731-whole-Small | 0 | [13 empty] | lamp replacement |  | 700 |  | 1595 |  |  | TR701 |  | 1595 | 28.3556 | 56.25 | 36.8844 | 43.2433 | 2.4597 | 3923.2747 |  | 1.6498 | 2631.4948 |  | 4428.5564 |  |  | 10983.3259 | 13.7287 | 14 | 0.0064 | 10.208 |  | 0.010933 | 17.4387 |  | 49.1349 |  | 76.7815 | 78.2987 | 3.1987 | 5101.8467 |  | 1.4222 | 2268.3891 |  | 4645.1111 |  |  | 12015.3469 | 13.7287 | 14 | 0.0074 | 11.803 |  | 0.014222 | 22.6839 |  | 62.9852 |  | 97.4721 | 99.3982 | 1032.021 | -68.0671 |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small700 | Office-Enclosed-whole-smallTR701
Office-Enclosed739-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 739 |  | 1595 |  |  | 0 |  | 1595 | 38.28 | 41.6667 | 0 | 0 | 3.0744 | 4903.668 |  | 0.72324 | 1153.5678 |  | 3473.4009 |  |  | 9530.6367 | 13.7287 | 14 | 0.0024 | 3.828 |  | 0.01476 | 23.5422 |  | 60.0686 |  | 87.4388 | 89.1666 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -9530.6367 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small739 | Office-Enclosed-whole-small0
Office-Enclosed0-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 0 |  | 1595 |  |  | 0 |  | 1595 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small0 | Office-Enclosed-whole-small0
Office-Enclosed0-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 0 |  | 1595 |  |  | 0 |  | 1595 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small0 | Office-Enclosed-whole-small0
Office-Enclosed700-whole-Small | Office-Enclosed731-whole-Small | 0 | [13 empty] | ballast replacement |  | 700 |  | 1595 |  |  | TR701 |  | 1595 | 59.328 |  | 76.59 | [11 empty] | 13.7287 | 14 | 1.84 | 2934.8 |  | 1.6498 | 2631.4948 |  | 8291.9843 |  | 13858.2791 | 14132.1187 | [10 empty] | 13.7287 | 14 | 2.3934 | 3817.5328 |  | 1.4222 | 2268.3891 |  | 7958.1873 |  | 14044.1092 | 14321.6208 | 0 | -9973.8759 |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small700 | Office-Enclosed-whole-smallTR701
Office-Enclosed739-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 739 |  | 1595 |  |  | 0 |  | 1595 | 14.688 |  | 1e-05 | [11 empty] | 13.7287 | 14 | 2.304 | 3674.88 |  | 0.72324 | 1153.5678 |  | 5137.9933 |  | 9966.4411 | 10163.378 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small739 | Office-Enclosed-whole-small0
Office-Enclosed0-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 0 |  | 1595 |  |  | 0 |  | 1595 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small0 | Office-Enclosed-whole-small0
Office-Enclosed0-whole-Small | Office-Enclosed0-whole-small | 0 | [15 empty] | 0 |  | 1595 |  |  | 0 |  | 1595 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-small |  |  | Office-Enclosed-whole-small0 | Office-Enclosed-whole-small0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | 0 | [13 empty] | Conference/Meeting/Multipurpose | 1.07 |  | 3642 | 440 | Conference/Meeting/Multipurpose | 0.97 |  | 3642 | 440 | 12.3567 |  | 11.9442 | [45 empty] | -71.8435 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 | 0 | [13 empty] | lamp replacement |  | 731 |  | 440 |  |  | TR704 |  | 440 | 4.95 | 88.8889 | 6.7375 | 65.3061 | 4.302 | 1892.88 |  | 0.90705 | 399.1012 |  | 1296.1813 |  |  | 3588.1624 | 13.7287 | 14 | 0.0045 | 1.98 |  | 0.0069188 | 3.0442 |  | 8.702 |  | 13.7263 | 13.9975 | 2.118 | 931.931 |  | 0.94172 | 414.3562 |  | 848.5012 |  |  | 2194.7884 | 13.7287 | 14 | 0.0049 | 2.156 |  | 0.0094172 | 4.1436 |  | 11.5052 |  | 17.8048 | 18.1566 | -1393.374 | -242.6752 |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 | 0 | [15 empty] | 511 |  | 440 |  |  | DL702 |  | 440 | 3.2267 | 136.3636 | 2.9333 | 150.0001 | 0.42871 | 188.6309 |  | 0.451 | 198.44 |  | 282.3606 |  |  | 669.4316 | 1.1532 | 2 | 0.15679 | 68.9861 |  | 0.02134 | 9.3896 |  | 66.4114 |  | 144.7871 | 251.1022 | 1.2021 | 528.9363 |  | 0.41 | 180.4 |  | 428.6982 |  |  | 1138.0345 | 13.7287 | 14 | 0.0016 | 0.704 |  | 0.0041 | 1.804 |  | 4.8614 |  | 7.3694 | 7.515 | 468.6029 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 | 0 | [15 empty] | 0 |  | 440 |  |  | 0 |  | 440 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 | 0 | [15 empty] | 727-1 |  | 440 |  |  | WW704 |  | 440 | 4.18 | 105.2632 | 2.2733 | 193.5484 | 2.5669 | 1129.436 |  | 0.58425 | 257.07 |  | 791.6826 |  |  | 2178.1886 | 13.7287 | 14 | 0.0019 | 0.836 |  | 0.0058425 | 2.5707 |  | 6.8223 |  | 10.229 | 10.4311 | 3.9763 | 1749.5573 |  | 0.5084 | 223.696 |  | 1057.8628 |  |  | 3031.1161 | 13.7287 | 14 | 0.0031 | 1.364 |  | 0.0031775 | 1.3981 |  | 4.2826 |  | 7.0447 | 7.1839 | 852.9275 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 | 0 | [13 empty] | ballast replacement |  | 731 |  | 440 |  |  | TR704 |  | 440 | 35.64 |  | 48.951 | [11 empty] | 13.7287 | 14 | 3.2231 | 1418.175 |  | 0.90705 | 399.1012 |  | 1869.9643 |  | 3687.2405 | 3760.1004 | [10 empty] | 13.7287 | 14 | 1.5848 | 697.3312 |  | 0.94172 | 414.3562 |  | 1453.6857 |  | 2565.3732 | 2616.0649 | 0 | 803.4548 |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 | 0 | [15 empty] | 511 |  | 440 |  |  | DL702 |  | 440 | 2.4651 |  | 8.64 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 13.7287 | 14 | 0.9004 | 396.1742 |  | 0.41 | 180.4 |  | 691.156 |  | 1267.7302 | 1292.7806 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 | 0 | [15 empty] | 0 |  | 440 |  |  | 0 |  | 440 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 | 0 | [15 empty] | 727-1 |  | 440 |  |  | WW704 |  | 440 | 17.1 |  | 13.113 | [11 empty] | 13.7287 | 14 | 1.9238 | 846.45 |  | 0.58425 | 257.07 |  | 1162.3037 |  | 2265.8237 | 2310.5963 | [10 empty] | 13.7287 | 14 | 2.9799 | 1311.145 |  | 0.5084 | 223.696 |  | 1373.0059 |  | 2907.8469 | 2965.306 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Corridor/Transition | Corridor/Transition | 0 | [13 empty] | Corridor/Transition | 0.66 |  | 3642 | 660 | Corridor/Transition | 0.41 |  | 3642 | 660 | 23.364 |  | 15.317 | [45 empty] | -3276.8429 |  |  |  | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 | 0 | [13 empty] | replacement costs are for lamps |  | 701 |  | 660 |  |  | DL706 |  | 660 | 20.9 | 31.5789 | 13.2 | 50 | 5.2271 | 3449.8961 |  | 1.9475 | 1285.35 |  | 2901.08 |  |  | 7636.3261 | 13.7287 | 14 | 0.0038 | 2.508 |  | 0.019475 | 12.8535 |  | 33.0591 |  | 48.4206 | 49.3774 | 3.3013 | 2178.8818 |  | 1.23 | 811.8 |  | 1832.2611 |  |  | 4822.9428 | 13.7287 | 14 | 0.0024 | 1.584 |  | 0.0123 | 8.118 |  | 20.8794 |  | 30.5814 | 31.1857 | -2813.3833 | -20.1486 |  |  | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 | 0 | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 | 0 | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 | 0 | [15 empty] | 703 |  | 660 |  |  | WW708 |  | 660 | 2.464 | 267.8571 | 2.117 | 311.7648 | 2.8737 | 1896.664 |  | 0.36736 | 242.4576 |  | 1146.7646 |  |  | 3285.8862 | 13.7287 | 14 | 0.0028 | 1.848 |  | 0.002296 | 1.5154 |  | 4.8744 |  | 8.2378 | 8.4005 | 2.4683 | 1629.0805 |  | 0.31562 | 208.3109 |  | 985.0352 |  |  | 2822.4267 | 13.7287 | 14 | 0.0017 | 1.122 |  | 0.0019726 | 1.3019 |  | 3.8948 |  | 6.3188 | 6.4436 | -463.4595 |  |  |  | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 | 0 | [13 empty] | replacement costs are for ballasts |  | 701 |  | 660 |  |  | DL706 |  | 660 | 23.256 |  | 14.688 | [11 empty] | 13.7287 | 14 | 3.9175 | 2585.5411 |  | 1.9475 | 1285.35 |  | 4775.2114 |  | 8646.1025 | 8816.9495 | [10 empty] | 13.7287 | 14 | 2.4742 | 1632.9733 |  | 1.23 | 811.8 |  | 3015.923 |  | 5460.6963 | 5568.5997 | 0 | -3700.9966 |  |  | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 | 0 | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 | 0 | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 | 0 | [15 empty] | 703 |  | 660 |  |  | WW708 |  | 660 | 17.64 |  | 15.147 | [11 empty] | 13.7287 | 14 | 2.1532 | 1421.112 |  | 0.36736 | 242.4576 |  | 1488.1613 |  | 3151.7309 | 3214.0091 | [10 empty] | 13.7287 | 14 | 1.85 | 1220.9689 |  | 0.31562 | 208.3109 |  | 1278.5752 |  | 2707.855 | 2761.3622 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Storage | Storage | 0 | [13 empty] | Storage | 0.46 |  | 3642 | 770 | Storage | 0.38 |  | 3642 | 770 | 9.3211 |  | 7.9081 | [45 empty] | -1610.2079 |  |  |  | Storage |  |  | Storage | Storage
Storage738 | StorageLB702 | 0 | [13 empty] | replacement costs are for lamps |  | 738 |  | 770 |  |  | LB702 |  | 770 | 9.3211 | 82.6087 | 7.9081 | 97.3684 | 3.0309 | 2333.8052 |  | 0.70055 | 539.4233 |  | 1643.8338 |  |  | 4517.0622 | 13.7287 | 14 | 0.0046 | 3.542 |  | 0.0074447 | 5.7324 |  | 16.269 |  | 25.5434 | 26.0481 | 1.76 | 1355.2125 |  | 0.59436 | 457.6541 |  | 1093.9878 |  |  | 2906.8543 | 13.7287 | 14 | 0.0038 | 2.926 |  | 0.0063162 | 4.8635 |  | 13.753 |  | 21.5425 | 21.9682 | -1610.2079 | -4.0799 |  |  | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage738 | StorageLB702 | 0 | [13 empty] | ballast replacement |  | 738 |  | 770 |  |  | LB702 |  | 770 | 47.61 |  | 35.226 | [11 empty] | 13.7287 | 14 | 2.2697 | 1747.6974 |  | 0.70055 | 539.4233 |  | 2421.0162 |  | 4708.1369 | 4801.1697 | [10 empty] | 13.7287 | 14 | 1.3172 | 1014.2149 |  | 0.59436 | 457.6541 |  | 1759.1519 |  | 3231.0208 | 3294.8658 | 0 | -1506.3039 |  |  | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 | 0 | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Restrooms | Restrooms | 0 | [13 empty] | Restrooms | 0.85 |  | 3642 | 220 | Restrooms | 0.63 |  | 3642 | 220 | 6.931 |  | 7.0718 | [45 empty] | -987.6417 |  |  |  | Restrooms |  |  | Restrooms | Restrooms
Restrooms604 | RestroomsDL709 | 0 | [13 empty] | replacement costs are for lamps |  | 604 |  | 220 |  |  | DL709 |  | 220 | 2.6552 | 82.8571 | 3.894 | 56.4972 | 4.2525 | 935.55 |  | 0.3637 | 80.0136 |  | 527.4389 |  |  | 1543.0025 | 9.8847 | 10 | 0.040431 | 8.8948 |  | 0.065978 | 14.5151 |  | 41.1481 |  | 64.5581 | 65.3113 | 3.5159 | 773.4987 |  | 1.0885 | 239.481 |  | 603.4236 |  |  | 1616.4033 | 13.7287 | 14 | 0.003717 | 0.81774 |  | 0.010885 | 2.3948 |  | 6.38 |  | 9.5925 | 9.7821 | 73.4008 | -108.7432 |  |  | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 | 0 | [15 empty] | 720 |  | 220 |  |  | 0 |  | 220 | 2 | 110 | 0 | 0 | 1.5353 | 337.774 |  | 0.55909 | 123 |  | 281.2919 |  |  | 742.0659 | 13.7287 | 14 | 0.002 | 0.44 |  | 0.0055909 | 1.23 |  | 3.2894 |  | 4.9594 | 5.0574 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -742.0659 |  |  |  | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 | 0 | [15 empty] | 0 |  | 220 |  |  | 0 |  | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 | 0 | [15 empty] | 534-2 |  | 220 |  |  | WG701 |  | 220 | 2.2759 | 96.6667 | 3.1778 | 69.2308 | 3.9657 | 872.4517 |  | 0.59867 | 131.7076 |  | 546.9858 |  |  | 1551.1451 | 9.8847 | 10 | 0.034655 | 7.6241 |  | 0.056552 | 12.4415 |  | 35.2698 |  | 55.3355 | 55.9811 | 2.6025 | 572.5402 |  | 0.88833 | 195.4333 |  | 464.1949 |  |  | 1232.1684 | 13.7287 | 14 | 0.0026 | 0.572 |  | 0.0088833 | 1.9543 |  | 5.1465 |  | 7.6729 | 7.8245 | -318.9767 |  |  |  | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Restrooms604 | RestroomsDL709 | 0 | [13 empty] | ballast replacement |  | 604 |  | 220 |  |  | DL709 |  | 220 | 24.2393 |  | 28.7696 | [11 empty] | 13.7287 | 14 | 0.36207 | 79.6552 |  | 0.74224 | 163.2931 |  | 450.066 |  | 693.0143 | 706.7082 | [10 empty] | 13.7287 | 14 | 2.6341 | 579.5107 |  | 1.0885 | 239.481 |  | 951.2345 |  | 1770.2262 | 1805.2059 | 0 | 1039.9078 |  |  | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 | 0 | [15 empty] | 720 |  | 220 |  |  | 0 |  | 220 | 12.6 |  | 1e-05 | [11 empty] | 13.7287 | 14 | 1.15 | 253.0005 |  | 0.55909 | 123 |  | 460.4698 |  | 836.4703 | 852.999 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 | 0 | [15 empty] | 0 |  | 220 |  |  | 0 |  | 220 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 | 0 | [15 empty] | 534-2 |  | 220 |  |  | WG701 |  | 220 | 24.3 |  | 24.102 | [11 empty] | 13.7287 | 14 | 0.31034 | 68.2759 |  | 0.63621 | 139.9655 |  | 385.7709 |  | 594.0122 | 605.7499 | [10 empty] | 13.7287 | 14 | 1.9499 | 428.9762 |  | 0.88833 | 195.4333 |  | 748.6185 |  | 1373.028 | 1400.1591 | 0 |  |  |  | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Lounge/Recreation - Break room | Lounge/Recreation - Break room | 0 | [13 empty] | Lounge/Recreation - Break room | #N/A |  | 3642 | 110 | Lounge/Recreation - Break room | #N/A |  | 3642 | 110 | 3.3477 |  | 5.5611 | [45 empty] | 145.0796 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 | 0 | [13 empty] | replacement costs are for lamps |  | 522 |  | 110 |  |  | DL707 |  | 110 | 2.0717 | 53.0973 | 3.85 | 28.5715 | 2.9226 | 321.4812 |  | 1.1583 | 127.4075 |  | 277.7072 |  |  | 726.5959 | 13.7287 | 14 | 0.00339 | 0.3729 |  | 0.011583 | 1.2741 |  | 3.3551 |  | 5.0021 | 5.101 | 7.1431 | 785.7423 |  | 2.1525 | 236.775 |  | 606.7026 |  |  | 1629.2199 | 13.7287 | 14 | 0.0028 | 0.308 |  | 0.021525 | 2.3678 |  | 5.9929 |  | 8.6687 | 8.84 | 902.6239 | 4.662 |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 | 0 | [15 empty] | 727-2 |  | 110 |  |  | WG702 |  | 110 | 1.276 | 86.2069 | 1.7111 | 64.2857 | 7.7749 | 855.239 |  | 0.7134 | 78.474 |  | 487.3067 |  |  | 1421.0197 | 13.7287 | 14 | 0.0029 | 0.319 |  | 0.007134 | 0.78474 |  | 2.1227 |  | 3.2265 | 3.2902 | 2.8026 | 308.2909 |  | 0.95667 | 105.2333 |  | 249.9511 |  |  | 663.4753 | 13.7287 | 14 | 0.0028 | 0.308 |  | 0.0095667 | 1.0523 |  | 2.7712 |  | 4.1315 | 4.2132 | -757.5444 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 | 0 | [13 empty] | ballast replacement |  | 522 |  | 110 |  |  | DL707 |  | 110 | 16.0178 |  | 22.428 | [11 empty] | 0 | 0 | 2.1894 | 240.8313 |  | 1.1583 | 127.4075 |  | 463.6063 |  | 831.8451 | 0 | [10 empty] | 13.7287 | 14 | 5.3552 | 589.0757 |  | 2.1525 | 236.775 |  | 950.6264 |  | 1776.4771 | 1811.5802 | 0 | 1224.144 |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 | 0 | [15 empty] | 727-2 |  | 110 |  |  | WG702 |  | 110 | 26.1 |  | 22.176 | [11 empty] | 13.7287 | 14 | 5.829 | 641.19 |  | 0.7134 | 78.474 |  | 595.7122 |  | 1315.3762 | 1341.368 | [10 empty] | 13.7287 | 14 | 2.0999 | 230.9872 |  | 0.95667 | 105.2333 |  | 403.1023 |  | 739.3228 | 753.9318 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Electrical/Mechanical | Electrical/Mechanical | 0 | [13 empty] | Electrical/Mechanical | 0.43 |  | 3642 | 110 | Electrical/Mechanical | 0.43 |  | 3642 | 110 | 2.8658 |  | 2.8838 | [45 empty] | -71.3028 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical | Electrical/Mechanical
Electrical/Mechanical738 | Electrical/MechanicalLB702 | 0 | [13 empty] | replacement costs are for lamps |  | 738 |  | 110 |  |  | LB702 |  | 110 | 0.66579 | 165.2174 | 0.68378 | 160.8696 | 1.5155 | 166.7004 |  | 0.35027 | 38.5302 |  | 117.4167 |  |  | 322.6473 | 13.7287 | 14 | 0.0023 | 0.253 |  | 0.0037224 | 0.40946 |  | 1.1621 |  | 1.8245 | 1.8606 | 1.0653 | 117.18 |  | 0.35974 | 39.5716 |  | 94.5929 |  |  | 251.3445 | 13.7287 | 14 | 0.0023 | 0.253 |  | 0.003823 | 0.42053 |  | 1.1892 |  | 1.8627 | 1.8995 | -71.3028 | 0.038925 |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 | 0 | [15 empty] | 739 |  | 110 |  |  | TL702 |  | 110 | 2.2 | 50 | 2.2 | 50.0001 | 2.562 | 281.82 |  | 0.6027 | 66.297 |  | 199.6207 |  |  | 547.7377 | 13.7287 | 14 | 0.002 | 0.22 |  | 0.0123 | 1.353 |  | 3.4522 |  | 5.0252 | 5.1245 | 2.562 | 281.82 |  | 0.6027 | 66.297 |  | 199.6207 |  |  | 547.7377 | 13.7287 | 14 | 0.002 | 0.22 |  | 0.0123 | 1.353 |  | 3.4522 |  | 5.0252 | 5.1245 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical738 | Electrical/MechanicalLB702 | 0 | [13 empty] | ballast replacement |  | 738 |  | 110 |  |  | LB702 |  | 110 | 23.805 |  | 21.321 | [11 empty] | 13.7287 | 14 | 1.1349 | 124.8355 |  | 0.35027 | 38.5302 |  | 172.9297 |  | 336.2955 | 342.9407 | [10 empty] | 13.7287 | 14 | 0.79723 | 87.6953 |  | 0.35974 | 39.5716 |  | 152.1071 |  | 279.374 | 284.8944 | 0 | -58.0463 |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 | 0 | [15 empty] | 739 |  | 110 |  |  | TL702 |  | 110 | 12.24 |  | 12.24 | [11 empty] | 13.7287 | 14 | 1.92 | 211.2 |  | 0.6027 | 66.297 |  | 295.287 |  | 572.784 | 584.1022 | [10 empty] | 13.7287 | 14 | 1.92 | 211.2 |  | 0.6027 | 66.297 |  | 295.287 |  | 572.784 | 584.1022 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 | 0 | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Stairway | Stairway | 0 | [13 empty] | Stairway | 0.58 |  | 3642 | 165 | Stairway | 0.49 |  | 3642 | 165 | 3.7147 |  | 3.2746 | [45 empty] | -795.5777 |  |  |  | Stairway |  |  | Stairway | Stairway
Stairway731 | StairwayTR703 | 0 | [13 empty] | replacement costs are for lamps |  | 731 |  | 165 |  |  | TR703 |  | 165 | 1.1962 | 137.931 | 1.2304 | 134.0997 | 2.7724 | 457.446 |  | 0.58454 | 96.4495 |  | 313.2438 |  |  | 867.1393 | 13.7287 | 14 | 0.0029 | 0.4785 |  | 0.0044588 | 0.73569 |  | 2.103 |  | 3.3172 | 3.3827 | 1.0317 | 170.2298 |  | 0.45861 | 75.6714 |  | 154.9744 |  |  | 400.8755 | 13.7287 | 14 | 0.00261 | 0.43065 |  | 0.0045861 | 0.75671 |  | 2.1244 |  | 3.3117 | 3.3772 | -466.2637 | -1.2151 |  |  | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 | 0 | [15 empty] | 702 |  | 165 |  |  | WG703 |  | 165 | 2.5184 | 65.5172 | 2.0442 | 80.7175 | 2.5976 | 428.6101 |  | 1.5019 | 247.8126 |  | 445.5073 |  |  | 1121.93 | 13.7287 | 14 | 0.0029 | 0.4785 |  | 0.0093868 | 1.5488 |  | 4.0945 |  | 6.1218 | 6.2428 | 2.2321 | 368.2975 |  | 0.76192 | 125.7163 |  | 298.6023 |  |  | 792.6161 | 13.7287 | 14 | 0.00223 | 0.36795 |  | 0.0076192 | 1.2572 |  | 3.3106 |  | 4.9357 | 5.0332 | -329.314 |  |  |  | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 | 0 | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 | 0 | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway731 | StairwayTR703 | 0 | [13 empty] | ballast replacement |  | 731 |  | 165 |  |  | TR703 |  | 165 | 22.968 |  | 26.0739 | [11 empty] | 13.7287 | 14 | 2.0771 | 342.7256 |  | 0.58454 | 96.4495 |  | 451.908 |  | 891.0831 | 908.6909 | [10 empty] | 13.7287 | 14 | 0.77181 | 127.3494 |  | 0.45861 | 75.6714 |  | 265.4778 |  | 468.4985 | 477.756 | 0 | -935.4113 |  |  | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 | 0 | [15 empty] | 702 |  | 165 |  |  | WG703 |  | 165 | 21.924 |  | 17.6616 | [11 empty] | 13.7287 | 14 | 1.9461 | 321.0987 |  | 1.5019 | 247.8126 |  | 809.0164 |  | 1377.9277 | 1405.1556 | [10 empty] | 13.7287 | 14 | 1.6724 | 275.9472 |  | 0.76192 | 125.7163 |  | 481.5633 |  | 883.2267 | 900.6792 | 0 |  |  |  | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 | 0 | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 | 0 | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Lobby | Lobby | 0 | [13 empty] | Lobby | 1 |  | 3642 | 330 | Lobby | 0.84 |  | 3642 | 330 | 9.1859 |  | 8.6456 | [45 empty] | -754.7546 |  |  |  | Lobby |  |  | Lobby | Lobby
Lobby723 | LobbyIP701 | 0 | [13 empty] | replacement costs are for lamps |  | 723 |  | 330 |  |  | IP701 |  | 330 | 5.1652 | 63.8889 | 5.0368 | 65.5173 | 9.962 | 3287.4543 |  | 1.262 | 416.4534 |  | 1984.0038 |  |  | 5687.9114 | 13.7287 | 14 | 0.0072 | 2.376 |  | 0.0096261 | 3.1766 |  | 9.2754 |  | 14.828 | 15.121 | 9.7132 | 3205.3456 |  | 1.2306 | 406.103 |  | 1934.4998 |  |  | 5545.9483 | 13.7287 | 14 | 0.0058 | 1.914 |  | 0.0093868 | 3.0977 |  | 8.7913 |  | 13.803 | 14.0757 | -141.9631 | -42.0151 |  |  | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 | 0 | [15 empty] | 522 |  | 330 |  |  | DL701 |  | 330 | 2.2 | 150 | 1.0421 | 316.6667 | 1.0345 | 341.396 |  | 0.41 | 135.3 |  | 294.9103 |  |  | 771.6063 | 13.7287 | 14 | 0.0012 | 0.396 |  | 0.0041 | 1.353 |  | 3.563 |  | 5.312 | 5.4169 | 0.56987 | 188.0575 |  | 0.19421 | 64.0895 |  | 152.3709 |  |  | 404.5178 | 13.7287 | 14 | 0.0012 | 0.396 |  | 0.0019421 | 0.64089 |  | 1.8189 |  | 2.8558 | 2.9122 | -367.0884 |  |  |  | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 | 0 | [15 empty] | 0 |  | 330 |  |  | 0 |  | 330 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 | 0 | [15 empty] | 534-2 |  | 330 |  |  | WG701 |  | 330 | 1.8207 | 181.25 | 2.5667 | 128.5715 | 2.115 | 697.9614 |  | 0.31929 | 105.366 |  | 437.5887 |  |  | 1240.9161 | 9.8847 | 10 | 0.018483 | 6.0993 |  | 0.030161 | 9.9532 |  | 28.2159 |  | 44.2684 | 44.7849 | 1.4013 | 462.4363 |  | 0.47833 | 157.85 |  | 374.9266 |  |  | 995.213 | 13.7287 | 14 | 0.0014 | 0.462 |  | 0.0047833 | 1.5785 |  | 4.1568 |  | 6.1973 | 6.3198 | -245.7031 |  |  |  | Lobby |  |  | Lobby534-2 | LobbyWG701
Lobby723 | LobbyIP701 | 0 | [13 empty] | ballast replacement |  | 723 |  | 330 |  |  | IP701 |  | 330 | 45.36 |  | 44.37 | [11 empty] | 13.7287 | 14 | 7.4661 | 2463.8087 |  | 1.262 | 416.4534 |  | 2570.5016 |  | 5450.7637 | 5558.4708 | [10 empty] | 13.7287 | 14 | 7.2805 | 2402.5737 |  | 1.2306 | 406.103 |  | 2506.6149 |  | 5315.2915 | 5420.3216 | 0 | 967.4259 |  |  | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 | 0 | [15 empty] | 522 |  | 330 |  |  | DL701 |  | 330 | 5.67 |  | 6.48 | [11 empty] | 0 | 0 | 0.775 | 255.75 |  | 0.41 | 135.3 |  | 492.3253 |  | 883.3753 | 0 | [10 empty] | 13.7287 | 14 | 0.4265 | 140.7461 |  | 0.19421 | 64.0895 |  | 245.5423 |  | 450.3778 | 459.2773 | 0 |  |  |  | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 | 0 | [15 empty] | 0 |  | 330 |  |  | 0 |  | 330 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 | 0 | [15 empty] | 534-2 |  | 330 |  |  | WG701 |  | 330 | 12.96 |  | 12.978 | [11 empty] | 13.7287 | 14 | 0.16552 | 54.6207 |  | 0.33931 | 111.9724 |  | 308.6167 |  | 475.2098 | 484.5999 | [10 empty] | 13.7287 | 14 | 1.0499 | 346.4808 |  | 0.47833 | 157.85 |  | 604.6534 |  | 1108.9842 | 1130.8977 | 0 |  |  |  | Lobby |  |  | Lobby534-2 | LobbyWG701
|  | 0 | [75 empty] | Lobby |  |  | Lobby | Lobby
Large Office | [13 empty] | Large_Office_Interior Lighting LPD |  | Large Office |  |  | 2938 |  | Large Office |  |  | 2938
Office-BLDG-LO | Office-BLDG-LO |  | X | [12 empty] | Office-BLDG-LO | 0.79 |  | 2938 | 498600 | Office-BLDG-LO | 0.64 |  | 2938 | 498600 | 9998.522 |  | 9169.6525 | [45 empty] | -910358.7867 |  |  | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO | Office-BLDG-LO
Office-BLDG-LO735 | Office-BLDG-LOID701 |  | X | [12 empty] | replacement costs are for lamps |  | 735 |  | 498600 |  |  | ID701 |  | 498600 | 9578.3684 | 52.0548 | 8509.4374 | 58.5938 | 12.8649 | 6414441.7642 |  | 1.5489 | 772270.3215 | 2 | 3832247.6811 |  |  | 11018961.7668 | 17.0184 | 18 | 0.0073 | 3639.78 |  | 0.011814 | 5890.6966 |  | 16718.0781 |  | 26248.5546 | 27762.5713 | 11.4284 | 5698176.3072 |  | 1.376 | 686086.3642 |  | 3404370.5906 |  |  | 9788633.2619 | 17.0184 | 18 | 0.005632 | 2808.1152 |  | 0.010496 | 5233.3056 |  | 14584.613 |  | 22626.0338 | 23931.1035 | -1230328.5049 | -3176.0066 | -3831.4678 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO735 | Office-BLDG-LOID701
Office-BLDG-LO0 | Office-BLDG-LO0 |  | X | [14 empty] | 0 |  | 498600 |  |  | 0 |  | 498600 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO0 | Office-BLDG-LO0
Office-BLDG-LO0 | Office-BLDG-LO0 |  | X | [14 empty] | 0 |  | 498600 |  |  | 0 |  | 498600 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO0 | Office-BLDG-LO0
Office-BLDG-LO703 | Office-BLDG-LOWW714 |  | X | [14 empty] | 703 |  | 498600 |  |  | WW714 |  | 498600 | 420.1536 | 1186.7089 | 660.2151 | 755.2085 | 0.64864 | 323413.2336 |  | 0.082918 | 41343.1142 |  | 195542.7287 |  |  | 560299.0765 | 17.0184 | 18 | 0.000632 | 315.1152 |  | 0.00051824 | 258.3945 |  | 831.1679 |  | 1404.6776 | 1485.6994 | 1.019 | 508088.3924 |  | 0.1303 | 64965.173 |  | 307215.2293 |  |  | 880268.7947 | 17.0184 | 18 | 0.000768 | 382.9248 |  | 0.00081434 | 406.0323 |  | 1235.4365 |  | 2024.3936 | 2141.1606 | 319969.7182 |  | 655.4612 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO703 | Office-BLDG-LOWW714
Office-BLDG-LO735 | Office-BLDG-LOID701 |  | X | [12 empty] | ballast replacement |  | 735 |  | 498600 |  |  | ID701 |  | 498600 | 65.7 |  | 55.7568 | [11 empty] | 17.0184 | 18 | 9.6432 | 4808101.4882 |  | 1.5489 | 772270.3215 |  | 4917278.591 |  | 10497650.4007 | 11103154.8758 | [10 empty] | 17.0184 | 18 | 8.567 | 4271526.144 |  | 1.376 | 686086.3642 |  | 4368519.2816 |  | 9326131.7898 | 9864063.0714 | 0 | -914314.7345 | -1239091.8044 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO735 | Office-BLDG-LOID701
Office-BLDG-LO0 | Office-BLDG-LO0 |  | X | [14 empty] | 0 |  | 498600 |  |  | 0 |  | 498600 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO0 | Office-BLDG-LO0
Office-BLDG-LO0 | Office-BLDG-LO0 |  | X | [14 empty] | 0 |  | 498600 |  |  | 0 |  | 498600 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO0 | Office-BLDG-LO0
Office-BLDG-LO703 | Office-BLDG-LOWW714 |  | X | [14 empty] | 703 |  | 498600 |  |  | WW714 |  | 498600 | 3.9816 |  | 6.2899 | [11 empty] | 17.0184 | 18 | 0.48601 | 242323.5888 |  | 0.082918 | 41343.1142 |  | 253756.6198 |  | 537423.3228 | 568421.9001 | [10 empty] | 17.0184 | 18 | 0.7637 | 380779.1007 |  | 0.1303 | 64965.173 |  | 398744.5793 |  | 844488.8529 | 893198.97 | 0 |  | 324777.0699 | LgOfc | Office-BLDG-LO |  |  | Office-BLDG-LO703 | Office-BLDG-LOWW714
Office - Open Plan (Including Other)-whole-large | Office - Open Plan (Including Other)-whole-large |  | 0 | [12 empty] | Office - Open Plan (Including Other)-whole | 0.81 |  | 2938 | 285144 | Office - Open Plan (Including Other)-whole-large | 0.61 |  | 2938 | 285144 | 8637.3619 |  | 5084.6196 | [45 empty] | -298335.8628 |  |  |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole | Office - Open Plan (Including Other)-whole
Office - Open Plan (Including Other)735-whole-Large | Office - Open Plan (Including Other)ID701-whole-large |  | 0 | [12 empty] | replacement costs are for lamps |  | 735 |  | 285144 |  |  | ID701 |  | 285144 | 3751.8947 | 76 | 4838.8058 | 58.9286 | 8.8116 | 2512568.8674 |  | 1.0609 | 302502.141 | 2 | 1501110.9021 |  |  | 4316183.9105 | 17.0184 | 18 | 0.005 | 1425.72 |  | 0.0080921 | 2307.4153 |  | 6548.5546 |  | 10281.6899 | 10874.7378 | 11.3634 | 3240210.514 |  | 1.3682 | 390136.0946 |  | 1935861.017 |  |  | 5566207.6256 | 17.0184 | 18 | 0.0056 | 1596.8064 |  | 0.010436 | 2975.8665 |  | 8293.3932 |  | 12866.0661 | 13608.1807 | 1250023.7152 | -8953.7485 | 2733.443 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole735 | Office - Open Plan (Including Other)-wholeID701
Office - Open Plan (Including Other)739-whole-large | Office - Open Plan (Including Other)0-whole-large |  | 0 | [14 empty] | 739 |  | 285144 |  |  | 0 |  | 285144 | 4277.16 | 66.6667 | 0 | 0 | 1.9215 | 547904.196 |  | 0.45203 | 128892.2166 |  | 388095.3875 |  |  | 1064891.8001 | 17.0184 | 18 | 0.0015 | 427.716 |  | 0.009225 | 2630.4534 |  | 6711.6756 |  | 9769.845 | 10333.3697 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -1064891.8001 |  | -10333.3697 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole739 | Office - Open Plan (Including Other)-whole0
Office - Open Plan (Including Other)0-whole-large | Office - Open Plan (Including Other)0-whole-large |  | 0 | [14 empty] | 0 |  | 285144 |  |  | 0 |  | 285144 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole0 | Office - Open Plan (Including Other)-whole0
Office - Open Plan (Including Other)703-whole-large | Office - Open Plan (Including Other)WW714-whole-large |  | 0 | [14 empty] | 703 |  | 285144 |  |  | WW714 |  | 285144 | 608.3072 | 468.75 | 245.8138 | 1160.0002 | 1.6421 | 468244.4672 |  | 0.20992 | 59857.4285 |  | 283110.8665 |  |  | 811212.7622 | 17.0184 | 18 | 0.0016 | 456.2304 |  | 0.001312 | 374.1089 |  | 1203.3824 |  | 2033.7217 | 2151.0267 | 0.66343 | 189173.3789 |  | 0.084828 | 24188.0772 |  | 114383.5282 |  |  | 327744.9844 | 17.0184 | 18 | 0.0005 | 142.572 |  | 0.00053017 | 151.1755 |  | 459.9823 |  | 753.7298 | 797.205 | -483467.7778 |  | -1353.8218 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole703 | Office - Open Plan (Including Other)-wholeWW714
Office - Open Plan (Including Other)735-whole-Large | Office - Open Plan (Including Other)ID701-whole-large |  | 0 | [12 empty] | ballast replacement |  | 735 |  | 285144 |  |  | ID701 |  | 285144 | 45 |  | 55.44 | [11 empty] | 17.0184 | 18 | 6.6049 | 1883357.3605 |  | 1.0609 | 302502.141 |  | 1926122.5769 |  | 4111982.0784 | 4349161.2047 | [10 empty] | 17.0184 | 18 | 8.5184 | 2428960.2807 |  | 1.3682 | 390136.0946 |  | 2484114.4506 |  | 5303210.8259 | 5609100.0264 | 0 | -408292.5318 | 1259938.8217 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole735 | Office - Open Plan (Including Other)-wholeID701
Office - Open Plan (Including Other)739-whole-large | Office - Open Plan (Including Other)0-whole-large |  | 0 | [14 empty] | 739 |  | 285144 |  |  | 0 |  | 285144 | 9.18 |  | 1e-05 | [11 empty] | 17.0184 | 18 | 1.44 | 410607.36 |  | 0.45203 | 128892.2166 |  | 574086.1891 |  | 1113585.7657 | 1177817.3927 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | -1177817.3927 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole739 | Office - Open Plan (Including Other)-whole0
Office - Open Plan (Including Other)0-whole-large | Office - Open Plan (Including Other)0-whole-large |  | 0 | [14 empty] | 0 |  | 285144 |  |  | 0 |  | 285144 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole0 | Office - Open Plan (Including Other)-whole0
Office - Open Plan (Including Other)703-whole-large | Office - Open Plan (Including Other)WW714-whole-large |  | 0 | [14 empty] | 703 |  | 285144 |  |  | WW714 |  | 285144 | 10.08 |  | 4.095 | [11 empty] | 17.0184 | 18 | 1.2304 | 350841.1776 |  | 0.20992 | 59857.4285 |  | 367394.1598 |  | 778092.7659 | 822973.1566 | [10 empty] | 17.0184 | 18 | 0.4972 | 141773.1052 |  | 0.084828 | 24188.0772 |  | 148462.0797 |  | 314423.2621 | 332559.1958 | 0 |  | -490413.9608 |  | Office - Open Plan (Including Other)-whole |  |  | Office - Open Plan (Including Other)-whole703 | Office - Open Plan (Including Other)-wholeWW714
Office-Enclosed-whole-large | Office-Enclosed-whole-Large |  | 0 | [12 empty] | Office-Enclosed-whole-large | 0.826 |  | 2938 | 92363 | Office-Enclosed-whole-large | 0.74 |  | 2938 | 92363 | 3663.7323 |  | 2135.8937 | [45 empty] | -429389.3896 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large | Office-Enclosed-whole-large
Office-Enclosed700-whole-large | Office-EnclosedTR701-whole-large |  | 0 | [12 empty] | replacement costs are for lamps |  | 700 |  | 92363 |  |  | TR701 |  | 92363 | 1539.3833 | 60 | 2135.8937 | 43.2433 | 2.306 | 212989.078 |  | 1.5467 | 142860.1612 |  | 240420.1156 |  |  | 596269.3548 | 17.0184 | 18 | 0.006 | 554.178 |  | 0.01025 | 946.7207 |  | 2667.4634 |  | 4168.3621 | 4408.7933 | 3.1987 | 295436.91 |  | 1.4222 | 131357.5041 |  | 268988.335 |  |  | 695782.749 | 17.0184 | 18 | 0.0074 | 683.4862 |  | 0.014222 | 1313.575 |  | 3647.339 |  | 5644.4002 | 5969.9692 | 99513.3942 | -3571.1276 |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large700 | Office-Enclosed-whole-largeTR701
Office-Enclosed739-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 739 |  | 92363 |  |  | 0 |  | 92363 | 2124.349 | 43.4783 | 0 | 0 | 2.9463 | 272129.1069 |  | 0.6931 | 64017.2571 |  | 192756.4198 |  |  | 528902.7838 | 17.0184 | 18 | 0.0023 | 212.4349 |  | 0.014145 | 1306.4746 |  | 3333.5067 |  | 4852.4162 | 5132.3036 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -528902.7838 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large739 | Office-Enclosed-whole-large0
Office-Enclosed0-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 0 |  | 92363 |  |  | 0 |  | 92363 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large0 | Office-Enclosed-whole-large0
Office-Enclosed0-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 0 |  | 92363 |  |  | 0 |  | 92363 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large0 | Office-Enclosed-whole-large0
Office-Enclosed700-whole-large | Office-EnclosedTR701-whole-large |  | 0 | [12 empty] | ballast replacement |  | 700 |  | 92363 |  |  | TR701 |  | 92363 | 55.62 |  | 76.59 | [11 empty] | 17.0184 | 18 | 1.725 | 159326.175 |  | 1.5467 | 142860.1612 |  | 450160.1981 |  | 752346.5342 | 795741.8823 | [10 empty] | 17.0184 | 18 | 2.3934 | 221065.0678 |  | 1.4222 | 131357.5041 |  | 460841.4149 |  | 813263.9868 | 860173.0535 | 0 | -520558.682 |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large700 | Office-Enclosed-whole-largeTR701
Office-Enclosed739-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 739 |  | 92363 |  |  | 0 |  | 92363 | 14.076 |  | 1e-05 | [11 empty] | 17.0184 | 18 | 2.208 | 203937.504 |  | 0.6931 | 64017.2571 |  | 285132.9905 |  | 553087.7517 | 584989.8532 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large739 | Office-Enclosed-whole-large0
Office-Enclosed0-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 0 |  | 92363 |  |  | 0 |  | 92363 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large0 | Office-Enclosed-whole-large0
Office-Enclosed0-whole-large | Office-Enclosed0-whole-large |  | 0 | [14 empty] | 0 |  | 92363 |  |  | 0 |  | 92363 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Office-Enclosed-whole-large |  |  | Office-Enclosed-whole-large0 | Office-Enclosed-whole-large0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  | 0 | [12 empty] | Conference/Meeting/Multipurpose | 1.07 |  | 2938 | 9628 | Conference/Meeting/Multipurpose | 0.97 |  | 2938 | 9628 | 270.3863 |  | 261.36 | [45 empty] | -1572.0672 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 |  | 0 | [12 empty] | replacement costs are for lamps |  | 731 |  | 9628 |  |  | TR704 |  | 9628 | 108.315 | 88.8889 | 147.4287 | 65.3061 | 4.302 | 41419.656 |  | 0.90705 | 8733.0593 |  | 28362.8025 |  |  | 78515.5178 | 17.0184 | 18 | 0.0045 | 43.326 |  | 0.0069188 | 66.6137 |  | 190.4162 |  | 300.356 | 317.6805 | 2.118 | 20392.3447 |  | 0.94172 | 9066.8681 |  | 18566.7486 |  |  | 48025.9615 | 17.0184 | 18 | 0.0049 | 47.1772 |  | 0.0094172 | 90.6687 |  | 251.7553 |  | 389.6011 | 412.0733 | -30489.5564 | -4241.2157 |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 |  | 0 | [14 empty] | 511 |  | 9628 |  |  | DL702 |  | 9628 | 70.6053 | 136.3636 | 64.1866 | 150.0001 | 0.42871 | 4127.5878 |  | 0.451 | 4342.228 |  | 6178.5643 |  |  | 14648.3801 | 1.4295 | 2 | 0.15679 | 1509.542 |  | 0.02134 | 205.4615 |  | 1453.2013 |  | 3168.2048 | 4432.4694 | 1.2021 | 11574.0884 |  | 0.41 | 3947.48 |  | 9380.6959 |  |  | 24902.2643 | 17.0184 | 18 | 0.0016 | 15.4048 |  | 0.0041 | 39.4748 |  | 106.3762 |  | 161.2558 | 170.557 | 10253.8842 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 |  | 0 | [14 empty] | 0 |  | 9628 |  |  | 0 |  | 9628 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 |  | 0 | [14 empty] | 727-1 |  | 9628 |  |  | WW704 |  | 9628 | 91.466 | 105.2632 | 49.7447 | 193.5484 | 2.5669 | 24714.1132 |  | 0.58425 | 5625.159 |  | 17323.4548 |  |  | 47662.727 | 17.0184 | 18 | 0.0019 | 18.2932 |  | 0.0058425 | 56.2516 |  | 149.2836 |  | 223.8284 | 236.7389 | 3.9763 | 38283.4955 |  | 0.5084 | 4894.8752 |  | 23147.9613 |  |  | 66326.332 | 17.0184 | 18 | 0.0031 | 29.8468 |  | 0.0031775 | 30.593 |  | 93.7115 |  | 154.1512 | 163.0427 | 18663.605 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 |  | 0 | [12 empty] | ballast replacement |  | 731 |  | 9628 |  |  | TR704 |  | 9628 | 35.64 |  | 48.951 | [11 empty] | 17.0184 | 18 | 3.2231 | 31032.2475 |  | 0.90705 | 8733.0593 |  | 40918.2195 |  | 80683.5263 | 85337.3521 | [10 empty] | 17.0184 | 18 | 1.5848 | 15258.8756 |  | 0.94172 | 9066.8681 |  | 31809.2854 |  | 56135.0291 | 59372.8976 | 0 | 18234.8067 |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 |  | 0 | [14 empty] | 511 |  | 9628 |  |  | DL702 |  | 9628 | 2.4651 |  | 8.64 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 17.0184 | 18 | 0.9004 | 8669.0127 |  | 0.41 | 3947.48 |  | 15123.7495 |  | 27740.2422 | 29340.2994 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 |  | 0 | [14 empty] | 0 |  | 9628 |  |  | 0 |  | 9628 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 |  | 0 | [14 empty] | 727-1 |  | 9628 |  |  | WW704 |  | 9628 | 17.1 |  | 13.113 | [11 empty] | 17.0184 | 18 | 1.9238 | 18521.865 |  | 0.58425 | 5625.159 |  | 25433.3173 |  | 49580.3413 | 52440.1353 | [10 empty] | 17.0184 | 18 | 2.9799 | 28690.2365 |  | 0.5084 | 4894.8752 |  | 30043.866 |  | 63628.9777 | 67299.0972 | 0 |  |  |  | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Corridor/Transition | Corridor/Transition |  | 0 | [12 empty] | Corridor/Transition | 0.66 |  | 2938 | 21304 | Corridor/Transition | 0.41 |  | 2938 | 21304 | 754.1616 |  | 494.4132 | [45 empty] | -105772.5153 |  |  |  | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 |  | 0 | [12 empty] | replacement costs are for lamps |  | 701 |  | 21304 |  |  | DL706 |  | 21304 | 674.6267 | 31.5789 | 426.0796 | 50 | 5.2271 | 111358.4651 |  | 1.9475 | 41489.54 |  | 93643.3464 |  |  | 246491.3514 | 17.0184 | 18 | 0.0038 | 80.9552 |  | 0.019475 | 414.8954 |  | 1067.1084 |  | 1562.959 | 1653.1104 | 3.3013 | 70331.6621 |  | 1.23 | 26203.92 |  | 59143.1661 |  |  | 155678.7483 | 17.0184 | 18 | 0.0024 | 51.1296 |  | 0.0123 | 262.0392 |  | 673.9632 |  | 987.132 | 1044.0698 | -90812.6032 | -674.5567 |  |  | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  | 0 | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  | 0 | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  | 0 | [14 empty] | 703 |  | 21304 |  |  | WW708 |  | 21304 | 79.5349 | 267.8571 | 68.3336 | 311.7648 | 2.8737 | 61222.0149 |  | 0.36736 | 7826.2374 |  | 37016.1719 |  |  | 106064.4243 | 17.0184 | 18 | 0.0028 | 59.6512 |  | 0.002296 | 48.914 |  | 157.3398 |  | 265.905 | 281.2424 | 2.4683 | 52584.7436 |  | 0.31562 | 6724.0248 |  | 31795.7438 |  |  | 91104.5122 | 17.0184 | 18 | 0.0017 | 36.2168 |  | 0.0019726 | 42.0252 |  | 125.7199 |  | 203.9619 | 215.7264 | -14959.9121 |  |  |  | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 |  | 0 | [12 empty] | ballast replacement |  | 701 |  | 21304 |  |  | DL706 |  | 21304 | 23.256 |  | 14.688 | [11 empty] | 17.0184 | 18 | 3.9175 | 83458.1324 |  | 1.9475 | 41489.54 |  | 154138.0367 |  | 279085.709 | 295183.3727 | [10 empty] | 17.0184 | 18 | 2.4742 | 52710.3994 |  | 1.23 | 26203.92 |  | 97350.3389 |  | 176264.6583 | 186431.6038 | 0 | -123905.9691 |  |  | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  | 0 | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  | 0 | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  | 0 | [14 empty] | 703 |  | 21304 |  |  | WW708 |  | 21304 | 17.64 |  | 15.147 | [11 empty] | 17.0184 | 18 | 2.1532 | 45871.7728 |  | 0.36736 | 7826.2374 |  | 48036.0417 |  | 101734.0519 | 107602.072 | [10 empty] | 17.0184 | 18 | 1.85 | 39411.3951 |  | 0.31562 | 6724.0248 |  | 41270.8579 |  | 87406.2777 | 92447.8719 | 0 |  |  |  | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Storage | Storage |  | 0 | [12 empty] | Storage | 0.46 |  | 2938 | 11866 | Storage | 0.38 |  | 2938 | 11866 | 143.6411 |  | 121.867 | [45 empty] | -24813.9308 |  |  |  | Storage |  |  | Storage | Storage
Storage738 | StorageLB702 |  | 0 | [12 empty] | replacement costs are for lamps |  | 738 |  | 11866 |  |  | LB702 |  | 11866 | 143.6411 | 82.6087 | 121.867 | 97.3684 | 3.0309 | 35964.8468 |  | 0.70055 | 8312.7232 |  | 25332.1187 |  |  | 69609.6887 | 17.0184 | 18 | 0.0046 | 54.5836 |  | 0.0074447 | 88.3392 |  | 250.711 |  | 393.6338 | 416.3386 | 1.76 | 20884.3524 |  | 0.59436 | 7052.6277 |  | 16858.7778 |  |  | 44795.7578 | 17.0184 | 18 | 0.0038 | 45.0908 |  | 0.0063162 | 74.9482 |  | 211.9397 |  | 331.9787 | 351.1273 | -24813.9308 | -65.2114 |  |  | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage738 | StorageLB702 |  | 0 | [12 empty] | ballast replacement |  | 738 |  | 11866 |  |  | LB702 |  | 11866 | 47.61 |  | 35.226 | [11 empty] | 17.0184 | 18 | 2.2697 | 26932.6974 |  | 0.70055 | 8312.7232 |  | 37308.8034 |  | 72554.2239 | 76739.1516 | [10 empty] | 17.0184 | 18 | 1.3172 | 15629.4462 |  | 0.59436 | 7052.6277 |  | 27109.2159 |  | 49791.2898 | 52663.2514 | 0 | -24075.9002 |  |  | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  | 0 | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Storage |  |  | Storage0 | Storage0
Restrooms | Restrooms |  | 0 | [12 empty] | Restrooms | 0.85 |  | 2938 | 15505 | Restrooms | 0.63 |  | 2938 | 15505 | 488.4804 |  | 498.3994 | [45 empty] | -69606.2923 |  |  |  | Restrooms |  |  | Restrooms | Restrooms
Restrooms604 | RestroomsDL709 |  | 0 | [12 empty] | replacement costs are for lamps |  | 604 |  | 15505 |  |  | DL709 |  | 15505 | 187.1293 | 82.8571 | 274.4384 | 56.4972 | 4.2525 | 65935.0125 |  | 0.3637 | 5639.1418 |  | 37172.4517 |  |  | 108746.606 | 12.2532 | 13 | 0.040431 | 626.8832 |  | 0.065978 | 1022.9864 |  | 2900.0079 |  | 4549.8774 | 4827.1672 | 3.5159 | 54514.0794 |  | 1.0885 | 16877.9677 |  | 42527.6503 |  |  | 113919.6975 | 17.0184 | 18 | 0.003717 | 57.6321 |  | 0.010885 | 168.7797 |  | 449.6441 |  | 676.0559 | 715.0508 | 5173.0915 | -8047.4219 |  |  | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  | 0 | [14 empty] | 720 |  | 15505 |  |  | 0 |  | 15505 | 140.9545 | 110 | 0 | 0 | 1.5353 | 23805.3903 |  | 0.55909 | 8668.7045 |  | 19824.684 |  |  | 52298.7789 | 17.0184 | 18 | 0.002 | 31.01 |  | 0.0055909 | 86.687 |  | 231.8291 |  | 349.5261 | 369.6868 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -52298.7789 |  |  |  | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  | 0 | [14 empty] | 0 |  | 15505 |  |  | 0 |  | 15505 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  | 0 | [14 empty] | 534-2 |  | 15505 |  |  | WG701 |  | 15505 | 160.3966 | 96.6667 | 223.961 | 69.2308 | 3.9657 | 61488.0181 |  | 0.59867 | 9282.389 |  | 38550.0695 |  |  | 109320.4767 | 12.2532 | 13 | 0.034655 | 537.3284 |  | 0.056552 | 876.8454 |  | 2485.721 |  | 3899.8949 | 4137.5719 | 2.6025 | 40351.0734 |  | 0.88833 | 13773.6083 |  | 32715.1901 |  |  | 86839.8718 | 17.0184 | 18 | 0.0026 | 40.313 |  | 0.0088833 | 137.7361 |  | 362.7129 |  | 540.762 | 571.9532 | -22480.6049 |  |  |  | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Restrooms604 | RestroomsDL709 |  | 0 | [12 empty] | ballast replacement |  | 604 |  | 15505 |  |  | DL709 |  | 15505 | 24.2393 |  | 28.7696 | [11 empty] | 17.0184 | 18 | 0.36207 | 5613.8793 |  | 0.74224 | 11508.4526 |  | 31719.424 |  | 48841.7559 | 51658.9484 | [10 empty] | 17.0184 | 18 | 2.6341 | 40842.3355 |  | 1.0885 | 16877.9677 |  | 67040.4104 |  | 124760.7137 | 131956.9117 | 0 | 76015.1642 |  |  | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  | 0 | [14 empty] | 720 |  | 15505 |  |  | 0 |  | 15505 | 12.6 |  | 1e-05 | [11 empty] | 17.0184 | 18 | 1.15 | 17830.7852 |  | 0.55909 | 8668.7045 |  | 32452.6575 |  | 58952.1473 | 62352.5071 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  | 0 | [14 empty] | 0 |  | 15505 |  |  | 0 |  | 15505 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  | 0 | [14 empty] | 534-2 |  | 15505 |  |  | WG701 |  | 15505 | 24.3 |  | 24.102 | [11 empty] | 17.0184 | 18 | 0.31034 | 4811.8966 |  | 0.63621 | 9864.3879 |  | 27188.0777 |  | 41864.3622 | 44279.0986 | [10 empty] | 17.0184 | 18 | 1.9499 | 30233.0703 |  | 0.88833 | 13773.6083 |  | 52760.5918 |  | 96767.2704 | 102348.8066 | 0 |  |  |  | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Lounge/Recreation - Break room | Lounge/Recreation - Break room |  | 0 | [12 empty] | Lounge/Recreation - Break room | #N/A |  | 2938 | 9530 | Lounge/Recreation - Break room | #N/A |  | 2938 | 9530 | 290.0297 |  | 481.7939 | [45 empty] | 12569.1651 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 |  | 0 | [12 empty] | replacement costs are for lamps |  | 522 |  | 9530 |  |  | DL707 |  | 9530 | 179.4817 | 53.0973 | 333.5496 | 28.5715 | 2.9226 | 27851.965 |  | 1.1583 | 11038.1225 |  | 24059.5404 |  |  | 62949.6279 | 17.0184 | 18 | 0.00339 | 32.3067 |  | 0.011583 | 110.3812 |  | 290.6769 |  | 433.3648 | 458.3613 | 7.1431 | 68073.8526 |  | 2.1525 | 20513.325 |  | 52562.507 |  |  | 141149.6846 | 17.0184 | 18 | 0.0028 | 26.684 |  | 0.021525 | 205.1333 |  | 519.205 |  | 751.0223 | 794.3413 | 78200.0567 | 418.9138 |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  | 0 | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  | 0 | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 |  | 0 | [14 empty] | 727-2 |  | 9530 |  |  | WG702 |  | 9530 | 110.548 | 86.2069 | 148.2444 | 64.2857 | 7.7749 | 74094.797 |  | 0.7134 | 6798.702 |  | 42218.4815 |  |  | 123111.9805 | 17.0184 | 18 | 0.0029 | 27.637 |  | 0.007134 | 67.987 |  | 183.9063 |  | 279.5303 | 295.6536 | 2.8026 | 26709.2016 |  | 0.95667 | 9117.0333 |  | 21654.8541 |  |  | 57481.089 | 17.0184 | 18 | 0.0028 | 26.684 |  | 0.0095667 | 91.1703 |  | 240.0871 |  | 357.9415 | 378.5875 | -65630.8916 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 |  | 0 | [12 empty] | ballast replacement |  | 522 |  | 9530 |  |  | DL707 |  | 9530 | 16.0178 |  | 22.428 | [11 empty] | 0 | 0 | 2.1894 | 20864.7438 |  | 1.1583 | 11038.1225 |  | 40165.1657 |  | 72068.032 | 0 | [10 empty] | 17.0184 | 18 | 5.3552 | 51035.3764 |  | 2.1525 | 20513.325 |  | 82358.8105 |  | 153907.5119 | 162784.8972 | 0 | 109999.0798 |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  | 0 | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  | 0 | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 |  | 0 | [14 empty] | 727-2 |  | 9530 |  |  | WG702 |  | 9530 | 26.1 |  | 22.176 | [11 empty] | 17.0184 | 18 | 5.829 | 55550.37 |  | 0.7134 | 6798.702 |  | 51610.3371 |  | 113959.4091 | 120532.5878 | [10 empty] | 17.0184 | 18 | 2.0999 | 20011.8882 |  | 0.95667 | 9117.0333 |  | 34923.3159 |  | 64052.2374 | 67746.7704 | 0 |  |  |  | #N/A |  |  | #N/A | #N/A
Electrical/Mechanical | Electrical/Mechanical |  | 0 | [12 empty] | Electrical/Mechanical | 0.43 |  | 2938 | 31023 | Electrical/Mechanical | 0.43 |  | 2938 | 31023 | 808.2308 |  | 813.305 | [45 empty] | -20109.3211 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical | Electrical/Mechanical
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  | 0 | [12 empty] | replacement costs are for lamps |  | 738 |  | 31023 |  |  | LB702 |  | 31023 | 187.7708 | 165.2174 | 192.8456 | 160.8696 | 1.5155 | 47014.0503 |  | 0.35027 | 10866.5772 |  | 33114.7109 |  |  | 90995.3384 | 17.0184 | 18 | 0.0023 | 71.3529 |  | 0.0037224 | 115.479 |  | 327.735 |  | 514.567 | 544.2472 | 1.0653 | 33047.9634 |  | 0.35974 | 11160.2685 |  | 26677.7853 |  |  | 70886.0173 | 17.0184 | 18 | 0.0023 | 71.3529 |  | 0.003823 | 118.6001 |  | 335.3791 |  | 525.3321 | 555.6332 | -20109.3211 | 11.3861 |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  | 0 | [14 empty] | 739 |  | 31023 |  |  | TL702 |  | 31023 | 620.46 | 50 | 620.4594 | 50.0001 | 2.562 | 79480.926 |  | 0.6027 | 18697.5621 |  | 56298.4934 |  |  | 154476.9815 | 17.0184 | 18 | 0.002 | 62.046 |  | 0.0123 | 381.5829 |  | 973.6195 |  | 1417.2484 | 1498.9953 | 2.562 | 79480.926 |  | 0.6027 | 18697.5621 |  | 56298.4934 |  |  | 154476.9815 | 17.0184 | 18 | 0.002 | 62.046 |  | 0.0123 | 381.5829 |  | 973.6195 |  | 1417.2484 | 1498.9953 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  | 0 | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  | 0 | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  | 0 | [12 empty] | ballast replacement |  | 738 |  | 31023 |  |  | LB702 |  | 31023 | 23.805 |  | 21.321 | [11 empty] | 17.0184 | 18 | 1.1349 | 35207.023 |  | 0.35027 | 10866.5772 |  | 48770.9004 |  | 94844.5006 | 100315.1314 | [10 empty] | 17.0184 | 18 | 0.79723 | 24732.4579 |  | 0.35974 | 11160.2685 |  | 42898.3556 |  | 78791.082 | 83335.7516 | 0 | -16979.3798 |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  | 0 | [14 empty] | 739 |  | 31023 |  |  | TL702 |  | 31023 | 12.24 |  | 12.24 | [11 empty] | 17.0184 | 18 | 1.92 | 59564.16 |  | 0.6027 | 18697.5621 |  | 83278.9788 |  | 161540.7009 | 170858.3685 | [10 empty] | 17.0184 | 18 | 1.92 | 59564.16 |  | 0.6027 | 18697.5621 |  | 83278.9788 |  | 161540.7009 | 170858.3685 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  | 0 | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  | 0 | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Stairway | Stairway |  | 0 | [12 empty] | Stairway | 0.58 |  | 2938 | 8484 | Stairway | 0.49 |  | 2938 | 8484 | 191.0016 |  | 168.3737 | [45 empty] | -40907.1584 |  |  |  | Stairway |  |  | Stairway | Stairway
Stairway731 | StairwayTR703 |  | 0 | [12 empty] | replacement costs are for lamps |  | 731 |  | 8484 |  |  | TR703 |  | 8484 | 61.509 | 137.931 | 63.2664 | 134.0997 | 2.7724 | 23521.0416 |  | 0.58454 | 4959.2554 |  | 16106.4268 |  |  | 44586.7238 | 17.0184 | 18 | 0.0029 | 24.6036 |  | 0.0044588 | 37.828 |  | 108.1319 |  | 170.5636 | 180.4017 | 1.0317 | 8752.9064 |  | 0.45861 | 3890.8836 |  | 7968.5 |  |  | 20612.29 | 17.0184 | 18 | 0.00261 | 22.1432 |  | 0.0045861 | 38.9088 |  | 109.2307 |  | 170.2828 | 180.1047 | -23974.4337 | -64.8039 |  |  | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 |  | 0 | [14 empty] | 702 |  | 8484 |  |  | WG703 |  | 8484 | 129.4926 | 65.5172 | 105.1073 | 80.7175 | 2.5976 | 22038.351 |  | 1.5019 | 12742.0749 |  | 22907.1749 |  |  | 57687.6009 | 17.0184 | 18 | 0.0029 | 24.6036 |  | 0.0093868 | 79.638 |  | 210.5328 |  | 314.7744 | 332.9306 | 2.2321 | 18937.1882 |  | 0.76192 | 6464.101 |  | 15353.5869 |  |  | 40754.8762 | 17.0184 | 18 | 0.00223 | 18.9193 |  | 0.0076192 | 64.641 |  | 170.225 |  | 253.7854 | 268.4237 | -16932.7247 |  |  |  | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 |  | 0 | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 |  | 0 | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway731 | StairwayTR703 |  | 0 | [12 empty] | ballast replacement |  | 731 |  | 8484 |  |  | TR703 |  | 8484 | 22.968 |  | 26.0739 | [11 empty] | 17.0184 | 18 | 2.0771 | 17622.3285 |  | 0.58454 | 4959.2554 |  | 23236.2901 |  | 45817.874 | 48460.6489 | [10 empty] | 17.0184 | 18 | 0.77181 | 6548.0724 |  | 0.45861 | 3890.8836 |  | 13650.3835 |  | 24089.3395 | 25478.8126 | 0 | -49885.65 |  |  | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 |  | 0 | [14 empty] | 702 |  | 8484 |  |  | WG703 |  | 8484 | 21.924 |  | 17.6616 | [11 empty] | 17.0184 | 18 | 1.9461 | 16510.3105 |  | 1.5019 | 12742.0749 |  | 41598.1535 |  | 70850.539 | 74937.198 | [10 empty] | 17.0184 | 18 | 1.6724 | 14188.7017 |  | 0.76192 | 6464.101 |  | 24761.1073 |  | 45413.91 | 48033.3844 | 0 |  |  |  | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 |  | 0 | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 |  | 0 | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Stairway |  |  | Stairway0 | Stairway0
Lobby | Lobby |  | 0 | [12 empty] | Lobby | 1 |  | 2938 | 13792 | Lobby | 0.84 |  | 2938 | 13792 | 383.9152 |  | 361.3341 | [45 empty] | -31544.1688 |  |  |  | Lobby |  |  | Lobby | Lobby
Lobby723 | LobbyIP701 |  | 0 | [12 empty] | replacement costs are for lamps |  | 723 |  | 13792 |  |  | IP701 |  | 13792 | 215.8748 | 63.8889 | 210.5094 | 65.5173 | 9.962 | 137395.6641 |  | 1.262 | 17405.2282 |  | 82919.3325 |  |  | 237720.2248 | 17.0184 | 18 | 0.0072 | 99.3024 |  | 0.0096261 | 132.763 |  | 387.6561 |  | 619.7214 | 655.467 | 9.7132 | 133964.0189 |  | 1.2306 | 16972.6421 |  | 80850.3681 |  |  | 231787.0291 | 17.0184 | 18 | 0.0058 | 79.9936 |  | 0.0093868 | 129.4633 |  | 367.4231 |  | 576.88 | 610.1545 | -5933.1957 | -1842.8451 |  |  | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  | 0 | [14 empty] | 522 |  | 13792 |  |  | DL701 |  | 13792 | 91.9467 | 150 | 43.5537 | 316.6667 | 1.0345 | 14268.2837 |  | 0.41 | 5654.72 |  | 12325.4624 |  |  | 32248.4662 | 17.0184 | 18 | 0.0012 | 16.5504 |  | 0.0041 | 56.5472 |  | 148.9109 |  | 222.0085 | 234.8139 | 0.56987 | 7859.663 |  | 0.19421 | 2678.5516 |  | 6368.1792 |  |  | 16906.3938 | 17.0184 | 18 | 0.0012 | 16.5504 |  | 0.0019421 | 26.7855 |  | 76.0186 |  | 119.3545 | 126.2389 | -15342.0723 |  |  |  | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  | 0 | [14 empty] | 0 |  | 13792 |  |  | 0 |  | 13792 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  | 0 | [14 empty] | 534-2 |  | 13792 |  |  | WG701 |  | 13792 | 76.0938 | 181.25 | 107.2711 | 128.5715 | 2.115 | 29170.5556 |  | 0.31929 | 4403.6619 |  | 18288.5541 |  |  | 51862.7716 | 12.2532 | 13 | 0.018483 | 254.9142 |  | 0.030161 | 415.9846 |  | 1179.2519 |  | 1850.1507 | 1962.9071 | 1.4013 | 19327.0361 |  | 0.47833 | 6597.1733 |  | 15669.6615 |  |  | 41593.8709 | 17.0184 | 18 | 0.0014 | 19.3088 |  | 0.0047833 | 65.9717 |  | 173.7294 |  | 259.0099 | 273.9496 | -10268.9008 |  |  |  | Lobby |  |  | Lobby534-2 | LobbyWG701
Lobby723 | LobbyIP701 |  | 0 | [12 empty] | ballast replacement |  | 723 |  | 13792 |  |  | IP701 |  | 13792 | 45.36 |  | 44.37 | [11 empty] | 17.0184 | 18 | 7.4661 | 102972.2713 |  | 1.262 | 17405.2282 |  | 107431.3876 |  | 227808.8871 | 240948.9037 | [10 empty] | 17.0184 | 18 | 7.2805 | 100413.0189 |  | 1.2306 | 16972.6421 |  | 104761.3093 |  | 222146.9703 | 234960.4076 | 0 | 41936.0344 |  |  | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  | 0 | [14 empty] | 522 |  | 13792 |  |  | DL701 |  | 13792 | 5.67 |  | 6.48 | [11 empty] | 0 | 0 | 0.775 | 10688.8 |  | 0.41 | 5654.72 |  | 20576.2136 |  | 36919.7336 | 0 | [10 empty] | 17.0184 | 18 | 0.4265 | 5882.3345 |  | 0.19421 | 2678.5516 |  | 10262.1782 |  | 18823.0642 | 19908.7786 | 0 |  |  |  | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  | 0 | [14 empty] | 0 |  | 13792 |  |  | 0 |  | 13792 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  | 0 | [14 empty] | 534-2 |  | 13792 |  |  | WG701 |  | 13792 | 12.96 |  | 12.978 | [11 empty] | 17.0184 | 18 | 0.16552 | 2282.8138 |  | 0.33931 | 4679.7683 |  | 12898.307 |  | 19860.889 | 21006.4651 | [10 empty] | 17.0184 | 18 | 1.0499 | 14480.7955 |  | 0.47833 | 6597.1733 |  | 25270.8485 |  | 46348.8173 | 49022.2171 | 0 |  |  |  | Lobby |  |  | Lobby534-2 | LobbyWG701
Standalone Retail | [13 empty] | Standalone_Retail_Interior Lighting LPD |  | Standalone Retail |  |  | 3613 |  | Standalone Retail |  |  | 3613 |  | 886.3411 | 216.207 | 873.9625 | 203.1931
Storage | Storage |  |  | X | [11 empty] | Storage | 0.46 |  | 3613 | 4088 | Storage | 0.38 |  | 3613 | 4088 | 49.4863 |  | 41.9849 | [45 empty] | -8548.74 |  |  | SoRtl | Storage |  |  | Storage | Storage
Storage738 | StorageLB702 |  |  | X | [11 empty] | replacement costs are for lamps |  | 738 |  | 4088 |  |  | LB702 |  | 4088 | 49.4863 | 82.6087 | 41.9849 | 97.3684 | 3.0309 | 12390.3837 |  | 0.70055 | 2863.8473 |  | 8727.2629 |  |  | 23981.494 | 13.8389 | 14 | 0.0046 | 18.8048 |  | 0.0074447 | 30.4341 |  | 86.3734 |  | 135.6123 | 137.1908 | 1.76 | 7194.9463 |  | 0.59436 | 2429.7271 |  | 5808.0805 |  |  | 15432.7539 | 13.8389 | 14 | 0.0038 | 15.5344 |  | 0.0063162 | 25.8207 |  | 73.0161 |  | 114.3712 | 115.7025 | -8548.74 | -21.4883 |  | SoRtl | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage738 | StorageLB702 |  |  | X | [11 empty] | ballast replacement |  | 738 |  | 4088 |  |  | LB702 |  | 4088 | 47.61 |  | 35.226 | [11 empty] | 13.8389 | 14 | 2.2697 | 9278.6842 |  | 0.70055 | 2863.8473 |  | 12853.3953 |  | 24995.9268 | 25286.8794 | [10 empty] | 13.8389 | 14 | 1.3172 | 5384.5589 |  | 0.59436 | 2429.7271 |  | 9339.4973 |  | 17153.7833 | 17353.4533 | 0 | -7933.426 |  | SoRtl | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  | X | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Storage |  |  | Storage0 | Storage0
Retail - Sales Area | Retail - Sales Area |  |  | X | [11 empty] | Retail - Sales Area | 1.22 |  | 3613 | 20467 | Retail - Sales Area | 1.05 |  | 3613 | 20467 | 833.264 |  | 828.598 | [45 empty] | -21363.2943 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area | Retail - Sales Area
Retail - Sales Area700 | Retail - Sales AreaTR701 |  |  | X | [11 empty] | replacement costs are for lamps |  | 700 |  | 20467 |  |  | TR701 |  | 20467 | 415.0253 | 49.3151 | 402.9439 | 50.7937 | 2.8056 | 57422.8974 |  | 1.8818 | 38515.7984 |  | 64818.4394 |  |  | 160757.1352 | 13.8389 | 14 | 0.0073 | 149.4091 |  | 0.012471 | 255.2405 |  | 719.1612 |  | 1123.8108 | 1136.892 | 2.7232 | 55735.2227 |  | 1.2108 | 24781.0598 |  | 50745.6051 |  |  | 131261.8877 | 13.8389 | 14 | 0.0063 | 128.9421 |  | 0.012108 | 247.8106 |  | 688.0835 |  | 1064.8362 | 1077.2309 | -29495.2475 | 394.2728 |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area700 | Retail - Sales AreaTR701
Retail - Sales Area741 | Retail - Sales AreaDL703 |  |  | X | [13 empty] | 741 |  | 20467 |  |  | DL703 |  | 20467 | 204.67 | 100 | 186.8725 | 109.5239 | 1.6519 | 33808.7824 |  | 0.615 | 12587.205 |  | 28421.5815 |  |  | 74817.5688 | 13.8389 | 14 | 0.0024 | 49.1208 |  | 0.00615 | 125.8721 |  | 339.1985 |  | 514.1913 | 520.1765 | 2.1026 | 43033.0804 |  | 0.56152 | 11492.6654 |  | 31803.5489 |  |  | 86329.2947 | 13.8389 | 14 | 0.0021 | 42.9807 |  | 0.0056152 | 114.9267 |  | 308.5269 |  | 466.4343 | 471.8636 | 11511.7259 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area741 | Retail - Sales AreaDL703
Retail - Sales Area0 | Retail - Sales Area0 |  |  | X | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area0 | Retail - Sales Area0
Retail - Sales Area537-1_LED | Retail - Sales AreaWG701 |  |  | X | [13 empty] | 537-1_LED |  | 20467 |  |  | WG701 |  | 20467 | 213.5687 | 95.8333 | 238.7815 | 85.7143 | 1.8806 | 38489.3503 |  | 0.96838 | 19819.9224 |  | 37656.9727 |  |  | 95966.2454 | 13.8389 | 14 | 0.0024 | 49.1208 |  | 6.4174e-07 | 0.013134 |  | 30.9449 |  | 80.0788 | 81.0109 | 2.102 | 43021.2929 |  | 0.7175 | 14685.0725 |  | 34880.1074 |  |  | 92586.4728 | 13.8389 | 14 | 0.0021 | 42.9807 |  | 0.007175 | 146.8507 |  | 386.7154 |  | 576.5468 | 583.2578 | -3379.7726 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area537-1_LED | Retail - Sales AreaWG701
Retail - Sales Area700 | Retail - Sales AreaTR701 |  |  | X | [11 empty] | ballast replacement |  | 700 |  | 20467 |  |  | TR701 |  | 20467 | 67.671 |  | 65.205 | [11 empty] | 13.8389 | 14 | 2.0987 | 42955.1162 |  | 1.8818 | 38515.7984 |  | 121365.3917 |  | 202836.3063 | 205197.3209 | [10 empty] | 13.8389 | 14 | 2.0377 | 41704.7105 |  | 1.2108 | 24781.0598 |  | 86939.3702 |  | 153425.1406 | 155211.0092 | 0 | -38861.8675 |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area700 | Retail - Sales AreaTR701
Retail - Sales Area741 | Retail - Sales AreaDL703 |  |  | X | [13 empty] | 741 |  | 20467 |  |  | DL703 |  | 20467 | 14.688 |  | 19.467 | [11 empty] | 13.8389 | 14 | 1.2371 | 25319.7462 |  | 0.615 | 12587.205 |  | 46762.8001 |  | 84669.7513 | 85655.3072 | [10 empty] | 13.8389 | 14 | 1.5753 | 32242.5748 |  | 0.56152 | 11492.6654 |  | 48438.7287 |  | 92173.9689 | 93246.8739 | 0 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area741 | Retail - Sales AreaDL703
Retail - Sales Area0 | Retail - Sales Area0 |  |  | X | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area0 | Retail - Sales Area0
Retail - Sales Area537-1_LED | Retail - Sales AreaWG701 |  |  | X | [13 empty] | 537-1_LED |  | 20467 |  |  | WG701 |  | 20467 | 22.248 |  | 19.467 | [11 empty] | 13.8389 | 14 | 0.93908 | 19220.1148 |  | 0.96838 | 19819.9224 |  | 60638.5488 |  | 99678.586 | 100838.8447 | [10 empty] | 13.8389 | 14 | 1.5749 | 32233.7341 |  | 0.7175 | 14685.0725 |  | 56252.0073 |  | 103170.8139 | 104371.7222 | 0 |  |  | SoRtl | Retail - Sales Area |  |  | Retail - Sales Area537-1_LED | Retail - Sales AreaWG701
Lobby | Lobby |  |  | X | [11 empty] | Lobby | 1 |  | 3613 | 129 | Lobby | 0.84 |  | 3613 | 129 | 3.5909 |  | 3.3796 | [45 empty] | -295.0404 |  |  | SoRtl | Lobby |  |  | Lobby | Lobby
Lobby723 | LobbyIP701 |  |  | X | [11 empty] | replacement costs are for lamps |  | 723 |  | 129 |  |  | IP701 |  | 129 | 2.0191 | 63.8889 | 1.9689 | 65.5173 | 9.962 | 1285.0958 |  | 1.262 | 162.7954 |  | 775.5651 |  |  | 2223.4563 | 13.8389 | 14 | 0.0072 | 0.9288 |  | 0.0096261 | 1.2418 |  | 3.6258 |  | 5.7964 | 5.8639 | 9.7132 | 1252.9987 |  | 1.2306 | 158.7493 |  | 756.2136 |  |  | 2167.9616 | 13.8389 | 14 | 0.0058 | 0.7482 |  | 0.0093868 | 1.2109 |  | 3.4366 |  | 5.3957 | 5.4585 | -55.4947 | -16.2933 |  | SoRtl | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  |  | X | [13 empty] | 522 |  | 129 |  |  | DL701 |  | 129 | 0.86 | 150 | 0.40737 | 316.6667 | 1.0345 | 133.4548 |  | 0.41 | 52.89 |  | 115.2831 |  |  | 301.6279 | 13.8389 | 14 | 0.0012 | 0.1548 |  | 0.0041 | 0.5289 |  | 1.3928 |  | 2.0765 | 2.1007 | 0.56987 | 73.5134 |  | 0.19421 | 25.0532 |  | 59.5632 |  |  | 158.1297 | 13.8389 | 14 | 0.0012 | 0.1548 |  | 0.0019421 | 0.25053 |  | 0.71102 |  | 1.1164 | 1.1293 | -143.4982 |  |  | SoRtl | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  |  | X | [13 empty] | 0 |  | 129 |  |  | 0 |  | 129 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  |  | X | [13 empty] | 534-2 |  | 129 |  |  | WG701 |  | 129 | 0.71172 | 181.25 | 1.0033 | 128.5715 | 2.115 | 272.8394 |  | 0.31929 | 41.1885 |  | 171.0574 |  |  | 485.0854 | 9.964 | 10 | 0.018483 | 2.3843 |  | 0.030161 | 3.8908 |  | 11.0298 |  | 17.3049 | 17.3674 | 1.4013 | 180.7706 |  | 0.47833 | 61.705 |  | 146.5622 |  |  | 389.0378 | 13.8389 | 14 | 0.0014 | 0.1806 |  | 0.0047833 | 0.61705 |  | 1.6249 |  | 2.4226 | 2.4508 | -96.0476 |  |  | SoRtl | Lobby |  |  | Lobby534-2 | LobbyWG701
Lobby723 | LobbyIP701 |  |  | X | [11 empty] | ballast replacement |  | 723 |  | 129 |  |  | IP701 |  | 129 | 45.36 |  | 44.37 | [11 empty] | 13.8389 | 14 | 7.4661 | 963.1252 |  | 1.262 | 162.7954 |  | 1004.8324 |  | 2130.7531 | 2155.555 | [10 empty] | 13.8389 | 14 | 7.2805 | 939.1879 |  | 1.2306 | 158.7493 |  | 979.8585 |  | 2077.7958 | 2101.9813 | 0 | 375.1643 |  | SoRtl | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  |  | X | [13 empty] | 522 |  | 129 |  |  | DL701 |  | 129 | 5.67 |  | 6.48 | [11 empty] | 0 | 0 | 0.775 | 99.975 |  | 0.41 | 52.89 |  | 192.4544 |  | 345.3194 | 0 | [10 empty] | 13.8389 | 14 | 0.4265 | 55.0189 |  | 0.19421 | 25.0532 |  | 95.9847 |  | 176.0568 | 178.1061 | 0 |  |  | SoRtl | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  |  | X | [13 empty] | 0 |  | 129 |  |  | 0 |  | 129 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SoRtl | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  |  | X | [13 empty] | 534-2 |  | 129 |  |  | WG701 |  | 129 | 12.96 |  | 12.978 | [11 empty] | 13.8389 | 14 | 0.16552 | 21.3517 |  | 0.33931 | 43.771 |  | 120.6411 |  | 185.7638 | 187.9261 | [10 empty] | 13.8389 | 14 | 1.0499 | 135.4425 |  | 0.47833 | 61.705 |  | 236.3645 |  | 433.512 | 438.5581 | 0 |  |  | SoRtl | Lobby |  |  | Lobby534-2 | LobbyWG701
Primary School | [13 empty] | Primary_School_Interior Lighting LPD |  | Primary School |  |  | 3774 |  | Primary School |  |  | 3774 |  | 2068.2367 | 593.6292 | 1911.6951 | 629.133
Restrooms | Restrooms |  |  |  | X | [10 empty] | Restrooms | 0.85 |  | 3774 | 2044 | Restrooms | 0.63 |  | 3774 | 2044 | 64.3956 |  | 65.7032 | [45 empty] | -9176.0891 |  |  | PriSch | Restrooms |  |  | Restrooms | Restrooms
Restrooms604 | RestroomsDL709 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 604 |  | 2044 |  |  | DL709 |  | 2044 | 24.669 | 82.8571 | 36.1788 | 56.4972 | 4.2525 | 8692.11 |  | 0.3637 | 743.3993 |  | 4900.3864 |  |  | 14335.8957 | 9.539 | 10 | 0.040431 | 82.641 |  | 0.065978 | 134.8587 |  | 382.3035 |  | 599.8033 | 628.7937 | 3.5159 | 7186.5062 |  | 1.0885 | 2224.9962 |  | 5606.3539 |  |  | 15017.8563 | 13.2485 | 14 | 0.003717 | 7.5975 |  | 0.010885 | 22.25 |  | 59.2759 |  | 89.1234 | 94.1785 | 681.9606 | -1046.9411 |  | PriSch | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  |  |  | X | [12 empty] | 720 |  | 2044 |  |  | 0 |  | 2044 | 18.5818 | 110 | 0 | 0 | 1.5353 | 3138.2275 |  | 0.55909 | 1142.7818 |  | 2613.4572 |  |  | 6894.4666 | 13.2485 | 14 | 0.002 | 4.088 |  | 0.0055909 | 11.4278 |  | 30.5617 |  | 46.0775 | 48.691 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -6894.4666 |  |  | PriSch | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  |  |  | X | [12 empty] | 0 |  | 2044 |  |  | 0 |  | 2044 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  |  |  | X | [12 empty] | 534-2 |  | 2044 |  |  | WG701 |  | 2044 | 21.1448 | 96.6667 | 29.5244 | 69.2308 | 3.9657 | 8105.8697 |  | 0.59867 | 1223.6829 |  | 5081.9956 |  |  | 14411.5482 | 9.539 | 10 | 0.034655 | 70.8352 |  | 0.056552 | 115.5932 |  | 327.6887 |  | 514.1171 | 538.9661 | 2.6025 | 5319.4192 |  | 0.88833 | 1815.7533 |  | 4312.7926 |  |  | 11447.965 | 13.2485 | 14 | 0.0026 | 5.3144 |  | 0.0088833 | 18.1575 |  | 47.8159 |  | 71.2878 | 75.3313 | -2963.5831 |  |  | PriSch | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Restrooms604 | RestroomsDL709 |  |  |  | X | [10 empty] | ballast replacement |  | 604 |  | 2044 |  |  | DL709 |  | 2044 | 24.2393 |  | 28.7696 | [11 empty] | 13.2485 | 14 | 0.36207 | 740.069 |  | 0.74224 | 1517.1414 |  | 4181.5223 |  | 6438.7326 | 6803.9375 | [10 empty] | 13.2485 | 14 | 2.6341 | 5384.1815 |  | 1.0885 | 2224.9962 |  | 8837.8329 |  | 16447.0106 | 17379.885 | 0 | 10011.8652 |  | PriSch | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  |  |  | X | [12 empty] | 720 |  | 2044 |  |  | 0 |  | 2044 | 12.6 |  | 1e-05 | [11 empty] | 13.2485 | 14 | 1.15 | 2350.6046 |  | 0.55909 | 1142.7818 |  | 4278.1833 |  | 7771.5698 | 8212.3732 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  |  |  | X | [12 empty] | 0 |  | 2044 |  |  | 0 |  | 2044 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  |  |  | X | [12 empty] | 534-2 |  | 2044 |  |  | WG701 |  | 2044 | 24.3 |  | 24.102 | [11 empty] | 13.2485 | 14 | 0.31034 | 634.3448 |  | 0.63621 | 1300.4069 |  | 3584.1619 |  | 5518.9137 | 5831.9464 | [10 empty] | 13.2485 | 14 | 1.9499 | 3985.5786 |  | 0.88833 | 1815.7533 |  | 6955.3466 |  | 12756.6785 | 13480.2373 | 0 |  |  | PriSch | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Dining Area | Dining Area |  |  |  | X | [10 empty] | Dining Area | 0.63 |  | 3774 | 3389 | Dining Area | 0.43 |  | 3774 | 3389 | 81.336 |  | 77.4941 | [45 empty] | 6673.4059 |  |  | PriSch | Dining Area |  |  | Dining Area | Dining Area
Dining Area731 | Dining AreaTR704 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 731 |  | 3389 |  |  | TR704 |  | 3389 | 13.556 | 250 | 19.0631 | 177.7778 | 1.5296 | 5183.8144 |  | 0.32251 | 1092.9728 |  | 3549.7036 |  |  | 9826.4909 | 13.2485 | 14 | 0.0016 | 5.4224 |  | 0.00246 | 8.3369 |  | 23.8313 |  | 37.5906 | 39.7227 | 0.77805 | 2636.8115 |  | 0.34594 | 1172.3822 |  | 2400.7546 |  |  | 6209.9482 | 13.2485 | 14 | 0.0018 | 6.1002 |  | 0.0034594 | 11.7238 |  | 32.553 |  | 50.377 | 53.2344 | -3616.5426 | -791.2244 |  | PriSch | Dining Area |  |  | Dining Area731 | Dining AreaTR704
Dining Area522 | Dining AreaDL707 |  |  |  | X | [12 empty] | 522 |  | 3389 |  |  | DL707 |  | 3389 | 33.89 | 100 | 50.8349 | 66.6667 | 1.5518 | 5259.0502 |  | 0.615 | 2084.235 |  | 4542.9588 |  |  | 11886.244 | 13.2485 | 14 | 0.0018 | 6.1002 |  | 0.00615 | 20.8423 |  | 54.8861 |  | 81.8286 | 86.4699 | 3.0613 | 10374.8592 |  | 0.9225 | 3126.3525 |  | 8010.8381 |  |  | 21512.0498 | 13.2485 | 14 | 0.0012 | 4.0668 |  | 0.009225 | 31.2635 |  | 79.1299 |  | 114.4603 | 120.9524 | 9625.8058 |  |  | PriSch | Dining Area |  |  | Dining Area522 | Dining AreaDL707
Dining Area0 | Dining Area0 |  |  |  | X | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Dining Area |  |  | Dining Area0 | Dining Area0
Dining Area537-1 | Dining AreaWW714 |  |  |  | X | [12 empty] | 537-1 |  | 3389 |  |  | WW714 |  | 3389 | 33.89 | 100 | 7.596 | 446.1539 | 1.0692 | 3623.5188 |  | 0.615 | 2084.235 |  | 3755.9411 |  |  | 9463.6949 | 9.539 | 10 | 0.0335 | 113.5315 |  | 0.054667 | 185.2676 |  | 525.2051 |  | 824.0042 | 863.8311 | 1.7249 | 5845.7562 |  | 0.22055 | 747.4498 |  | 3534.6317 |  |  | 10127.8377 | 13.2485 | 14 | 0.0013 | 4.4057 |  | 0.0013784 | 4.6716 |  | 14.2142 |  | 23.2914 | 24.6125 | 664.1428 |  |  | PriSch | Dining Area |  |  | Dining Area537-1 | Dining AreaWW714
Dining Area731 | Dining AreaTR704 |  |  |  | X | [10 empty] | ballast replacement |  | 731 |  | 3389 |  |  | TR704 |  | 3389 | 12.672 |  | 17.982 | [11 empty] | 13.2485 | 14 | 1.146 | 3883.794 |  | 0.32251 | 1092.9728 |  | 5121.0579 |  | 10097.8247 | 10670.5733 | [10 empty] | 13.2485 | 14 | 0.58219 | 1973.0334 |  | 0.34594 | 1172.3822 |  | 4113.0674 |  | 7258.483 | 7670.1842 | 0 | 22706.5669 |  | PriSch | Dining Area |  |  | Dining Area731 | Dining AreaTR704
Dining Area522 | Dining AreaDL707 |  |  |  | X | [12 empty] | 522 |  | 3389 |  |  | DL707 |  | 3389 | 8.505 |  | 9.612 | [11 empty] | 0 | 0 | 1.1625 | 3939.7125 |  | 0.615 | 2084.235 |  | 7584.0474 |  | 13607.9949 | 0 | [10 empty] | 13.2485 | 14 | 2.2951 | 7778.0943 |  | 0.9225 | 3126.3525 |  | 12551.9716 |  | 23456.4184 | 24786.8665 | 0 |  |  | PriSch | Dining Area |  |  | Dining Area522 | Dining AreaDL707
Dining Area0 | Dining Area0 |  |  |  | X | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Dining Area |  |  | Dining Area0 | Dining Area0
Dining Area537-1 | Dining AreaWW714 |  |  |  | X | [12 empty] | 537-1 |  | 3389 |  |  | WW714 |  | 3389 | 20.084 |  | 10.647 | [11 empty] | 13.2485 | 14 | 0.3 | 1016.7 |  | 0.615 | 2084.235 |  | 5744.5372 |  | 8845.4722 | 9347.1874 | [10 empty] | 13.2485 | 14 | 1.2927 | 4381.0129 |  | 0.22055 | 747.4498 |  | 4587.7128 |  | 9716.1754 | 10267.2769 | 0 |  |  | PriSch | Dining Area |  |  | Dining Area537-1 | Dining AreaWW714
Classroom/Lecture/Training | Classroom/Lecture/Training |  |  |  | X | [10 empty] | Classroom/Lecture/Training | 0.92 |  | 3774 | 37187 | Classroom/Lecture/Training | 0.71 |  | 3774 | 37187 | 944.2399 |  | 969.346 | [45 empty] | -83553.0574 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training | Classroom/Lecture/Training
Classroom/Lecture/Training600_LED | Classroom/Lecture/TrainingTR701 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 600_LED |  | 37187 |  |  | TR701 |  | 37187 | 655.4209 | 56.7376 | 639.1514 | 58.1818 | 3.0385 | 112994.5589 |  | 1.6357 | 60825.3512 |  | 113099.1284 |  |  | 286919.0384 | 13.2485 | 14 | 0.00705 | 262.1683 |  | 0.010839 | 403.0838 |  | 1152.2206 |  | 1817.4727 | 1920.5598 | 2.3774 | 88407.4441 |  | 1.057 | 39307.8211 |  | 80492.8917 |  |  | 208208.1569 | 13.2485 | 14 | 0.0055 | 204.5285 |  | 0.01057 | 393.0782 |  | 1091.4409 |  | 1689.0476 | 1784.8504 | -78710.8815 | -71.7741 |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training600_LED | Classroom/Lecture/TrainingTR701
Classroom/Lecture/Training701 | Classroom/Lecture/TrainingDL706 |  |  |  | X | [12 empty] | 701 |  | 37187 |  |  | DL706 |  | 37187 | 216.9242 | 171.4286 | 278.9023 | 133.3334 | 0.96289 | 35806.978 |  | 0.35875 | 13340.8363 |  | 30110.7351 |  |  | 79258.5494 | 13.2485 | 14 | 0.0007 | 26.0309 |  | 0.0035875 | 133.4084 |  | 343.1255 |  | 502.5647 | 531.0702 | 1.238 | 46037.5432 |  | 0.46125 | 17152.5037 |  | 38713.8023 |  |  | 101903.8493 | 13.2485 | 14 | 0.0009 | 33.4683 |  | 0.0046125 | 171.525 |  | 441.1613 |  | 646.1547 | 682.8046 | 22645.2998 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training701 | Classroom/Lecture/TrainingDL706
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 |  |  |  | X | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training0 | Classroom/Lecture/Training0
Classroom/Lecture/Training703 | Classroom/Lecture/TrainingWW714 |  |  |  | X | [12 empty] | 703 |  | 37187 |  |  | WW714 |  | 37187 | 71.8949 | 517.2414 | 51.2924 | 725.0001 | 1.4882 | 55341.0736 |  | 0.19024 | 7074.4549 |  | 33460.4259 |  |  | 95875.9544 | 13.2485 | 14 | 0.00145 | 53.9211 |  | 0.001189 | 44.2153 |  | 142.2259 |  | 240.3624 | 253.9957 | 1.0615 | 39473.6158 |  | 0.13572 | 5047.1735 |  | 23867.6894 |  |  | 68388.4787 | 13.2485 | 14 | 0.0008 | 29.7496 |  | 0.00084828 | 31.5448 |  | 95.9816 |  | 157.276 | 166.1967 | -27487.4757 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training703 | Classroom/Lecture/TrainingWW714
Classroom/Lecture/Training600_LED | Classroom/Lecture/TrainingTR701 |  |  |  | X | [10 empty] | ballast replacement |  | 600_LED |  | 37187 |  |  | TR701 |  | 37187 | 63.45 |  | 56.925 | [11 empty] | 13.2485 | 14 | 2.2736 | 84549.2929 |  | 1.6357 | 60825.3512 |  | 202181.9868 |  | 347556.6308 | 367270.0429 | [10 empty] | 13.2485 | 14 | 1.7789 | 66152.1867 |  | 1.057 | 39307.8211 |  | 137903.5938 |  | 243363.6017 | 257167.1851 | 0 | -110856.3768 |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training600_LED | Classroom/Lecture/TrainingTR701
Classroom/Lecture/Training701 | Classroom/Lecture/TrainingDL706 |  |  |  | X | [12 empty] | 701 |  | 37187 |  |  | DL706 |  | 37187 | 4.284 |  | 5.508 | [11 empty] | 13.2485 | 14 | 0.72164 | 26835.7104 |  | 0.35875 | 13340.8363 |  | 49562.62 |  | 89739.1666 | 94829.1722 | [10 empty] | 13.2485 | 14 | 0.92783 | 34503.0562 |  | 0.46125 | 17152.5037 |  | 63723.3686 |  | 115378.9285 | 121923.2214 | 0 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training701 | Classroom/Lecture/TrainingDL706
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 |  |  |  | X | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training0 | Classroom/Lecture/Training0
Classroom/Lecture/Training703 | Classroom/Lecture/TrainingWW714 |  |  |  | X | [12 empty] | 703 |  | 37187 |  |  | WW714 |  | 37187 | 9.135 |  | 6.552 | [11 empty] | 13.2485 | 14 | 1.1151 | 41465.3644 |  | 0.19024 | 7074.4549 |  | 43421.7352 |  | 91961.5544 | 97177.6137 | [10 empty] | 13.2485 | 14 | 0.79552 | 29582.8997 |  | 0.13572 | 5047.1735 |  | 30978.6458 |  | 65608.7189 | 69330.0455 | 0 |  |  | PriSch | Classroom/Lecture/Training |  |  | Classroom/Lecture/Training703 | Classroom/Lecture/TrainingWW714
Corridor/Transition | Corridor/Transition |  |  |  | X | [10 empty] | Corridor/Transition | 0.66 |  | 3774 | 12073 | Corridor/Transition | 0.41 |  | 3774 | 12073 | 427.3842 |  | 280.1845 | [45 empty] | -59941.3996 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 701 |  | 12073 |  |  | DL706 |  | 12073 | 382.3117 | 31.5789 | 241.4598 | 50 | 5.2271 | 63106.9634 |  | 1.9475 | 23512.1675 |  | 53067.7864 |  |  | 139686.9173 | 13.2485 | 14 | 0.0038 | 45.8774 |  | 0.019475 | 235.1217 |  | 604.7315 |  | 885.7306 | 935.9692 | 3.3013 | 39857.0295 |  | 1.23 | 14849.79 |  | 33516.4967 |  |  | 88223.3162 | 13.2485 | 14 | 0.0024 | 28.9752 |  | 0.0123 | 148.4979 |  | 381.9357 |  | 559.4088 | 591.1384 | -51463.6011 | -381.925 |  | PriSch | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  |  |  | X | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  |  |  | X | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  |  |  | X | [12 empty] | 703 |  | 12073 |  |  | WW708 |  | 12073 | 45.0725 | 267.8571 | 38.7247 | 311.7648 | 2.8737 | 34694.5825 |  | 0.36736 | 4435.1373 |  | 20977.1049 |  |  | 60106.8248 | 13.2485 | 14 | 0.0028 | 33.8044 |  | 0.002296 | 27.7196 |  | 89.1646 |  | 150.6886 | 159.2357 | 2.4683 | 29799.8315 |  | 0.31562 | 3810.5122 |  | 18018.6827 |  |  | 51629.0263 | 13.2485 | 14 | 0.0017 | 20.5241 |  | 0.0019726 | 23.8157 |  | 71.2456 |  | 115.5854 | 122.1414 | -8477.7985 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 |  |  |  | X | [10 empty] | ballast replacement |  | 701 |  | 12073 |  |  | DL706 |  | 12073 | 23.256 |  | 14.688 | [11 empty] | 13.2485 | 14 | 3.9175 | 47295.8145 |  | 1.9475 | 23512.1675 |  | 87350.1932 |  | 158158.1752 | 167128.9069 | [10 empty] | 13.2485 | 14 | 2.4742 | 29871.0407 |  | 1.23 | 14849.79 |  | 55168.5431 |  | 99889.3738 | 105555.0991 | 0 | -70153.9148 |  | PriSch | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  |  |  | X | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  |  |  | X | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  |  |  | X | [12 empty] | 703 |  | 12073 |  |  | WW708 |  | 12073 | 17.64 |  | 15.147 | [11 empty] | 13.2485 | 14 | 2.1532 | 25995.5836 |  | 0.36736 | 4435.1373 |  | 27222.0771 |  | 57652.798 | 60922.8647 | [10 empty] | 13.2485 | 14 | 1.85 | 22334.4805 |  | 0.31562 | 3810.5122 |  | 23388.2401 |  | 49533.2328 | 52342.7577 | 0 |  |  | PriSch | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area |  |  |  | X | [10 empty] | Gymnasium/Fitness-Fitness Area | 0.5 |  | 3774 | 3841 | Gymnasium/Fitness-Fitness Area | 0.7 |  | 3774 | 3841 | 50.5395 |  | 81.4757 | [45 empty] | 35583.0803 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area
Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 735 |  | 3841 |  |  | ID701 |  | 3841 | 50.5395 | 76 | 81.4757 | 47.1429 | 8.8116 | 33845.2747 |  | 1.0609 | 4074.8209 |  | 20220.5369 |  |  | 58140.6325 | 13.2485 | 14 | 0.005 | 19.205 |  | 0.0080921 | 31.0818 |  | 88.2116 |  | 138.4983 | 146.354 | 14.2043 | 54558.6115 |  | 1.7103 | 6569.1052 |  | 32595.9961 |  |  | 93723.7128 | 13.2485 | 14 | 0.007 | 26.887 |  | 0.013045 | 50.1076 |  | 139.644 |  | 216.6386 | 228.9264 | 35583.0803 | 82.5724 |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701 |  |  |  | X | [10 empty] | ballast replacement |  | 735 |  | 3841 |  |  | ID701 |  | 3841 | 45 |  | 69.3 | [11 empty] | 13.2485 | 14 | 6.6049 | 25369.5523 |  | 1.0609 | 4074.8209 |  | 25945.6163 |  | 55389.9895 | 58531.7097 | [10 empty] | 13.2485 | 14 | 10.648 | 40898.7934 |  | 1.7103 | 6569.1052 |  | 41827.4784 |  | 89295.377 | 94360.2108 | 0 | 35828.5011 |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  | X | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Food Preparation | Food Preparation |  |  |  | 0 | [10 empty] | Food Preparation | 1.06 |  | 3774 | 1808 | Food Preparation | 1.09 |  | 3774 | 1808 | 47.8582 |  | 60.7133 | [45 empty] | -12612.6745 |  |  |  | Food Preparation |  |  | Food Preparation | Food Preparation
Food Preparation731 | Food PreparationTR704 |  |  |  | 0 | [10 empty] | replacement costs are for lamps |  | 731 |  | 1808 |  |  | TR704 |  | 1808 | 40.68 | 44.4444 | 51.415 | 35.1648 | 8.604 | 15556.032 |  | 1.8141 | 3279.886 |  | 10652.2532 |  |  | 29488.1712 | 13.2485 | 14 | 0.009 | 16.272 |  | 0.013838 | 25.0182 |  | 71.5149 |  | 112.8051 | 119.2034 | 3.9335 | 7111.7228 |  | 1.7489 | 3162.0225 |  | 6475.0558 |  |  | 16748.8011 | 13.2485 | 14 | 0.0091 | 16.4528 |  | 0.017489 | 31.6202 |  | 87.7983 |  | 135.8713 | 143.578 | -12739.3701 | 29.7867 |  |  | Food Preparation |  |  | Food Preparation731 | Food PreparationTR704
Food Preparation730 | Food PreparationTR703 |  |  |  | 0 | [10 empty] | Not included in costs, as increase due to IES, not 90.1 |  | 730 |  | 1808 |  |  | TR703 |  | 1808 | 7.1782 | 251.875 | 9.2983 | 194.4445 | 0.7599 | 1373.9005 |  | 0.24417 | 441.4571 |  | 1087.3424 |  |  | 2902.7001 | 13.2485 | 14 | 0.0015881 | 2.8713 |  | 0.0024417 | 4.4146 |  | 12.6191 |  | 19.9049 | 21.034 | 0.71151 | 1286.4178 |  | 0.31629 | 571.8446 |  | 1171.1333 |  |  | 3029.3957 | 13.2485 | 14 | 0.0018 | 3.2544 |  | 0.0031629 | 5.7184 |  | 16.0537 |  | 25.0265 | 26.446 | 126.6957 | -11328.5621 |  |  | Food Preparation |  |  | Food Preparation730 | Food PreparationTR703
Food Preparation0 | Food Preparation0 |  |  |  | 0 | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Food Preparation |  |  | Food Preparation0 | Food Preparation0
Food Preparation0 | Food Preparation0 |  |  |  | 0 | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Food Preparation |  |  | Food Preparation0 | Food Preparation0
Food Preparation731 | Food PreparationTR704 |  |  |  | 0 | [10 empty] | ballast replacement |  | 731 |  | 1808 |  |  | TR704 |  | 1808 | 71.28 |  | 90.909 | [11 empty] | 13.2485 | 14 | 6.4463 | 11654.82 |  | 1.8141 | 3279.886 |  | 15367.7069 |  | 30302.4129 | 32021.1657 | [10 empty] | 13.2485 | 14 | 2.9433 | 5321.4525 |  | 1.7489 | 3162.0225 |  | 11093.3207 |  | 19576.7957 | 20687.1916 | 0 | -10972.1941 |  |  | Food Preparation |  |  | Food Preparation731 | Food PreparationTR704
Food Preparation730 | Food PreparationTR703 |  |  |  | 0 | [12 empty] | 730 |  | 1808 |  |  | TR703 |  | 1808 | 13.968 |  | 17.982 | [11 empty] | 13.2485 | 14 | 0.56873 | 1028.272 |  | 0.24417 | 441.4571 |  | 1728.3286 |  | 3198.0576 | 3379.4515 | [10 empty] | 13.2485 | 14 | 0.53229 | 962.3726 |  | 0.31629 | 571.8446 |  | 2006.2018 |  | 3540.4189 | 3741.2315 | 0 |  |  |  | Food Preparation |  |  | Food Preparation730 | Food PreparationTR703
Food Preparation0 | Food Preparation0 |  |  |  | 0 | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Food Preparation |  |  | Food Preparation0 | Food Preparation0
Food Preparation0 | Food Preparation0 |  |  |  | 0 | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Food Preparation |  |  | Food Preparation0 | Food Preparation0
Library | Library |  |  |  | 0 | [10 empty] | Library | 0.82 |  | 3774 | 4293 | Library | 0.96 |  | 3774 | 4293 | 118.9305 |  | 147.746 | [45 empty] | 32957.2583 |  |  |  | Library |  |  | Library | Library
Library735 | LibraryID701 |  |  |  | 0 | [10 empty] | replacement costs are for lamps |  | 735 |  | 4293 |  |  | ID701 |  | 4293 | 56.4868 | 76 | 81.3068 | 52.8 | 8.8116 | 37828.1084 |  | 1.0609 | 4554.3364 |  | 22600.0429 |  |  | 64982.4877 | 13.2485 | 14 | 0.005 | 21.465 |  | 0.0080921 | 34.7394 |  | 98.5921 |  | 154.7965 | 163.5766 | 12.6824 | 54445.4847 |  | 1.527 | 6555.4842 |  | 32528.4085 |  |  | 93529.3774 | 13.2485 | 14 | 0.00625 | 26.8313 |  | 0.011648 | 50.0037 |  | 139.3545 |  | 216.1894 | 228.4517 | 28546.8897 | 74.2012 |  |  | Library |  |  | Library735 | LibraryID701
Library720 | LibraryDL709 |  |  |  | 0 | [10 empty] | Not included in costs, as increase due to IES, not 90.1 |  | 720 |  | 4293 |  |  | DL709 |  | 4293 | 62.4436 | 68.75 | 66.4393 | 64.6154 | 2.4565 | 10545.9184 |  | 0.89455 | 3840.2836 |  | 8782.4437 |  |  | 23168.6458 | 13.2485 | 14 | 0.0032 | 13.7376 |  | 0.0089455 | 38.4028 |  | 102.7016 |  | 154.842 | 163.6246 | 3.0742 | 13197.4067 |  | 0.95179 | 4086.0161 |  | 10295.5916 |  |  | 27579.0144 | 13.2485 | 14 | 0.00325 | 13.9522 |  | 0.0095179 | 40.8602 |  | 108.8551 |  | 163.6675 | 172.9508 | 4410.3686 | 28754.2957 |  |  | Library |  |  | Library720 | LibraryDL709
Library0 | Library0 |  |  |  | 0 | [12 empty] | 0 |  | 4293 |  |  | 0 |  | 4293 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Library |  |  | Library0 | Library0
Library0 | Library0 |  |  |  | 0 | [12 empty] | 0 |  | 4293 |  |  | 0 |  | 4293 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Library |  |  | Library0 | Library0
Library735 | LibraryID701 |  |  |  | 0 | [10 empty] | ballast replacement |  | 735 |  | 4293 |  |  | ID701 |  | 4293 | 45 |  | 61.875 | [11 empty] | 13.2485 | 14 | 6.6049 | 28354.9826 |  | 1.0609 | 4554.3364 |  | 28998.8365 |  | 61908.1554 | 65419.586 | [10 empty] | 13.2485 | 14 | 9.5071 | 40813.9901 |  | 1.527 | 6555.4842 |  | 41740.7494 |  | 89110.2237 | 94164.5556 | 0 | 33064.2176 |  |  | Library |  |  | Library735 | LibraryID701
Library720 | LibraryDL709 |  |  |  | 0 | [12 empty] | 720 |  | 4293 |  |  | DL709 |  | 4293 | 20.16 |  | 25.155 | [11 empty] | 13.2485 | 14 | 1.84 | 7899.1356 |  | 0.89455 | 3840.2836 |  | 14376.7052 |  | 26116.1244 | 27597.431 | [10 empty] | 13.2485 | 14 | 2.3032 | 9887.5908 |  | 0.95179 | 4086.0161 |  | 16229.9276 |  | 30203.5345 | 31916.679 | 0 |  |  |  | Library |  |  | Library720 | LibraryDL709
Library0 | Library0 |  |  |  | 0 | [12 empty] | 0 |  | 4293 |  |  | 0 |  | 4293 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Library |  |  | Library0 | Library0
Library0 | Library0 |  |  |  | 0 | [12 empty] | 0 |  | 4293 |  |  | 0 |  | 4293 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  |  | Library |  |  | Library0 | Library0
Lobby | Lobby |  |  |  | X | [10 empty] | Lobby | 1 |  | 3774 | 1840 | Lobby | 0.84 |  | 3774 | 1840 | 51.2184 |  | 48.2058 | [45 empty] | -4208.3288 |  |  | PriSch | Lobby |  |  | Lobby | Lobby
Lobby723 | LobbyIP701 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 723 |  | 1840 |  |  | IP701 |  | 1840 | 28.8 | 63.8889 | 28.0842 | 65.5173 | 9.962 | 18330.048 |  | 1.262 | 2322.0432 |  | 11062.3239 |  |  | 31714.4151 | 13.2485 | 14 | 0.0072 | 13.248 |  | 0.0096261 | 17.712 |  | 51.7175 |  | 82.6775 | 87.3669 | 9.7132 | 17872.2299 |  | 1.2306 | 2264.3316 |  | 10786.302 |  |  | 30922.8635 | 13.2485 | 14 | 0.0058 | 10.672 |  | 0.0093868 | 17.2718 |  | 49.0182 |  | 76.962 | 81.3272 | -791.5516 | -242.757 |  | PriSch | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  |  |  | X | [12 empty] | 522 |  | 1840 |  |  | DL701 |  | 1840 | 12.2667 | 150 | 5.8105 | 316.6667 | 1.0345 | 1903.5413 |  | 0.41 | 754.4 |  | 1644.3482 |  |  | 4302.2896 | 13.2485 | 14 | 0.0012 | 2.208 |  | 0.0041 | 7.544 |  | 19.8663 |  | 29.6183 | 31.2983 | 0.56987 | 1048.5629 |  | 0.19421 | 357.3474 |  | 849.5831 |  |  | 2255.4934 | 13.2485 | 14 | 0.0012 | 2.208 |  | 0.0019421 | 3.5735 |  | 10.1417 |  | 15.9232 | 16.8263 | -2046.7962 |  |  | PriSch | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  |  |  | X | [12 empty] | 0 |  | 1840 |  |  | 0 |  | 1840 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  |  |  | X | [12 empty] | 534-2 |  | 1840 |  |  | WG701 |  | 1840 | 10.1517 | 181.25 | 14.3111 | 128.5715 | 2.115 | 3891.6634 |  | 0.31929 | 587.4955 |  | 2439.8883 |  |  | 6919.0473 | 9.539 | 10 | 0.018483 | 34.0083 |  | 0.030161 | 55.4968 |  | 157.3248 |  | 246.8299 | 258.76 | 1.4013 | 2578.4329 |  | 0.47833 | 880.1333 |  | 2090.5001 |  |  | 5549.0663 | 13.2485 | 14 | 0.0014 | 2.576 |  | 0.0047833 | 8.8013 |  | 23.1774 |  | 34.5547 | 36.5146 | -1369.981 |  |  | PriSch | Lobby |  |  | Lobby534-2 | LobbyWG701
Lobby723 | LobbyIP701 |  |  |  | X | [10 empty] | ballast replacement |  | 723 |  | 1840 |  |  | IP701 |  | 1840 | 45.36 |  | 44.37 | [11 empty] | 13.2485 | 14 | 7.4661 | 13737.6 |  | 1.262 | 2322.0432 |  | 14332.4937 |  | 30392.1369 | 32115.9789 | [10 empty] | 13.2485 | 14 | 7.2805 | 13396.1684 |  | 1.2306 | 2264.3316 |  | 13976.2768 |  | 29636.7768 | 31317.7748 | 0 | 5589.6365 |  | PriSch | Lobby |  |  | Lobby723 | LobbyIP701
Lobby522 | LobbyDL701 |  |  |  | X | [12 empty] | 522 |  | 1840 |  |  | DL701 |  | 1840 | 5.67 |  | 6.48 | [11 empty] | 0 | 0 | 0.775 | 1426 |  | 0.41 | 754.4 |  | 2745.0865 |  | 4925.4865 | 0 | [10 empty] | 13.2485 | 14 | 0.4265 | 784.7662 |  | 0.19421 | 357.3474 |  | 1369.0841 |  | 2511.1977 | 2653.6328 | 0 |  |  | PriSch | Lobby |  |  | Lobby522 | LobbyDL701
Lobby0 | Lobby0 |  |  |  | X | [12 empty] | 0 |  | 1840 |  |  | 0 |  | 1840 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Lobby |  |  | Lobby0 | Lobby0
Lobby534-2 | LobbyWG701 |  |  |  | X | [12 empty] | 534-2 |  | 1840 |  |  | WG701 |  | 1840 | 12.96 |  | 12.978 | [11 empty] | 13.2485 | 14 | 0.16552 | 304.5517 |  | 0.33931 | 624.331 |  | 1720.7718 |  | 2649.6546 | 2799.943 | [10 empty] | 13.2485 | 14 | 1.0499 | 1931.8927 |  | 0.47833 | 880.1333 |  | 3371.4009 |  | 6183.4269 | 6534.1509 | 0 |  |  | PriSch | Lobby |  |  | Lobby534-2 | LobbyWG701
Electrical/Mechanical | Electrical/Mechanical |  |  |  | X | [10 empty] | Electrical/Mechanical | 0.43 |  | 3774 | 2712 | Electrical/Mechanical | 0.43 |  | 3774 | 2712 | 70.6547 |  | 71.0983 | [45 empty] | -1757.937 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical | Electrical/Mechanical
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 738 |  | 2712 |  |  | LB702 |  | 2712 | 16.4147 | 165.2174 | 16.8584 | 160.8696 | 1.5155 | 4109.9218 |  | 0.35027 | 949.9454 |  | 2894.8553 |  |  | 7954.7226 | 13.2485 | 14 | 0.0023 | 6.2376 |  | 0.0037224 | 10.0951 |  | 28.6503 |  | 44.9829 | 47.5344 | 1.0653 | 2889.0203 |  | 0.35974 | 975.6196 |  | 2332.1456 |  |  | 6196.7856 | 13.2485 | 14 | 0.0023 | 6.2376 |  | 0.003823 | 10.3679 |  | 29.3185 |  | 45.924 | 48.5288 | -1757.937 | 0.99446 |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  |  |  | X | [12 empty] | 739 |  | 2712 |  |  | TL702 |  | 2712 | 54.24 | 50 | 54.2399 | 50.0001 | 2.562 | 6948.144 |  | 0.6027 | 1634.5224 |  | 4921.5587 |  |  | 13504.2251 | 13.2485 | 14 | 0.002 | 5.424 |  | 0.0123 | 33.3576 |  | 85.1129 |  | 123.8945 | 130.9217 | 2.562 | 6948.144 |  | 0.6027 | 1634.5224 |  | 4921.5587 |  |  | 13504.2251 | 13.2485 | 14 | 0.002 | 5.424 |  | 0.0123 | 33.3576 |  | 85.1129 |  | 123.8945 | 130.9217 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  | X | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  | X | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  |  |  | X | [10 empty] | ballast replacement |  | 738 |  | 2712 |  |  | LB702 |  | 2712 | 23.805 |  | 21.321 | [11 empty] | 13.2485 | 14 | 1.1349 | 3077.7632 |  | 0.35027 | 949.9454 |  | 4263.5039 |  | 8291.2125 | 8761.4901 | [10 empty] | 13.2485 | 14 | 0.79723 | 2162.087 |  | 0.35974 | 975.6196 |  | 3750.1319 |  | 6887.8385 | 7278.5167 | 0 | -1482.9734 |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  |  |  | X | [12 empty] | 739 |  | 2712 |  |  | TL702 |  | 2712 | 12.24 |  | 12.24 | [11 empty] | 13.2485 | 14 | 1.92 | 5207.04 |  | 0.6027 | 1634.5224 |  | 7280.166 |  | 14121.7284 | 14922.7129 | [10 empty] | 13.2485 | 14 | 1.92 | 5207.04 |  | 0.6027 | 1634.5224 |  | 7280.166 |  | 14121.7284 | 14922.7129 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  | X | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  | X | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Office-Enclosed | Office-Enclosed |  |  |  | X | [10 empty] | Office-Enclosed | 0.93 |  | 3774 | 4745 | Office-Enclosed | 0.74 |  | 3774 | 4745 | 211.6797 |  | 109.7281 | [45 empty] | -29177.0759 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed | Office-Enclosed
Office-Enclosed700 | Office-EnclosedTR701 |  |  |  | X | [10 empty] | replacement costs are for lamps |  | 700 |  | 4745 |  |  | TR701 |  | 4745 | 88.3097 | 53.7313 | 109.7281 | 43.2433 | 2.575 | 12218.5332 |  | 1.7272 | 8195.4513 |  | 13792.1681 |  |  | 34206.1525 | 13.2485 | 14 | 0.0067 | 31.7915 |  | 0.011446 | 54.3105 |  | 153.0242 |  | 239.1262 | 252.6894 | 3.1987 | 15177.5943 |  | 1.4222 | 6748.2797 |  | 13818.8414 |  |  | 35744.7153 | 13.2485 | 14 | 0.0074 | 35.113 |  | 0.014222 | 67.4828 |  | 187.3762 |  | 289.9719 | 306.4192 | 1538.5628 | -244.0545 |  | PriSch | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 |  |  |  | X | [12 empty] | 739 |  | 4745 |  |  | 0 |  | 4745 | 123.37 | 38.4615 | 0 | 0 | 3.3306 | 15803.697 |  | 0.78351 | 3717.755 |  | 11194.1868 |  |  | 30715.6387 | 13.2485 | 14 | 0.0026 | 12.337 |  | 0.01599 | 75.8726 |  | 193.5909 |  | 281.8005 | 297.7842 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -30715.6387 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  | X | [12 empty] | 0 |  | 4745 |  |  | 0 |  | 4745 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  | X | [12 empty] | 0 |  | 4745 |  |  | 0 |  | 4745 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed700 | Office-EnclosedTR701 |  |  |  | X | [10 empty] | ballast replacement |  | 700 |  | 4745 |  |  | TR701 |  | 4745 | 62.109 |  | 76.59 | [11 empty] | 13.2485 | 14 | 1.9263 | 9140.0562 |  | 1.7272 | 8195.4513 |  | 25824.3163 |  | 43159.8238 | 45607.849 | [10 empty] | 13.2485 | 14 | 2.3934 | 11356.8609 |  | 1.4222 | 6748.2797 |  | 23674.9836 |  | 41780.1243 | 44149.8929 | 0 | -35399.9746 |  | PriSch | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 |  |  |  | X | [12 empty] | 739 |  | 4745 |  |  | 0 |  | 4745 | 15.912 |  | 1e-05 | [11 empty] | 13.2485 | 14 | 2.496 | 11843.52 |  | 0.78351 | 3717.755 |  | 16558.8879 |  | 32120.1629 | 33942.0185 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  | X | [12 empty] | 0 |  | 4745 |  |  | 0 |  | 4745 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  | X | [12 empty] | 0 |  | 4745 |  |  | 0 |  | 4745 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | PriSch | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Small Hotel | [13 empty] | Small_Hotel_Interior Lighting LPD |  | Small Hotel |  |  |  |  | Small Hotel |  |  |  |  | 1021.0561 | 537.6309 | 593.773 | 574.4356
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms |  |  |  |  | X | [9 empty] | Highway Lodging Guest Rooms | 0.77 |  | 3588 | 27933 | Highway Lodging Guest Rooms | 0.41 |  | 3588 | 27933 | 595.7738 |  | 263.4161 |  | 2.7561 | [21 empty] | 5.1471 | [21 empty] | 69925.2247 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms | Highway Lodging Guest Rooms
Highway Lodging Guest Rooms524 | Highway Lodging Guest Roomsww714 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 524 |  | 27933 |  |  | WW714 |  | 27933 | 494.1992 | 56.5217 | 154.1131 | 181.25 | 2.142 | 59832.7009 |  | 1.0881 | 30393.2527 |  | 58135.8164 |  |  | 148361.77 | 2.7871 | 3 | 0.55554 | 15517.8558 |  | 0.10262 | 2866.3555 |  | 16785.9739 |  | 35170.1853 | 37857.1874 | 4.246 | 118602.3622 |  | 0.5429 | 15164.7294 |  | 71712.8209 |  |  | 205479.9124 | 13.9353 | 14 | 0.0032 | 89.3856 |  | 0.0033931 | 94.7796 |  | 288.3862 |  | 472.5514 | 474.744 | 57118.1425 | -37361.4009 |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms524 | Highway Lodging Guest RoomsWW714
Highway Lodging Guest Rooms720 | Highway Lodging Guest RoomsDL703 |  |  |  |  | X | [11 empty] | 720 |  | 27933 |  |  | DL703 |  | 27933 | 101.5745 | 275 | 109.303 | 255.5557 | 0.61413 | 17154.6203 |  | 0.22364 | 6246.8345 |  | 14286.0471 |  |  | 37687.5019 | 13.9353 | 14 | 0.0008 | 22.3464 |  | 0.0022364 | 62.4683 |  | 167.0605 |  | 251.8752 | 253.0439 | 0.9011 | 25170.3376 |  | 0.24065 | 6722.1372 |  | 18602.1092 |  |  | 50494.5841 | 13.9353 | 14 | 0.0009 | 25.1397 |  | 0.0024065 | 67.2214 |  | 180.4595 |  | 272.8205 | 274.0864 | 12807.0822 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms720 | Highway Lodging Guest RoomsDL703
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 |  |  |  |  | X | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 |  |  |  |  | X | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
Highway Lodging Guest Rooms524 | Highway Lodging Guest Roomsww714 |  |  |  |  | X | [9 empty] | ballast replacement |  | 524 |  | 27933 |  |  | WW714 |  | 27933 | 14.3358 |  | 26.208 | [11 empty] | 13.9353 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 13.9353 | 14 | 3.1821 | 88884.7324 |  | 0.5429 | 15164.7294 |  | 93078.3889 |  | 197127.8507 | 198042.524 | 0 | 209526.6911 |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms524 | Highway Lodging Guest RoomsWW714
Highway Lodging Guest Rooms720 | Highway Lodging Guest RoomsDL703 |  |  |  |  | X | [11 empty] | 720 |  | 27933 |  |  | DL703 |  | 27933 | 5.04 |  | 8.343 | [11 empty] | 13.9353 | 14 | 0.46 | 12849.2054 |  | 0.22364 | 6246.8345 |  | 23386.0066 |  | 42482.0465 | 42679.1632 | [10 empty] | 13.9353 | 14 | 0.67515 | 18858.8985 |  | 0.24065 | 6722.1372 |  | 28332.1377 |  | 53913.1733 | 54163.3304 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms720 | Highway Lodging Guest RoomsDL703
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 |  |  |  |  | X | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 |  |  |  |  | X | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Highway Lodging Guest Rooms |  |  | Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0
Corridor/Transition | Corridor/Transition |  |  |  |  | X | [9 empty] | Corridor/Transition | 0.66 |  | 8760 | 5668 | Corridor/Transition | 0.41 |  | 8760 | 5668 | 200.6472 |  | 131.5403 |  | 8.1008 | [21 empty] | 5.7696 | [21 empty] | -28141.1292 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 701 |  | 5668 |  |  | DL706 |  | 5668 | 179.4867 | 31.5789 | 113.3599 | 50 | 5.2271 | 29627.2897 |  | 1.9475 | 11038.43 |  | 24914.1235 |  |  | 65579.8432 | 5.7078 | 6 | 0.0038 | 21.5384 |  | 0.019475 | 110.3843 |  | 283.9077 |  | 415.8304 | 437.1209 | 3.3013 | 18711.9724 |  | 1.23 | 6971.64 |  | 15735.2359 |  |  | 41418.8484 | 5.7078 | 6 | 0.0024 | 13.6032 |  | 0.0123 | 69.7164 |  | 179.3101 |  | 262.6297 | 276.0764 | -24160.9949 | -178.3685 |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | X | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | X | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  |  |  |  | X | [11 empty] | 703 |  | 5668 |  |  | WW708 |  | 5668 | 21.1605 | 267.8571 | 18.1804 | 311.7648 | 2.8737 | 16288.3205 |  | 0.36736 | 2082.1965 |  | 9848.2756 |  |  | 28218.7926 | 5.7078 | 6 | 0.0028 | 15.8704 |  | 0.002296 | 13.0137 |  | 41.8608 |  | 70.7449 | 74.367 | 2.4683 | 13990.3458 |  | 0.31562 | 1788.9491 |  | 8459.3633 |  |  | 24238.6582 | 5.7078 | 6 | 0.0017 | 9.6356 |  | 0.0019726 | 11.1809 |  | 33.4482 |  | 54.2647 | 57.0431 | -3980.1343 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 |  |  |  |  | X | [9 empty] | ballast replacement |  | 701 |  | 5668 |  |  | DL706 |  | 5668 | 23.256 |  | 14.688 | [11 empty] | 5.7078 | 6 | 3.9175 | 22204.3135 |  | 1.9475 | 11038.43 |  | 41008.9369 |  | 74251.6804 | 78053.3664 | [10 empty] | 5.7078 | 6 | 2.4742 | 14023.7769 |  | 1.23 | 6971.64 |  | 25900.3812 |  | 46895.7981 | 49296.863 | 0 | -32763.6273 |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | X | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | X | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 |  |  |  |  | X | [11 empty] | 703 |  | 5668 |  |  | WW708 |  | 5668 | 17.64 |  | 15.147 | [11 empty] | 5.7078 | 6 | 2.1532 | 12204.3376 |  | 0.36736 | 2082.1965 |  | 12780.1485 |  | 27066.6826 | 28452.4968 | [10 empty] | 5.7078 | 6 | 1.85 | 10485.5326 |  | 0.31562 | 1788.9491 |  | 10980.2489 |  | 23254.7307 | 24445.3729 | 0 |  |  | SmHtl | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Stairway | Stairway |  |  |  |  | X | [9 empty] | Stairway | 0.58 |  | 8760 | 1728 | Stairway | 0.49 |  | 8760 | 1728 | 38.9027 |  | 34.2939 |  | 5.37 | [21 empty] | 3.2638 | [21 empty] | -8331.8682 |  |  | SmHtl | Stairway |  |  | Stairway | Stairway
Stairway731 | StairwayTR703 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 731 |  | 1728 |  |  | TR703 |  | 1728 | 12.528 | 137.931 | 12.8859 | 134.0997 | 2.7724 | 4790.7072 |  | 0.58454 | 1010.0888 |  | 3280.5169 |  |  | 9081.3129 | 5.7078 | 6 | 0.0029 | 5.0112 |  | 0.0044588 | 7.7047 |  | 22.024 |  | 34.74 | 36.5187 | 1.0317 | 1782.7702 |  | 0.45861 | 792.4855 |  | 1623.0042 |  |  | 4198.2599 | 5.7078 | 6 | 0.00261 | 4.5101 |  | 0.0045861 | 7.9249 |  | 22.2478 |  | 34.6828 | 36.4585 | -4883.053 | -13.1182 |  | SmHtl | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 |  |  |  |  | X | [11 empty] | 702 |  | 1728 |  |  | WG703 |  | 1728 | 26.3747 | 65.5172 | 21.408 | 80.7175 | 2.5976 | 4488.7165 |  | 1.5019 | 2595.2741 |  | 4665.6764 |  |  | 11749.6669 | 5.7078 | 6 | 0.0029 | 5.0112 |  | 0.0093868 | 16.2205 |  | 42.8808 |  | 64.1125 | 67.395 | 2.2321 | 3857.0794 |  | 0.76192 | 1316.592 |  | 3127.1804 |  |  | 8300.8517 | 5.7078 | 6 | 0.00223 | 3.8534 |  | 0.0076192 | 13.1659 |  | 34.671 |  | 51.6904 | 54.3369 | -3448.8152 |  |  | SmHtl | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 |  |  |  |  | X | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 |  |  |  |  | X | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Stairway |  |  | Stairway0 | Stairway0
Stairway731 | StairwayTR703 |  |  |  |  | X | [9 empty] | ballast replacement |  | 731 |  | 1728 |  |  | TR703 |  | 1728 | 22.968 |  | 26.0739 | [11 empty] | 5.7078 | 6 | 2.0771 | 3589.272 |  | 0.58454 | 1010.0888 |  | 4732.7097 |  | 9332.0705 | 9809.8725 | [10 empty] | 5.7078 | 6 | 0.77181 | 1333.6951 |  | 0.45861 | 792.4855 |  | 2780.2761 |  | 4906.4567 | 5157.6673 | 0 | -10098.335 |  | SmHtl | Stairway |  |  | Stairway731 | StairwayTR703
Stairway702 | StairwayWG703 |  |  |  |  | X | [11 empty] | 702 |  | 1728 |  |  | WG703 |  | 1728 | 21.924 |  | 17.6616 | [11 empty] | 5.7078 | 6 | 1.9461 | 3362.7789 |  | 1.5019 | 2595.2741 |  | 8472.6083 |  | 14430.6614 | 15169.5113 | [10 empty] | 5.7078 | 6 | 1.6724 | 2889.9194 |  | 0.76192 | 1316.592 |  | 5043.2807 |  | 9249.7921 | 9723.3815 | 0 |  |  | SmHtl | Stairway |  |  | Stairway702 | StairwayWG703
Stairway0 | Stairway0 |  |  |  |  | X | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Stairway |  |  | Stairway0 | Stairway0
Stairway0 | Stairway0 |  |  |  |  | X | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Stairway |  |  | Stairway0 | Stairway0
Lobby - Hotel | Lobby - Hotel |  |  |  |  | X | [9 empty] | Lobby - Hotel | 1.06 |  | 7170 | 1755 | Lobby - Hotel | 0.51 |  | 7170 | 1755 | 35.1 |  | 32.5613 |  | 2.753 | [21 empty] | 4.4573 | [21 empty] | 4363.6362 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel | Lobby - Hotel
Lobby - Hotel572 | Lobby - HotelDL702 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 572 |  | 1755 |  |  | DL702 |  | 1755 | 21.06 | 83.3333 | 29.25 | 60 | 0.59136 | 1037.8368 |  | 0.738 | 1295.19 |  | 1749.8975 |  |  | 4082.9243 | 0.11855 | 1 | 0.25656 | 450.2628 |  | 0.282 | 494.91 |  | 1495.4928 |  | 2440.6656 | 20587.7318 | 3.0053 | 5274.3366 |  | 1.025 | 1798.875 |  | 4274.803 |  |  | 11348.0146 | 6.9735 | 7 | 0.004 | 7.02 |  | 0.01025 | 17.9887 |  | 48.4759 |  | 73.4846 | 73.7639 | 7265.0903 | -20538.5349 |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel572 | Lobby - HotelDL702
Lobby - Hotel0 | Lobby - Hotel0 |  |  |  |  | X | [11 empty] | 0 |  | 1755 |  |  | 0 |  | 1755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel0 | Lobby - Hotel0
Lobby - Hotel0 | Lobby - Hotel0 |  |  |  |  | X | [11 empty] | 0 |  | 1755 |  |  | 0 |  | 1755 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel0 | Lobby - Hotel0
Lobby - Hotel727-1 | Lobby - HotelWW703 |  |  |  |  | X | [11 empty] | 727-1 |  | 1755 |  |  | WW703 |  | 1755 | 14.04 | 125 | 3.3113 | 530.0001 | 2.1616 | 3793.608 |  | 0.492 | 863.46 |  | 2659.1444 |  |  | 7316.2124 | 6.9735 | 7 | 0.0016 | 2.808 |  | 0.00492 | 8.6346 |  | 22.915 |  | 34.3576 | 34.4881 | 1.4519 | 2548.1607 |  | 0.18566 | 325.834 |  | 1540.7637 |  |  | 4414.7583 | 6.9735 | 7 | 0.001 | 1.755 |  | 0.0011604 | 2.0365 |  | 6.0922 |  | 9.8836 | 9.9212 | -2901.4541 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel727-1 | Lobby - HotelWW703
Lobby - Hotel572 | Lobby - HotelDL702 |  |  |  |  | X | [9 empty] | ballast replacement |  | 572 |  | 1755 |  |  | DL702 |  | 1755 | 15.39 |  | 21.6 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 6.9735 | 7 | 2.251 | 3950.4875 |  | 1.025 | 1798.875 |  | 6891.9247 |  | 12641.2871 | 12689.324 | 0 | 9301.482 |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel572 | Lobby - HotelDL702
Lobby - Hotel0 | Lobby - Hotel0 |  |  |  |  | X | [11 empty] | 0 |  | 1755 |  |  | 0 |  | 1755 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel0 | Lobby - Hotel0
Lobby - Hotel0 | Lobby - Hotel0 |  |  |  |  | X | [11 empty] | 0 |  | 1755 |  |  | 0 |  | 1755 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel0 | Lobby - Hotel0
Lobby - Hotel727-1 | Lobby - HotelWW703 |  |  |  |  | X | [11 empty] | 727-1 |  | 1755 |  |  | WW703 |  | 1755 | 14.4 |  | 8.91 | [11 empty] | 6.9735 | 7 | 1.62 | 2843.1 |  | 0.492 | 863.46 |  | 3904.0056 |  | 7610.5656 | 7639.4857 | [10 empty] | 6.9735 | 7 | 1.0882 | 1909.8042 |  | 0.18566 | 325.834 |  | 1999.9104 |  | 4235.5486 | 4251.6437 | 0 |  |  | SmHtl | Lobby - Hotel |  |  | Lobby - Hotel727-1 | Lobby - HotelWW703
Storage | Storage |  |  |  |  | X | [9 empty] | Storage | 0.46 |  | 2148 | 1404 | Storage | 0.38 |  | 2148 | 1404 | 16.9958 |  | 14.4195 |  | 3.0309 | [21 empty] | 1.76 | [21 empty] | -2936.0154 |  |  | SmHtl | Storage |  |  | Storage | Storage
Storage738 | StorageLB702 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 738 |  | 1404 |  |  | LB702 |  | 1404 | 16.9958 | 82.6087 | 14.4195 | 97.3684 | 3.0309 | 4255.4058 |  | 0.70055 | 983.5718 |  | 2997.3281 |  |  | 8236.3057 | 23.2775 | 24 | 0.0046 | 6.4584 |  | 0.0074447 | 10.4524 |  | 29.6644 |  | 46.5753 | 48.0209 | 1.76 | 2471.0628 |  | 0.59436 | 834.4757 |  | 1994.7517 |  |  | 5300.2902 | 23.2775 | 24 | 0.0038 | 5.3352 |  | 0.0063162 | 8.868 |  | 25.077 |  | 39.2801 | 40.4994 | -2936.0154 | -7.5216 |  | SmHtl | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage738 | StorageLB702 |  |  |  |  | X | [9 empty] | ballast replacement |  | 738 |  | 1404 |  |  | LB702 |  | 1404 | 47.61 |  | 35.226 | [11 empty] | 23.2775 | 24 | 2.2697 | 3186.7105 |  | 0.70055 | 983.5718 |  | 4414.4244 |  | 8584.7068 | 8851.1761 | [10 empty] | 23.2775 | 24 | 1.3172 | 1849.2957 |  | 0.59436 | 834.4757 |  | 3207.5964 |  | 5891.3678 | 6074.2359 | 0 | -2776.9402 |  | SmHtl | Storage |  |  | Storage738 | StorageLB702
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Storage0 | Storage0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Storage |  |  | Storage0 | Storage0
Office-Enclosed | Office-Enclosed |  |  |  |  | X | [9 empty] | Office-Enclosed | 0.93 |  | 5722 | 1404 | Office-Enclosed | 0.74 |  | 5722 | 1404 | 62.634 |  | 32.4675 |  | 5.9056 | [21 empty] | 3.1987 | [21 empty] | -8633.217 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed | Office-Enclosed
Office-Enclosed700 | Office-EnclosedTR701 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 700 |  | 1404 |  |  | TR701 |  | 1404 | 26.13 | 53.7313 | 32.4675 | 43.2433 | 2.575 | 3615.3468 |  | 1.7272 | 2424.9555 |  | 4080.9703 |  |  | 10121.2725 | 8.7382 | 9 | 0.0067 | 9.4068 |  | 0.011446 | 16.0699 |  | 45.2784 |  | 70.7552 | 72.875 | 3.1987 | 4490.9046 |  | 1.4222 | 1996.7513 |  | 4088.8627 |  |  | 10576.5185 | 8.7382 | 9 | 0.0074 | 10.3896 |  | 0.014222 | 19.9675 |  | 55.4428 |  | 85.7999 | 88.3705 | 455.246 | -70.3847 |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 739 |  | 1404 |  |  | 0 |  | 1404 | 36.504 | 38.4615 | 0 | 0 | 3.3306 | 4676.1624 |  | 0.78351 | 1100.048 |  | 3312.2525 |  |  | 9088.463 | 8.7382 | 9 | 0.0026 | 3.6504 |  | 0.01599 | 22.45 |  | 57.2817 |  | 83.3821 | 85.8802 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -9088.463 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed700 | Office-EnclosedTR701 |  |  |  |  | X | [9 empty] | ballast replacement |  | 700 |  | 1404 |  |  | TR701 |  | 1404 | 62.109 |  | 76.59 | [11 empty] | 8.7382 | 9 | 1.9263 | 2704.455 |  | 1.7272 | 2424.9555 |  | 7641.1676 |  | 12770.578 | 13153.1845 | [10 empty] | 8.7382 | 9 | 2.3934 | 3360.3863 |  | 1.4222 | 1996.7513 |  | 7005.2006 |  | 12362.3381 | 12732.7138 | 0 | -10209.2602 |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 739 |  | 1404 |  |  | 0 |  | 1404 | 15.912 |  | 1e-05 | [11 empty] | 8.7382 | 9 | 2.496 | 3504.384 |  | 0.78351 | 1100.048 |  | 4899.6162 |  | 9504.0482 | 9788.7895 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 |  |  |  |  | X | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Laundry-washing | Laundry-washing |  |  |  |  | X | [9 empty] | Laundry-washing | 0.43 |  | 3276 | 1053 | Laundry-Washing | 0.53 |  | 3276 | 1053 | 11.2355 |  | 15.9454 |  | 2.0422 | [21 empty] | 2.095 | [21 empty] | 651.6492 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing | Laundry-washing
Laundry-washing730 | Laundry-washingTR703 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 730 |  | 1053 |  |  | TR703 |  | 1053 | 11.2355 | 93.7209 | 15.9454 | 66.0378 | 2.0422 | 2150.4716 |  | 0.6562 | 690.9823 |  | 1701.942 |  |  | 4543.3959 | 15.2625 | 16 | 0.004268 | 4.4942 |  | 0.006562 | 6.9098 |  | 19.7518 |  | 31.1558 | 32.6613 | 2.095 | 2206.05 |  | 0.93129 | 980.6439 |  | 2008.3512 |  |  | 5195.0451 | 15.2625 | 16 | 0.0053 | 5.5809 |  | 0.0093129 | 9.8064 |  | 27.5301 |  | 42.9174 | 44.9912 | 651.6492 | 12.3299 |  | SmHtl | Laundry-washing |  |  | Laundry-washing730 | Laundry-washingTR703
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing730 | Laundry-washingTR703 |  |  |  |  | X | [9 empty] | ballast replacement |  | 730 |  | 1053 |  |  | TR703 |  | 1053 | 37.539 |  | 52.947 | [11 empty] | 15.2625 | 16 | 1.5285 | 1609.4831 |  | 0.6562 | 690.9823 |  | 2705.2334 |  | 5005.6987 | 5247.574 | [10 empty] | 15.2625 | 16 | 1.5673 | 1650.3519 |  | 0.93129 | 980.6439 |  | 3440.392 |  | 6071.3877 | 6364.7571 | 0 | 1117.1831 |  | SmHtl | Laundry-washing |  |  | Laundry-washing730 | Laundry-washingTR703
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Laundry-washing0 | Laundry-washing0 |  |  |  |  | X | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Laundry-washing |  |  | Laundry-washing0 | Laundry-washing0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  |  |  |  | X | [9 empty] | Conference/Meeting/Multipurpose | 1.07 |  | 4386 | 864 | Conference/Meeting/Multipurpose | 0.97 |  | 4386 | 864 | 24.264 |  | 23.454 |  | 7.2976 | [21 empty] | 7.2964 | [21 empty] | -141.0746 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 731 |  | 864 |  |  | TR704 |  | 864 | 9.72 | 88.8889 | 13.23 | 65.3061 | 4.302 | 3716.928 |  | 0.90705 | 783.6896 |  | 2545.2286 |  |  | 7045.8462 | 11.3999 | 12 | 0.0045 | 3.888 |  | 0.0069188 | 5.9778 |  | 17.0876 |  | 26.9534 | 28.3722 | 2.118 | 1829.9736 |  | 0.94172 | 813.645 |  | 1666.1478 |  |  | 4309.7664 | 11.3999 | 12 | 0.0049 | 4.2336 |  | 0.0094172 | 8.1364 |  | 22.5921 |  | 34.9621 | 36.8025 | -2736.0798 | -279.819 |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 |  |  |  |  | X | [11 empty] | 511 |  | 864 |  |  | DL702 |  | 864 | 6.336 | 136.3636 | 5.76 | 150.0001 | 0.42871 | 370.4026 |  | 0.451 | 389.664 |  | 554.4536 |  |  | 1314.5202 | 0.95759 | 1 | 0.15679 | 135.4637 |  | 0.02134 | 18.4378 |  | 130.4078 |  | 284.3092 | 296.9 | 1.2021 | 1038.6386 |  | 0.41 | 354.24 |  | 841.8074 |  |  | 2234.686 | 11.3999 | 12 | 0.0016 | 1.3824 |  | 0.0041 | 3.5424 |  | 9.546 |  | 14.4708 | 15.2326 | 920.1658 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 |  |  |  |  | X | [11 empty] | 0 |  | 864 |  |  | 0 |  | 864 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 |  |  |  |  | X | [11 empty] | 727-1 |  | 864 |  |  | WW704 |  | 864 | 8.208 | 105.2632 | 4.464 | 193.5484 | 2.5669 | 2217.8016 |  | 0.58425 | 504.792 |  | 1554.5767 |  |  | 4277.1703 | 11.3999 | 12 | 0.0019 | 1.6416 |  | 0.0058425 | 5.0479 |  | 13.3965 |  | 20.086 | 21.1433 | 3.9763 | 3435.4944 |  | 0.5084 | 439.2576 |  | 2077.2578 |  |  | 5952.0098 | 11.3999 | 12 | 0.0031 | 2.6784 |  | 0.0031775 | 2.7454 |  | 8.4095 |  | 13.8333 | 14.5614 | 1674.8395 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704 |  |  |  |  | X | [9 empty] | ballast replacement |  | 731 |  | 864 |  |  | TR704 |  | 864 | 35.64 |  | 48.951 | [11 empty] | 11.3999 | 12 | 3.2231 | 2784.78 |  | 0.90705 | 783.6896 |  | 3671.93 |  | 7240.3995 | 7621.5342 | [10 empty] | 11.3999 | 12 | 1.5848 | 1369.305 |  | 0.94172 | 813.645 |  | 2854.51 |  | 5037.46 | 5302.6319 | 0 | 1628.5624 |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose731 | Conference/Meeting/MultipurposeTR704
Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702 |  |  |  |  | X | [11 empty] | 511 |  | 864 |  |  | DL702 |  | 864 | 2.4651 |  | 8.64 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 11.3999 | 12 | 0.9004 | 777.9421 |  | 0.41 | 354.24 |  | 1357.179 |  | 2489.3612 | 2620.4011 | 0 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose511 | Conference/Meeting/MultipurposeDL702
Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0 |  |  |  |  | X | [11 empty] | 0 |  | 864 |  |  | 0 |  | 864 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose0 | Conference/Meeting/Multipurpose0
Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704 |  |  |  |  | X | [11 empty] | 727-1 |  | 864 |  |  | WW704 |  | 864 | 17.1 |  | 13.113 | [11 empty] | 11.3999 | 12 | 1.9238 | 1662.12 |  | 0.58425 | 504.792 |  | 2282.3417 |  | 4449.2537 | 4683.4624 | [10 empty] | 11.3999 | 12 | 2.9799 | 2574.612 |  | 0.5084 | 439.2576 |  | 2696.0844 |  | 5709.954 | 6010.5259 | 0 |  |  | SmHtl | Conference/Meeting/Multipurpose |  |  | Conference/Meeting/Multipurpose727-1 | Conference/Meeting/MultipurposeWW704
Restrooms | Restrooms |  |  |  |  | X | [9 empty] | Restrooms | 0.85 |  | 8760 | 351 | Restrooms | 0.63 |  | 8760 | 351 | 11.0582 |  | 11.2827 |  | 9.7535 | [21 empty] | 6.1184 | [21 empty] | -1575.7374 |  |  | SmHtl | Restrooms |  |  | Restrooms | Restrooms
Restrooms604 | RestroomsDL709 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 604 |  | 351 |  |  | DL709 |  | 351 | 4.2362 | 82.8571 | 6.2127 | 56.4972 | 4.2525 | 1492.6275 |  | 0.3637 | 127.6581 |  | 841.5047 |  |  | 2461.7903 | 4.1096 | 5 | 0.040431 | 14.1913 |  | 0.065978 | 23.1582 |  | 65.65 |  | 102.9995 | 125.316 | 3.5159 | 1234.082 |  | 1.0885 | 382.0811 |  | 962.7349 |  |  | 2578.898 | 5.7078 | 6 | 0.003717 | 1.3047 |  | 0.010885 | 3.8208 |  | 10.179 |  | 15.3045 | 16.088 | 117.1077 | -212.0909 |  | SmHtl | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  |  |  |  | X | [11 empty] | 720 |  | 351 |  |  | 0 |  | 351 | 3.1909 | 110 | 0 | 0 | 1.5353 | 538.9031 |  | 0.55909 | 196.2409 |  | 448.7884 |  |  | 1183.9324 | 5.7078 | 6 | 0.002 | 0.702 |  | 0.0055909 | 1.9624 |  | 5.2481 |  | 7.9125 | 8.3176 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -1183.9324 |  |  | SmHtl | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  |  |  |  | X | [11 empty] | 534-2 |  | 351 |  |  | WG701 |  | 351 | 3.631 | 96.6667 | 5.07 | 69.2308 | 3.9657 | 1391.9571 |  | 0.59867 | 210.1334 |  | 872.691 |  |  | 2474.7815 | 4.1096 | 5 | 0.034655 | 12.164 |  | 0.056552 | 19.8499 |  | 56.2714 |  | 88.2853 | 107.4137 | 2.6025 | 913.4619 |  | 0.88833 | 311.805 |  | 740.6019 |  |  | 1965.8688 | 5.7078 | 6 | 0.0026 | 0.9126 |  | 0.0088833 | 3.1181 |  | 8.211 |  | 12.2417 | 12.8685 | -508.9128 |  |  | SmHtl | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Restrooms604 | RestroomsDL709 |  |  |  |  | X | [9 empty] | ballast replacement |  | 604 |  | 351 |  |  | DL709 |  | 351 | 24.2393 |  | 28.7696 | [11 empty] | 5.7078 | 6 | 0.36207 | 127.0862 |  | 0.74224 | 260.5267 |  | 718.0598 |  | 1105.6728 | 1162.2832 | [10 empty] | 5.7078 | 6 | 2.6341 | 924.583 |  | 1.0885 | 382.0811 |  | 1517.6513 |  | 2824.3154 | 2968.9204 | 0 | 1710.2777 |  | SmHtl | Restrooms |  |  | Restrooms604 | RestroomsDL709
Restrooms720 | Restrooms0 |  |  |  |  | X | [11 empty] | 720 |  | 351 |  |  | 0 |  | 351 | 12.6 |  | 1e-05 | [11 empty] | 5.7078 | 6 | 1.15 | 403.6508 |  | 0.55909 | 196.2409 |  | 734.6587 |  | 1334.5504 | 1402.8794 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Restrooms |  |  | Restrooms720 | Restrooms0
Restrooms0 | Restrooms0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Restrooms |  |  | Restrooms0 | Restrooms0
Restrooms534-2 | RestroomsWG701 |  |  |  |  | X | [11 empty] | 534-2 |  | 351 |  |  | WG701 |  | 351 | 24.3 |  | 24.102 | [11 empty] | 5.7078 | 6 | 0.31034 | 108.931 |  | 0.63621 | 223.3086 |  | 615.4799 |  | 947.7195 | 996.2428 | [10 empty] | 5.7078 | 6 | 1.9499 | 684.412 |  | 0.88833 | 311.805 |  | 1194.3868 |  | 2190.6038 | 2302.7627 | 0 |  |  | SmHtl | Restrooms |  |  | Restrooms534-2 | RestroomsWG701
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area |  |  |  |  | X | [9 empty] | Gymnasium/Fitness-Fitness Area | 0.5 |  | 5824 | 351 | Gymnasium/Fitness-Fitness Area | 0.7 |  | 5824 | 351 | 4.6184 |  | 7.4455 |  | 8.8116 | [21 empty] | 14.2043 | [21 empty] | 3251.6691 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area
Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 735 |  | 351 |  |  | ID701 |  | 351 | 4.6184 | 76 | 7.4455 | 47.1429 | 8.8116 | 3092.8642 |  | 1.0609 | 372.3671 |  | 1847.8022 |  |  | 5313.0336 | 8.5852 | 9 | 0.005 | 1.755 |  | 0.0080921 | 2.8403 |  | 8.061 |  | 12.6563 | 13.2679 | 14.2043 | 4985.6997 |  | 1.7103 | 600.3009 |  | 2978.7021 |  |  | 8564.7027 | 8.5852 | 9 | 0.007 | 2.457 |  | 0.013045 | 4.579 |  | 12.761 |  | 19.797 | 20.7536 | 3251.6691 | 7.4857 |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701 |  |  |  |  | X | [9 empty] | ballast replacement |  | 735 |  | 351 |  |  | ID701 |  | 351 | 45 |  | 69.3 | [11 empty] | 8.5852 | 9 | 6.6049 | 2318.3319 |  | 1.0609 | 372.3671 |  | 2370.974 |  | 5061.6731 | 5306.2531 | [10 empty] | 8.5852 | 9 | 10.648 | 3737.432 |  | 1.7103 | 600.3009 |  | 3822.2976 |  | 8160.0305 | 8554.3232 | 0 | 3248.0701 |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area735 | Gymnasium/Fitness-Fitness AreaID701
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Gymnasium/Fitness-Fitness Area |  |  | Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0
Lounge/Recreation - Break room | Lounge/Recreation - Break room |  |  |  |  | X | [9 empty] | Lounge/Recreation - Breakroom | 0.62 |  | 4128 | 351 | Lounge/Recreation - Breakroom | 0.59 |  | 4128 | 351 | 10.6821 |  | 17.745 |  | 10.6975 | [21 empty] | 9.9458 | [21 empty] | 462.9357 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 522 |  | 351 |  |  | DL707 |  | 351 | 6.6105 | 53.0973 | 12.285 | 28.5715 | 2.9226 | 1025.8174 |  | 1.1583 | 406.5457 |  | 886.1384 |  |  | 2318.5015 | 12.1124 | 13 | 0.00339 | 1.1899 |  | 0.011583 | 4.0655 |  | 10.7059 |  | 15.9613 | 17.1309 | 7.1431 | 2507.2321 |  | 2.1525 | 755.5275 |  | 1935.9328 |  |  | 5198.6925 | 12.1124 | 13 | 0.0028 | 0.9828 |  | 0.021525 | 7.5553 |  | 19.1229 |  | 27.6609 | 29.6879 | 2880.191 | 15.6566 |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 |  |  |  |  | X | [11 empty] | 727-2 |  | 351 |  |  | WG702 |  | 351 | 4.0716 | 86.2069 | 5.46 | 64.2857 | 7.7749 | 2728.9899 |  | 0.7134 | 250.4034 |  | 1554.9514 |  |  | 4534.3447 | 12.1124 | 13 | 0.0029 | 1.0179 |  | 0.007134 | 2.504 |  | 6.7735 |  | 10.2954 | 11.0498 | 2.8026 | 983.7282 |  | 0.95667 | 335.79 |  | 797.5712 |  |  | 2117.0894 | 12.1124 | 13 | 0.0028 | 0.9828 |  | 0.0095667 | 3.3579 |  | 8.8427 |  | 13.1834 | 14.1494 | -2417.2553 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702
Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707 |  |  |  |  | X | [9 empty] | ballast replacement |  | 522 |  | 351 |  |  | DL707 |  | 351 | 16.0178 |  | 22.428 | [11 empty] | 0 | 0 | 2.1894 | 768.4706 |  | 1.1583 | 406.5457 |  | 1479.3256 |  | 2654.342 | 0 | [10 empty] | 12.1124 | 13 | 5.3552 | 1879.687 |  | 2.1525 | 755.5275 |  | 3033.3623 |  | 5668.5768 | 6083.9701 | 0 | 4111.1376 |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom522 | Lounge/Recreation - BreakroomDL707
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom0 | Lounge/Recreation - Breakroom0
Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702 |  |  |  |  | X | [11 empty] | 727-2 |  | 351 |  |  | WG702 |  | 351 | 26.1 |  | 22.176 | [11 empty] | 12.1124 | 13 | 5.829 | 2045.979 |  | 0.7134 | 250.4034 |  | 1900.8634 |  | 4197.2458 | 4504.82 | [10 empty] | 12.1124 | 13 | 2.0999 | 737.059 |  | 0.95667 | 335.79 |  | 1286.2627 |  | 2359.1118 | 2531.9875 | 0 |  |  | SmHtl | Lounge/Recreation - Breakroom |  |  | Lounge/Recreation - Breakroom727-2 | Lounge/Recreation - BreakroomWG702
Electrical/Mechanical | Electrical/Mechanical |  |  |  |  | X | [9 empty] | Electrical/Mechanical | 0.43 |  | 2148 | 351 | Electrical/Mechanical | 0.43 |  | 2148 | 351 | 9.1445 |  | 9.2019 |  | 4.0775 | [21 empty] | 3.6273 | [21 empty] | -227.5206 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical | Electrical/Mechanical
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  |  |  |  | X | [9 empty] | replacement costs are for lamps |  | 738 |  | 351 |  |  | LB702 |  | 351 | 2.1245 | 165.2174 | 2.1819 | 160.8696 | 1.5155 | 531.9257 |  | 0.35027 | 122.9465 |  | 374.666 |  |  | 1029.5382 | 23.2775 | 24 | 0.0023 | 0.8073 |  | 0.0037224 | 1.3066 |  | 3.7081 |  | 5.8219 | 6.0026 | 1.0653 | 373.9108 |  | 0.35974 | 126.2694 |  | 301.8374 |  |  | 802.0176 | 23.2775 | 24 | 0.0023 | 0.8073 |  | 0.003823 | 1.3419 |  | 3.7945 |  | 5.9437 | 6.1282 | -227.5206 | 0.12558 |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  |  |  |  | X | [11 empty] | 739 |  | 351 |  |  | TL702 |  | 351 | 7.02 | 50 | 7.02 | 50.0001 | 2.562 | 899.262 |  | 0.6027 | 211.5477 |  | 636.9716 |  |  | 1747.7813 | 23.2775 | 24 | 0.002 | 0.702 |  | 0.0123 | 4.3173 |  | 11.0157 |  | 16.035 | 16.5327 | 2.562 | 899.262 |  | 0.6027 | 211.5477 |  | 636.9716 |  |  | 1747.7813 | 23.2775 | 24 | 0.002 | 0.702 |  | 0.0123 | 4.3173 |  | 11.0157 |  | 16.035 | 16.5327 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical738 | Electrical/MechanicalLB702 |  |  |  |  | X | [9 empty] | ballast replacement |  | 738 |  | 351 |  |  | LB702 |  | 351 | 23.805 |  | 21.321 | [11 empty] | 23.2775 | 24 | 1.1349 | 398.3388 |  | 0.35027 | 122.9465 |  | 551.8031 |  | 1073.0883 | 1106.397 | [10 empty] | 23.2775 | 24 | 0.79723 | 279.8276 |  | 0.35974 | 126.2694 |  | 485.36 |  | 891.457 | 919.1278 | 0 | -187.2692 |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical738 | Electrical/MechanicalLB702
Electrical/Mechanical739 | Electrical/MechanicalTL702 |  |  |  |  | X | [11 empty] | 739 |  | 351 |  |  | TL702 |  | 351 | 12.24 |  | 12.24 | [11 empty] | 23.2775 | 24 | 1.92 | 673.92 |  | 0.6027 | 211.5477 |  | 942.2339 |  | 1827.7016 | 1884.4334 | [10 empty] | 23.2775 | 24 | 1.92 | 673.92 |  | 0.6027 | 211.5477 |  | 942.2339 |  | 1827.7016 | 1884.4334 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical739 | Electrical/MechanicalTL702
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | X | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | SmHtl | Electrical/Mechanical |  |  | Electrical/Mechanical0 | Electrical/Mechanical0
Mid-rise Apartment | [13 empty] | Mid-rise Apartment_Interior Lighting LPD |  | Mid-rise Apartment |  |  |  |  | Mid-rise Apartment |  |  |  |  | 625.6828 | 127.8576 | 563.7046 | 116.473
Office-Enclosed | Office-Enclosed | [5 empty] | X | [8 empty] | Office-Enclosed | 0.93 |  | 3231 | 950 | Office-Enclosed | 0.74 |  | 3231 | 950 | 42.3806 |  | 21.9687 | [45 empty] | -5841.5642 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed | Office-Enclosed
Office-Enclosed700 | Office-EnclosedTR701 | [5 empty] | X | [8 empty] | replacement costs are for lamps |  | 700 |  | 950 |  |  | TR701 |  | 950 | 17.6806 | 53.7313 | 21.9687 | 43.2433 | 2.575 | 2446.2817 |  | 1.7272 | 1640.8174 |  | 2761.3403 |  |  | 6848.4394 | 15.4751 | 16 | 0.0067 | 6.365 |  | 0.011446 | 10.8735 |  | 30.6371 |  | 47.8756 | 49.4996 | 3.1987 | 3038.7175 |  | 1.4222 | 1351.0781 |  | 2766.6806 |  |  | 7156.4762 | 15.4751 | 16 | 0.0074 | 7.03 |  | 0.014222 | 13.5108 |  | 37.5147 |  | 58.0555 | 60.0247 | 308.0368 | -47.8081 |  | MrApt | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 739 |  | 950 |  |  | 0 |  | 950 | 24.7 | 38.4615 | 0 | 0 | 3.3306 | 3164.07 |  | 0.78351 | 744.3345 |  | 2241.1965 |  |  | 6149.601 | 15.4751 | 16 | 0.0026 | 2.47 |  | 0.01599 | 15.1905 |  | 38.759 |  | 56.4195 | 58.3332 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | -6149.601 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 0 |  | 950 |  |  | 0 |  | 950 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 0 |  | 950 |  |  | 0 |  | 950 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed700 | Office-EnclosedTR701 | [5 empty] | X | [8 empty] | ballast replacement |  | 700 |  | 950 |  |  | TR701 |  | 950 | 62.109 |  | 76.59 | [11 empty] | 15.4751 | 16 | 1.9263 | 1829.9375 |  | 1.7272 | 1640.8174 |  | 5170.3057 |  | 8641.0606 | 8934.1654 | [10 empty] | 15.4751 | 16 | 2.3934 | 2273.7656 |  | 1.4222 | 1351.0781 |  | 4739.9862 |  | 8364.8299 | 8648.565 | 0 | -6934.5351 |  | MrApt | Office-Enclosed |  |  | Office-Enclosed700 | Office-EnclosedTR701
Office-Enclosed739 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 739 |  | 950 |  |  | 0 |  | 950 | 15.912 |  | 1e-05 | [11 empty] | 15.4751 | 16 | 2.496 | 2371.2 |  | 0.78351 | 744.3345 |  | 3315.2673 |  | 6430.8018 | 6648.9346 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed739 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 0 |  | 950 |  |  | 0 |  | 950 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Office-Enclosed0 | Office-Enclosed0 | [5 empty] | X | [10 empty] | 0 |  | 950 |  |  | 0 |  | 950 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Office-Enclosed |  |  | Office-Enclosed0 | Office-Enclosed0
Corridor/Transition | Corridor/Transition | [5 empty] | X | [8 empty] | Corridor/Transition | 0.66 |  | 8760 | 3345 | Corridor/Transition | 0.41 |  | 8760 | 3345 | 118.413 |  | 77.6292 | [45 empty] | -16607.6354 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition | Corridor/Transition
Corridor/Transition701 | Corridor/TransitionDL706 | [5 empty] | X | [8 empty] | replacement costs are for lamps |  | 701 |  | 3345 |  |  | DL706 |  | 3345 | 105.925 | 31.5789 | 66.8999 | 50 | 5.2271 | 17484.7008 |  | 1.9475 | 6514.3875 |  | 14703.201 |  |  | 38702.2893 | 5.7078 | 6 | 0.0038 | 12.711 |  | 0.019475 | 65.1439 |  | 167.5496 |  | 245.4045 | 257.9692 | 3.3013 | 11042.9689 |  | 1.23 | 4114.35 |  | 9286.2322 |  |  | 24443.5511 | 5.7078 | 6 | 0.0024 | 8.028 |  | 0.0123 | 41.1435 |  | 105.8208 |  | 154.9923 | 162.9279 | -14258.7382 | -105.2651 |  | MrApt | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | X | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | X | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 | [5 empty] | X | [10 empty] | 703 |  | 3345 |  |  | WW708 |  | 3345 | 12.488 | 267.8571 | 10.7292 | 311.7648 | 2.8737 | 9612.638 |  | 0.36736 | 1228.8192 |  | 5812.0116 |  |  | 16653.4688 | 5.7078 | 6 | 0.0028 | 9.366 |  | 0.002296 | 7.6801 |  | 24.7044 |  | 41.7505 | 43.8881 | 2.4683 | 8256.4761 |  | 0.31562 | 1055.7577 |  | 4992.3377 |  |  | 14304.5716 | 5.7078 | 6 | 0.0017 | 5.6865 |  | 0.0019726 | 6.5985 |  | 19.7396 |  | 32.0246 | 33.6643 | -2348.8972 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Corridor/Transition701 | Corridor/TransitionDL706 | [5 empty] | X | [8 empty] | ballast replacement |  | 701 |  | 3345 |  |  | DL706 |  | 3345 | 23.256 |  | 14.688 | [11 empty] | 5.7078 | 6 | 3.9175 | 13103.9923 |  | 1.9475 | 6514.3875 |  | 24201.6397 |  | 43820.0196 | 46063.6046 | [10 empty] | 5.7078 | 6 | 2.4742 | 8276.2057 |  | 1.23 | 4114.35 |  | 15285.2461 |  | 27675.8018 | 29092.8029 | 0 | -19335.6269 |  | MrApt | Corridor/Transition |  |  | Corridor/Transition701 | Corridor/TransitionDL706
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | X | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | X | [10 empty] | 0 |  | 3345 |  |  | 0 |  | 3345 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition0 | Corridor/Transition0
Corridor/Transition703 | Corridor/TransitionWW708 | [5 empty] | X | [10 empty] | 703 |  | 3345 |  |  | WW708 |  | 3345 | 17.64 |  | 15.147 | [11 empty] | 5.7078 | 6 | 2.1532 | 7202.454 |  | 0.36736 | 1228.8192 |  | 7542.2718 |  | 15973.545 | 16791.3906 | [10 empty] | 5.7078 | 6 | 1.85 | 6188.0922 |  | 0.31562 | 1055.7577 |  | 6480.0516 |  | 13723.9016 | 14426.5653 | 0 |  |  | MrApt | Corridor/Transition |  |  | Corridor/Transition703 | Corridor/TransitionWW708
Dwelling-Unit | Dwelling-Unit | [5 empty] | X | [8 empty] | Dwelling-Unit | 0.29 |  | 526 | 29450 | Dwelling-Unit | 0.2905 |  | 526 | 29450 | 464.8893 |  | 464.1067 | [45 empty] | 460.6644 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit | Dwelling-Unit
Dwelling-Unit301 | Dwelling-Unit301 | [5 empty] | X | [8 empty] | replacement costs are for lamps |  | 301 |  | 29450 |  |  | 301 |  | 29450 | 44.175 | 666.6667 | 44.7332 | 658.3478 | 0.010477 | 308.5473 |  | 0 | 0 |  | 148.4729 |  |  | 457.0202 | 1.9011 | 2 | 0.010477 | 308.5473 |  | 0 | 0 |  | 194.175 |  | 502.7222 | 528.8638 | 0.0013519 | 39.8126 |  | 0 | 0 |  | 19.1578 |  |  | 58.9703 | 1.9011 | 2 | 0.0013519 | 39.8126 |  | 0 | 0 |  | 25.0548 |  | 64.8674 | 68.2405 | -398.0499 | 533.0809 |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit301 | Dwelling-Unit301
Dwelling-Unit302 | Dwelling-Unit302 | [5 empty] | X | [10 empty] | 302 |  | 29450 |  |  | 302 |  | 29450 | 420.7143 | 70 | 419.3735 | 70.2238 | 0.0076555 | 225.4553 |  | 0 | 0 |  | 108.4891 |  |  | 333.9445 | 19.0114 | 20 | 0.0076555 | 225.4553 |  | 0 | 0 |  | 141.8836 |  | 367.3389 | 386.4405 | 0.027341 | 805.1976 |  | 0 | 0 |  | 387.4611 |  |  | 1192.6588 | 19.0114 | 20 | 0.027341 | 805.1976 |  | 0 | 0 |  | 506.727 |  | 1311.9246 | 1380.1447 | 858.7143 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit302 | Dwelling-Unit302
Dwelling-Unit303 | Dwelling-Unit303 | [5 empty] | X | [10 empty] | 303 |  | 29450 |  |  | 303 |  | 29450 | 0 | #DIV/0! | 0 | #DIV/0! | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 28.5171 | 29 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 28.5171 | 29 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit303 | Dwelling-Unit303
Dwelling-Unit0 | Dwelling-Unit0 | [5 empty] | X | [10 empty] | 0 |  | 29450 |  |  | 0 |  | 29450 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit0 | Dwelling-Unit0
Dwelling-Unit301 | Dwelling-Unit301 | [5 empty] | X | [8 empty] | ballast replacement |  | 301 |  | 29450 |  |  | 301 |  | 29450 | 6.3568 |  | 0.82025 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit301 | Dwelling-Unit301
Dwelling-Unit302 | Dwelling-Unit302 | [5 empty] | X | [10 empty] | 302 |  | 29450 |  |  | 302 |  | 29450 | 2.5837 |  | 9.2277 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit302 | Dwelling-Unit302
Dwelling-Unit303 | Dwelling-Unit303 | [5 empty] | X | [10 empty] | 303 |  | 29450 |  |  | 303 |  | 29450 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit303 | Dwelling-Unit303
Dwelling-Unit0 | Dwelling-Unit0 | [5 empty] | X | [10 empty] | 0 |  | 29450 |  |  | 0 |  | 29450 | 1e-07 |  | 1e-05 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  |  | MrApt | Dwelling-Unit |  |  | Dwelling-Unit0 | Dwelling-Unit0
Where there was no LPD difference between 2016 and 2019; 2013 LSC designs were used for both 2013 and 2019.
Where there was an increase in LPD, the space was not included in the cost estimate, as the added cost is not required by 90.1.

## Int Ltg LPD Proto IECC (hidden)
| #VALUE! | [18 empty] | State Commercial Energy Code Cost Effectiveness - Interior Lighting Power Density - IECC 2009 and IECC 2012 - Costs Totals for Each Prototype | [54 empty] | 90.1 Cost Effectiveness - Interior Lighting Power Density 90.1-07by and 90.1-07de Costs - Prototype
Summary
IECC 2012 has changes to interior lighting power allowances, generally significantly lower that for IECC 2009
The cost of interior lighting for the prototypes that meets the lighting power allowances for IECC 2009 and IECC 2012 are shown below.
Interior Lighting - Summary of Total New Construction, Maintenance, and Replacement Costs By Replacement Year by Prototype
[7 empty] | Cost Parameters | [30 empty] | #N/A
[20 empty] | 2009 IECC |  |  |  |  | 2012 IECC | [5 empty] | IECC 2009 Baseline Costs - without implementation of the addenda. | [21 empty] | IECC 2012 - costs with addendum | [20 empty] | Incremental Costs | Small Office | [7 empty] | Large Office | [7 empty] | Standalone Retail | [7 empty] | Primary School | [7 empty] | Small Hotel | [7 empty] | Mid-rise Apartment
|  | Related 90.1-07 Addenda and IECC 2012 Sections |  |  |  | Prototypes Affected | [5 empty] | Climate Location | [5 empty] | Name of Item | [12 empty] | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | New Construction Costs | [9 empty] | Replacement Costs | [11 empty] | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost |  | IECC 2009 |  |  | IECC 2012 |  |  | Incremental Cost
2009 Lookup | 2012 Lookup | 90.1 Addenda | IECC 2009 Chapter(s) Affected | IECC 2012 Section(s) affected | Affected Items | Small Office | Large Office | Standalone Retail | Primary School | Small Hotel | Mid-rise Apartment | 2A Houston | 3A Memphis | 3B El Paso | 4A Baltimore | 5A Chicago | Not Used | Interior Lighting Power Density | Not Used | Costs to provide lighting fixtures, lamps and ballasts to meet space by space lighting power density (LPD) maximum allowed LPD values under IECC 2009. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs are for equipment etc. at today's prices that just meet the IECC 2009 requirements. Costs by IECC 2009 Prototype and Lighting Space Type | IECC 2009 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent Operating Hours for Space Type Lamp Life for Fixtures (Used to Calculate Replacement Life) | Area of Space Type In Prototype Models | Costs to provide lighting fixtures, lamps and ballasts to meet space by space maximum allowed LPD values under IECC 2012 Table 9.6.1. Fixtures, lamps and ballasts and quantities defined from 90.1 development interior lighting models and additional input from 90.1 Lighting Subcommittee. Costs by IECC 2012 Prototype and Lighting Space Type | IECC 2012 Allowed Maximum LPD W/ft2 | Fixture ID Numbers | Annual Full Load Equivalent (FLE) Operating Hours | Area of Space Type, ft2 | Not Used | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Not Used | Not Used | Total | Replacement Life (hours of operation/ component life) | Replacement Period (costs assigned to a 1 year period) | Material Cost/ft2 | Material Subtotal Cost/ft2 × area for space type | Labor Crew Type Not Used | Labor Cost/ft2 | Labor Subtotal Cost/ft2 × Area | Construction Equipment Subtotal | Cost Adjustments | Subtotal | Total (adjusted for actual quantity of replacements in replacement period) | New Construction Costs 2010 minus 2007 | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year | Category | All Costs, First Replacement Only | With Repeated Replacements | Category | Replacement First Year | With Repeated Replacements | 30 Year | 40 Year
[6 empty] | n | [5 empty] | X | X | X | X | X |  | Small _Office_Interior_Lighting_LPD |  | Small Office |  |  | 3642 |  | Small Office |  |  | 3642 | [46 empty] | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0 | New Construction | 0 | 0 | New Construction | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other) |  |  |  |  | n | [13 empty] | Office - Open Plan (Including Other) | 1.1 |  |  | 1100 | Office - Open Plan (Including Other) | 0.9555 |  |  | 1100 | [45 empty] | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0 | Maintenance | 0 | 0 | Maintenance | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 |  |  |  |  | n | [13 empty] | replacement costs shown are for lamps |  | 535 |  | 1100 |  |  | 535 |  | 1100 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0 | Replacement - Year |  |  | Replacement - Year |  |  | 0 | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 |  |  |  |  | n | [15 empty] | 539 |  | 1100 |  |  | 539 |  | 1100 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 |  |  |  |  | n | [15 empty] | 524 |  | 1100 |  |  | 0 |  | 1100 |  | 0.14484 | 159.3197 |  | 0.099336 | 109.2691 |  | 182.1627 |  |  | 450.7515 | 2.7457 | 3 | 0.050718 | 55.7894 |  | 0.0093682 | 10.3051 |  | 46.3463 |  | 112.4408 | 122.8528 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1100 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 3 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 1100 |  |  | 535 |  | 1100 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 |  |  |  |  | n | [15 empty] | 539 |  | 1100 |  |  | 539 |  | 1100 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 |  |  |  |  | n | [15 empty] | 524 |  | 1100 |  |  | 0 |  | 1100 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1100 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 7 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed |  |  |  |  | n | [13 empty] | Office-Enclosed | 1.1 |  |  | 1595 | Office-Enclosed | 1.0822 |  |  | 1595 | [45 empty] | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 0
Office-Enclosed535 | Office-Enclosed531 |  |  |  |  | n | [13 empty] | lamp replacement |  | 535 |  | 1595 |  |  | 531 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 9 | 0 | 0 | 0 | 0
Office-Enclosed539 | Office-Enclosed539 |  |  |  |  | n | [15 empty] | 539 |  | 1595 |  |  | 539 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 10 | 0 | 0 | 0 | 0
Office-Enclosed537-2 | Office-Enclosed0 |  |  |  |  | n | [15 empty] | 537-2 |  | 1595 |  |  | 0 |  | 1595 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 11 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1595 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 12 | 0 | 0 | 0 | 0
Office-Enclosed535 | Office-Enclosed531 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 1595 |  |  | 531 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0
Office-Enclosed539 | Office-Enclosed539 |  |  |  |  | n | [15 empty] | 539 |  | 1595 |  |  | 539 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 14 | 0 | 0 | 0 | 0
Office-Enclosed537-2 | Office-Enclosed0 |  |  |  |  | n | [15 empty] | 537-2 |  | 1595 |  |  | 0 |  | 1595 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 15 | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed537-1 |  |  |  |  | n | [20 empty] | 537-1 |  | 1595 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  |  |  |  | n | [13 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 550 | Conference/Meeting/Multipurpose | 1.1992 |  |  | 550 | [45 empty] | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | lamp replacement |  | 535 |  | 550 |  |  | 535 |  | 550 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 18 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 550 |  |  | 511 |  | 550 |  | 1.3501 | 742.5691 |  | 0.80171 | 440.9385 |  | 783.0451 |  |  | 1966.5527 | 9.8847 | 10 | 0.04367 | 24.0186 |  | 0.071264 | 39.195 |  | 57.8546 |  | 121.0682 | 122.4807 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 19 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 550 |  |  | 0 |  | 550 |  | 0.1594 | 87.6705 |  | 0.26438 | 145.4082 |  | 182.577 |  |  | 415.6557 | 1.1532 | 2 | 0.091909 | 50.5501 |  | 0.01251 | 6.8803 |  | 39.3146 |  | 96.7449 | 167.7834 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 20 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [20 empty] | 527-1 |  | 550 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 21 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 550 |  |  | 535 |  | 550 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 22 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 550 |  |  | 511 |  | 550 | [11 empty] | 13.7287 | 14 | 0.39108 | 215.092 |  | 0.80171 | 440.9385 |  | 616.1716 |  | 1272.202 | 1297.3407 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 23 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 550 |  |  | 0 |  | 550 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 24 | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [20 empty] | 527-1 |  | 550 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 0 | 0 | 0
Corridor/Transition | Corridor/Transition |  |  |  |  | n | [13 empty] | Corridor/Transition | 0.5 |  |  | 660 | Corridor/Transition | 0.6435 |  |  | 660 | [45 empty] | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 26 | 0 | 0 | 0 | 0
Corridor/Transition530 | Corridor/Transition521 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 660 |  |  | 521 |  | 660 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 0 | 0 | 0
Corridor/Transition537-2 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 537-2 |  | 660 |  |  | 0 |  | 660 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 28 | 0 | 0 | 0 | 0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 29 | 0 | 0 | 0 | 0
Corridor/Transition | Corridor/Transition527-2 |  |  |  |  | n | [20 empty] | 0 |  | 660 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 0 | 0
Corridor/Transition530 | Corridor/Transition521 |  |  |  |  | n | [13 empty] | replacement costs are for ballasts |  | 530 |  | 660 |  |  | 521 |  | 660 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0 | 31 | 0 | 0 | 31 | 0 | 0 |  | 0
Corridor/Transition537-2 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 537-2 |  | 660 |  |  | 0 |  | 660 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0 | 32 | 0 | 0 | 32 | 0 | 0 |  | 0
Corridor/Transition0 | Corridor/Transition0 |  |  |  |  | n | [15 empty] | 0 |  | 660 |  |  | 0 |  | 660 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0 | 33 | 0 | 0 | 33 | 0 | 0 |  | 0
Corridor/Transition | Corridor/Transition527-2 |  |  |  |  | n | [20 empty] | 0 |  | 660 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0 | 34 | 0 | 0 | 34 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose |  |  |  |  | n | [13 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 440 | Conference/Meeting/Multipurpose |  |  |  | 550 | [45 empty] | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0 | 35 | 0 | 0 | 35 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 535 |  | 440 |  |  | 535 |  | 550 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0 | 36 | 0 | 0 | 36 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 440 |  |  | 511 |  | 550 |  | 1.3501 | 594.0553 |  | 0.80171 | 352.7508 |  | 626.4361 |  |  | 1573.2422 | 9.8847 | 10 | 0.04367 | 19.2149 |  | 0.071264 | 31.356 |  | 46.2837 |  | 96.8546 | 97.9845 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0 | 37 | 0 | 0 | 37 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 440 |  |  | 0 |  | 550 |  | 0.1594 | 70.1364 |  | 0.26438 | 116.3266 |  | 146.0616 |  |  | 332.5246 | 1.1532 | 2 | 0.091909 | 40.44 |  | 0.01251 | 5.5042 |  | 31.4517 |  | 77.396 | 134.2267 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0 | 38 | 0 | 0 | 38 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [17 empty] | 440 |  |  | 527-1 |  | 550 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0 | 39 | 0 | 0 | 39 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 |  |  |  |  | n | [13 empty] | ballast replacement |  | 535 |  | 440 |  |  | 535 |  | 550 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0 | 40 | 0 | 0 | 40 | 0 | 0 |  | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 |  |  |  |  | n | [15 empty] | 537-1 |  | 440 |  |  | 511 |  | 550 | [11 empty] | 13.7287 | 14 | 0.39108 | 172.0736 |  | 0.80171 | 352.7508 |  | 492.9373 |  | 1017.7616 | 1037.8726 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0 | Residual Year 30 |  | 0 | Residual Year 30 |  | 0 |  | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 |  |  |  |  | n | [15 empty] | 511 |  | 440 |  |  | 0 |  | 550 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0 | Residual Year 40 |  | 0 | Residual Year 40 |  | 0 |  | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 |  |  |  |  | n | [17 empty] | 440 |  |  | 527-1 |  | 550 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage | Storage |  |  |  |  | n | [13 empty] | Storage | 0.8 |  |  | 770 | Storage | 0.61425 |  |  | 770
Storage530 | Storage538 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 770 |  |  | 538 |  | 770 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Storage553 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage0 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage | Storage0 |  |  |  |  | n | [20 empty] | 0 |  | 770 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage530 | Storage538 |  |  |  |  | n | [13 empty] | ballast replacement |  | 530 |  | 770 |  |  | 538 |  | 770 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage553 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage0 | Storage0 |  |  |  |  | n | [15 empty] | 0 |  | 770 |  |  | 0 |  | 770 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage0 |  |  |  |  | n | [20 empty] | 0 |  | 770 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms |  |  |  |  | n | [13 empty] | Restrooms | 0.9 |  |  | 220 | Restrooms | 0.9555 |  |  | 220
Restrooms521 | Restrooms604 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 521 |  | 220 |  |  | 604 |  | 220 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 |  |  |  |  | n | [15 empty] | 537-1 |  | 220 |  |  | 520 |  | 220 |  | 1.2172 | 267.7936 |  | 0.7228 | 159.0162 |  | 282.3905 |  |  | 709.2003 | 9.8847 | 10 | 0.039372 | 8.6619 |  | 0.06425 | 14.1349 |  | 20.8642 |  | 43.661 | 44.1703 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 |  |  |  |  | n | [15 empty] | 524 |  | 220 |  |  | 0 |  | 220 |  | 0.3093 | 68.0465 |  | 0.21213 | 46.6696 |  | 77.8029 |  |  | 192.519 | 2.7457 | 3 | 0.10831 | 23.828 |  | 0.020006 | 4.4014 |  | 19.7948 |  | 48.0242 | 52.4713 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 220 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 |  |  |  |  | n | [13 empty] | ballast replacement |  | 521 |  | 220 |  |  | 604 |  | 220 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 |  |  |  |  | n | [15 empty] | 537-1 |  | 220 |  |  | 520 |  | 220 | [11 empty] | 13.7287 | 14 | 0.35259 | 77.5689 |  | 0.7228 | 159.0162 |  | 222.2107 |  | 458.7957 | 467.8616 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms524 | Restrooms0 |  |  |  |  | n | [15 empty] | 524 |  | 220 |  |  | 0 |  | 220 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 220 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Break room |  |  |  |  | n | [13 empty] | Lounge/Recreation - Break room | 1.2 |  |  | 110 | Lounge/Recreation - Break room | 0.71175 |  |  | 110
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 537-1 |  | 110 |  |  | 521 |  | 110 |  | 1.3506 | 148.5678 |  | 0.802 | 88.2197 |  | 156.6659 |  |  | 393.4534 | 9.8847 | 10 | 0.043686 | 4.8055 |  | 0.07129 | 7.8419 |  | 11.5751 |  | 24.2224 | 24.505 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 521 |  | 110 |  |  | 0 |  | 110 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Break room | Lounge/Recreation - Breakroom527-2 |  |  |  |  | n | [17 empty] | 110 |  |  | 527-2 |  | 110 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 |  |  |  |  | n | [13 empty] | ballast replacement |  | 537-1 |  | 110 |  |  | 521 |  | 110 | [11 empty] | 13.7287 | 14 | 0.39122 | 43.034 |  | 0.802 | 88.2197 |  | 123.2791 |  | 254.5329 | 259.5624 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 |  |  |  |  | n | [15 empty] | 521 |  | 110 |  |  | 0 |  | 110 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Breakroom527-2 |  |  |  |  | n | [17 empty] | 110 |  |  | 527-2 |  | 110 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical |  |  |  |  | n | [13 empty] | Electrical/Mechanical | 1.5 |  |  | 110 | Electrical/Mechanical | 0.92625 |  |  | 110
Electrical/Mechanical538 | Electrical/Mechanical538 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 538 |  | 110 |  |  | 538 |  | 110 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 |  |  |  |  | n | [17 empty] | 110 |  |  | 0 |  | 110 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 |  |  |  |  | n | [13 empty] | ballast replacement |  | 538 |  | 110 |  |  | 538 |  | 110 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 |  |  |  |  | n | [15 empty] | 0 |  | 110 |  |  | 0 |  | 110 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 |  |  |  |  | n | [17 empty] | 110 |  |  | 0 |  | 110 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway |  |  |  |  | n | [13 empty] | Stairway | 0.6 |  |  | 165 | Stairway | 0.67275 |  |  | 165
Stairway530 | Stairway530 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 530 |  | 165 |  |  | 530 |  | 165 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway602 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 602 |  | 165 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway0 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway | Stairway0 |  |  |  |  | n | [17 empty] | 165 |  |  | 0 |  | 165 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway530 | Stairway530 |  |  |  |  | n | [13 empty] | ballast replacement |  | 530 |  | 165 |  |  | 530 |  | 165 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway602 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 602 |  | 165 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway0 |  |  |  |  | n | [15 empty] | 0 |  | 165 |  |  | 0 |  | 165 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway0 |  |  |  |  | n | [17 empty] | 165 |  |  | 0 |  | 165 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby |  |  |  |  | n | [13 empty] | Lobby | 1.3 |  |  | 330 | Lobby | 0.8775 |  |  | 330
Lobby534-2 | Lobby523 |  |  |  |  | n | [13 empty] | replacement costs are for lamps |  | 534-2 |  | 330 |  |  | 523 |  | 330 |  | 3.4171 | 1127.6332 |  | 0.5204 | 171.7311 |  | 708.4214 |  |  | 2007.7857 | 9.8847 | 10 | 0.030124 | 9.941 |  | 0.049158 | 16.2223 |  | 23.9452 |  | 50.1085 | 50.6931 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby523 | Lobby521 |  |  |  |  | n | [15 empty] | 523 |  | 330 |  |  | 521 |  | 330 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby521 | Lobby0 |  |  |  |  | n | [15 empty] | 521 |  | 330 |  |  | 0 |  | 330 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby534-2 |  |  |  |  | n | [17 empty] | 330 |  |  | 534-2 |  | 330 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 |  |  |  |  | n | [13 empty] | ballast replacement |  | 534-2 |  | 330 |  |  | 523 |  | 330 | [11 empty] | 13.7287 | 14 | 0.26977 | 89.0237 |  | 0.55303 | 182.4985 |  | 255.0252 |  | 526.5474 | 536.9519 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby523 | Lobby521 |  |  |  |  | n | [15 empty] | 523 |  | 330 |  |  | 521 |  | 330 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby521 | Lobby0 |  |  |  |  | n | [15 empty] | 521 |  | 330 |  |  | 0 |  | 330 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby534-2 |  |  |  |  | n | [20 empty] | 534-2 |  | 330 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
n
[18 empty] | Large_Office_Interior Lighting LPD |  | Large Office |  |  | 2938 |  | Large Office |  |  | 2938
Office - Open Plan (Including Other) | Office - Open Plan (Including Other) | [18 empty] | Office - Open Plan (Including Other) | 1.1 |  |  | 285144 | Office - Open Plan (Including Other) | 0.97216 |  |  | 285144 | [27 empty] | 0
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 285144 |  |  | 535 |  | 285144 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 | [5 empty] | n | [14 empty] | 539 |  | 285144 |  |  | 539 |  | 285144 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 | [5 empty] | n | [14 empty] | 524 |  | 285144 |  |  | 0 |  | 285144 |  | 0.14484 | 41299.1443 |  | 0.099336 | 28324.94 |  | 47220.5379 |  |  | 116844.6222 | 2.7457 | 3 | 0.050718 | 14461.8393 |  | 0.0093682 | 2671.2952 |  | 12013.9691 |  | 29147.1035 | 31846.1253 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 285144 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office - Open Plan (Including Other)535 | Office - Open Plan (Including Other)535 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 285144 |  |  | 535 |  | 285144 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office - Open Plan (Including Other)539 | Office - Open Plan (Including Other)539 | [5 empty] | n | [14 empty] | 539 |  | 285144 |  |  | 539 |  | 285144 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office - Open Plan (Including Other)524 | Office - Open Plan (Including Other)0 | [5 empty] | n | [14 empty] | 524 |  | 285144 |  |  | 0 |  | 285144 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office - Open Plan (Including Other) | Office - Open Plan (Including Other)537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 285144 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed | Office-Enclosed | [5 empty] | n | [12 empty] | Office-Enclosed | 1.1 |  |  | 92363 | Office-Enclosed | 1.1011 |  |  | 92363 | [27 empty] | 0
Office-Enclosed535 | Office-Enclosed531 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 92363 |  |  | 531 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [5 empty] | n | [14 empty] | 539 |  | 92363 |  |  | 539 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [5 empty] | n | [14 empty] | 537-2 |  | 92363 |  |  | 0 |  | 92363 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 92363 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 92363 |  |  | 531 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [5 empty] | n | [14 empty] | 539 |  | 92363 |  |  | 539 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [5 empty] | n | [14 empty] | 537-2 |  | 92363 |  |  | 0 |  | 92363 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [5 empty] | n | [19 empty] | 537-1 |  | 92363 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | [5 empty] | n | [12 empty] | Conference/Meeting/Multipurpose | 1.3 |  |  | 9628 | Conference/Meeting/Multipurpose | 1.2202 |  |  | 9628
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 535 |  | 9628 |  |  | 535 |  | 9628 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [5 empty] | n | [14 empty] | 537-1 |  | 9628 |  |  | 511 |  | 9628 |  | 1.3501 | 12999.0098 |  | 0.80171 | 7718.8288 |  | 13707.5602 |  |  | 34425.3988 | 9.8847 | 10 | 0.04367 | 420.4565 |  | 0.071264 | 686.1267 |  | 1012.7707 |  | 2119.3539 | 2144.0797 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [5 empty] | n | [14 empty] | 511 |  | 9628 |  |  | 0 |  | 9628 |  | 0.1594 | 1534.7125 |  | 0.26438 | 2545.4373 |  | 3196.0928 |  |  | 7276.2426 | 1.1532 | 2 | 0.091909 | 884.9016 |  | 0.01251 | 120.4426 |  | 688.2198 |  | 1693.5641 | 2937.124 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [5 empty] | n | [19 empty] | 527-1 |  | 9628 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [5 empty] | n | [12 empty] | ballast replacement |  | 535 |  | 9628 |  |  | 535 |  | 9628 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [5 empty] | n | [14 empty] | 537-1 |  | 9628 |  |  | 511 |  | 9628 | [11 empty] | 13.7287 | 14 | 0.39108 | 3765.2824 |  | 0.80171 | 7718.8288 |  | 10786.3637 |  | 22270.4749 | 22710.5395 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [5 empty] | n | [14 empty] | 511 |  | 9628 |  |  | 0 |  | 9628 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [5 empty] | n | [19 empty] | 527-1 |  | 9628 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition | Corridor/Transition | [5 empty] | n | [12 empty] | Corridor/Transition | 0.5 |  |  | 21304 | Corridor/Transition | 0.65472 |  |  | 21304
Corridor/Transition530 | Corridor/Transition521 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 21304 |  |  | 521 |  | 21304 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 537-2 |  | 21304 |  |  | 0 |  | 21304 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [5 empty] | n | [19 empty] | 0 |  | 21304 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 21304 |  |  | 521 |  | 21304 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 537-2 |  | 21304 |  |  | 0 |  | 21304 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [5 empty] | n | [14 empty] | 0 |  | 21304 |  |  | 0 |  | 21304 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [5 empty] | n | [19 empty] | 0 |  | 21304 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage | [5 empty] | n | [12 empty] | Storage | 0.8 |  |  | 11866 | Storage | 0.62496 |  |  | 11866
Storage530 | Storage538 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 11866 |  |  | 538 |  | 11866 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Storage553 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage0 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage | Storage0 | [5 empty] | n | [19 empty] | 0 |  | 11866 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage530 | Storage538 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 11866 |  |  | 538 |  | 11866 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage553 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage0 | Storage0 | [5 empty] | n | [14 empty] | 0 |  | 11866 |  |  | 0 |  | 11866 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage0 | [5 empty] | n | [19 empty] | 0 |  | 11866 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms | [5 empty] | n | [12 empty] | Restrooms | 0.9 |  |  | 15505 | Restrooms | 0.97216 |  |  | 15505
Restrooms521 | Restrooms604 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 521 |  | 15505 |  |  | 604 |  | 15505 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [5 empty] | n | [14 empty] | 537-1 |  | 15505 |  |  | 520 |  | 15505 |  | 1.2172 | 18873.3619 |  | 0.7228 | 11207.0267 |  | 19902.1115 |  |  | 49982.5001 | 9.8847 | 10 | 0.039372 | 610.4641 |  | 0.06425 | 996.1926 |  | 1470.4496 |  | 3077.1062 | 3113.0058 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [5 empty] | n | [14 empty] | 524 |  | 15505 |  |  | 0 |  | 15505 |  | 0.3093 | 4795.7329 |  | 0.21213 | 3289.1444 |  | 5483.3361 |  |  | 13568.2134 | 2.7457 | 3 | 0.10831 | 1679.3355 |  | 0.020006 | 310.1957 |  | 1395.0843 |  | 3384.6155 | 3698.0309 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 15505 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 | [5 empty] | n | [12 empty] | ballast replacement |  | 521 |  | 15505 |  |  | 604 |  | 15505 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [5 empty] | n | [14 empty] | 537-1 |  | 15505 |  |  | 520 |  | 15505 | [11 empty] | 13.7287 | 14 | 0.35259 | 5466.8423 |  | 0.7228 | 11207.0267 |  | 15660.8041 |  | 32334.6731 | 32973.6062 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [5 empty] | n | [14 empty] | 524 |  | 15505 |  |  | 0 |  | 15505 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 15505 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Break room | Lounge/Recreation - Break room | [5 empty] | n | [12 empty] | Lounge/Recreation - Break room | 1.2 |  |  | 9530 | Lounge/Recreation - Break room | 0.72416 |  |  | 9530
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 537-1 |  | 9530 |  |  | 521 |  | 9530 |  | 1.3506 | 12871.3726 |  | 0.802 | 7643.0377 |  | 13572.9657 |  |  | 34087.376 | 9.8847 | 10 | 0.043686 | 416.3281 |  | 0.07129 | 679.3896 |  | 1002.8263 |  | 2098.544 | 2123.027 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 521 |  | 9530 |  |  | 0 |  | 9530 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [5 empty] | n | [19 empty] | 527-2 |  | 9530 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [5 empty] | n | [12 empty] | ballast replacement |  | 537-1 |  | 9530 |  |  | 521 |  | 9530 | [11 empty] | 13.7287 | 14 | 0.39122 | 3728.3111 |  | 0.802 | 7643.0377 |  | 10680.4525 |  | 22051.8012 | 22487.5448 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 0 |  | 9530 |  |  | 0 |  | 9530 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [5 empty] | n | [14 empty] | 521 |  | 9530 |  |  | 0 |  | 9530 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [5 empty] | n | [19 empty] | 527-2 |  | 9530 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical | [5 empty] | n | [12 empty] | Electrical/Mechanical | 1.5 |  |  | 31023 | Electrical/Mechanical | 0.9424 |  |  | 31023
Electrical/Mechanical538 | Electrical/Mechanical538 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 538 |  | 31023 |  |  | 538 |  | 31023 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [5 empty] | n | [19 empty] | 0 |  | 31023 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [5 empty] | n | [12 empty] | ballast replacement |  | 538 |  | 31023 |  |  | 538 |  | 31023 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [5 empty] | n | [14 empty] | 0 |  | 31023 |  |  | 0 |  | 31023 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [5 empty] | n | [19 empty] | 0 |  | 31023 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway | [5 empty] | n | [12 empty] | Stairway | 0.6 |  |  | 8484 | Stairway | 0.68448 |  |  | 8484
Stairway530 | Stairway530 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 530 |  | 8484 |  |  | 530 |  | 8484 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway602 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 602 |  | 8484 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway0 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway | Stairway0 | [5 empty] | n | [19 empty] | 0 |  | 8484 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway530 | Stairway530 | [5 empty] | n | [12 empty] | ballast replacement |  | 530 |  | 8484 |  |  | 530 |  | 8484 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway602 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 602 |  | 8484 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway0 | [5 empty] | n | [14 empty] | 0 |  | 8484 |  |  | 0 |  | 8484 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway0 | [5 empty] | n | [19 empty] | 0 |  | 8484 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby | [5 empty] | n | [12 empty] | Lobby | 1.3 |  |  | 13792 | Lobby | 0.8928 |  |  | 13792
Lobby534-2 | Lobby523 | [5 empty] | n | [12 empty] | replacement costs are for lamps |  | 534-2 |  | 13792 |  |  | 523 |  | 13792 |  | 3.4171 | 47128.2336 |  | 0.5204 | 7177.3199 |  | 29607.7222 |  |  | 83913.2757 | 9.8847 | 10 | 0.030124 | 415.4726 |  | 0.049158 | 677.9936 |  | 1000.7657 |  | 2094.2319 | 2118.6646 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [5 empty] | n | [14 empty] | 523 |  | 13792 |  |  | 521 |  | 13792 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [5 empty] | n | [14 empty] | 521 |  | 13792 |  |  | 0 |  | 13792 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 13792 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [5 empty] | n | [12 empty] | ballast replacement |  | 534-2 |  | 13792 |  |  | 523 |  | 13792 | [11 empty] | 13.7287 | 14 | 0.26977 | 3720.65 |  | 0.55303 | 7627.3325 |  | 10658.5059 |  | 22006.4885 | 22441.3367 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby523 | Lobby521 | [5 empty] | n | [14 empty] | 523 |  | 13792 |  |  | 521 |  | 13792 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby521 | Lobby0 | [5 empty] | n | [14 empty] | 521 |  | 13792 |  |  | 0 |  | 13792 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby534-2 | [5 empty] | n | [19 empty] | 534-2 |  | 13792 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
[18 empty] | Standalone_Retail_Interior Lighting LPD |  | Standalone Retail |  |  | 3613 |  | Standalone Retail |  |  | 3613 | [28 empty] | 0
Storage | Storage | [6 empty] | n | [11 empty] | Storage | 0.7752 |  |  | 4088 | Storage | 0.58716 |  |  | 4088 | [27 empty] | 0
Storage530 | Storage538 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 530 |  | 4088 |  |  | 538 |  | 4088 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Storage553 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage0 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage | Storage0 | [6 empty] | n | [18 empty] | 0 |  | 4088 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage530 | Storage538 | [6 empty] | n | [11 empty] | ballast replacement |  | 530 |  | 4088 |  |  | 538 |  | 4088 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage553 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage0 | Storage0 | [6 empty] | n | [13 empty] | 0 |  | 4088 |  |  | 0 |  | 4088 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage0 | [6 empty] | n | [18 empty] | 0 |  | 4088 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Retail - Sales Area | Retail - Sales Area | [6 empty] | n | [11 empty] | Retail - Sales Area | 1.6473 |  |  | 20467 | Retail - Sales Area | 1.5658 |  |  | 20467 | [27 empty] | 0
Retail - Sales Area535 | Retail - Sales Area535 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 535 |  | 20467 |  |  | 535 |  | 20467 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Retail - Sales Area541 | Retail - Sales Area541 | [6 empty] | n | [13 empty] | 541 |  | 20467 |  |  | 541 |  | 20467 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Retail - Sales Area572 | Retail - Sales Area0 | [6 empty] | n | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Retail - Sales Area | Retail - Sales Area537-1 | [6 empty] | n | [18 empty] | 537-1 |  | 20467 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Retail - Sales Area535 | Retail - Sales Area535 | [6 empty] | n | [11 empty] | ballast replacement |  | 535 |  | 20467 |  |  | 535 |  | 20467 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Retail - Sales Area541 | Retail - Sales Area541 | [6 empty] | n | [13 empty] | 541 |  | 20467 |  |  | 541 |  | 20467 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Retail - Sales Area572 | Retail - Sales Area0 | [6 empty] | n | [13 empty] | 0 |  | 20467 |  |  | 0 |  | 20467 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Retail - Sales Area | Retail - Sales Area537-1 | [6 empty] | n | [18 empty] | 537-1 |  | 20467 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby | Lobby | [6 empty] | n | [11 empty] | Lobby | 1.2597 |  |  | 129 | Lobby | 0.8388 |  |  | 129 | [27 empty] | 0
Lobby534-2 | Lobby523 | [6 empty] | n | [11 empty] | replacement costs are for lamps |  | 534-2 |  | 129 |  |  | 523 |  | 129 |  | 3.3111 | 427.1372 |  | 0.50427 | 65.0502 |  | 268.3436 |  |  | 760.531 | 9.8847 | 10 | 0.02919 | 3.7656 |  | 0.047635 | 6.1449 |  | 9.0702 |  | 18.9806 | 19.2021 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [6 empty] | n | [13 empty] | 523 |  | 129 |  |  | 521 |  | 129 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [6 empty] | n | [13 empty] | 521 |  | 129 |  |  | 0 |  | 129 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [6 empty] | n | [18 empty] | 534-2 |  | 129 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [6 empty] | n | [11 empty] | ballast replacement |  | 534-2 |  | 129 |  |  | 523 |  | 129 | [11 empty] | 13.7287 | 14 | 0.26141 | 33.7214 |  | 0.53588 | 69.1288 |  | 96.6012 |  | 199.4514 | 203.3925 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby523 | Lobby521 | [6 empty] | n | [13 empty] | 523 |  | 129 |  |  | 521 |  | 129 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby521 | Lobby0 | [6 empty] | n | [13 empty] | 521 |  | 129 |  |  | 0 |  | 129 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby534-2 | [6 empty] | n | [18 empty] | 534-2 |  | 129 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
0
[18 empty] | Primary_School_Interior Lighting LPD |  | Primary School |  |  | 3774 |  | Primary School |  |  | 3774 | [28 empty] | 0
Restrooms | Restrooms | [7 empty] | n | [10 empty] | Restrooms | 0.9099 |  |  | 2044 | Restrooms | 0.9212 |  |  | 2044 | [27 empty] | 0
Restrooms521 | Restrooms604 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 521 |  | 2044 |  |  | 604 |  | 2044 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [7 empty] | n | [12 empty] | 537-1 |  | 2044 |  |  | 520 |  | 2044 |  | 1.2306 | 2515.4144 |  | 0.73075 | 1493.6563 |  | 2652.5247 |  |  | 6661.5954 | 9.8847 | 10 | 0.039805 | 81.3618 |  | 0.064957 | 132.7711 |  | 195.9794 |  | 410.1123 | 414.8969 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [7 empty] | n | [12 empty] | 524 |  | 2044 |  |  | 0 |  | 2044 |  | 0.3127 | 639.1684 |  | 0.21447 | 438.3724 |  | 730.8111 |  |  | 1808.3519 | 2.7457 | 3 | 0.1095 | 223.8194 |  | 0.020226 | 41.3424 |  | 185.9348 |  | 451.0967 | 492.8682 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 2044 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms521 | Restrooms604 | [7 empty] | n | [10 empty] | ballast replacement |  | 521 |  | 2044 |  |  | 604 |  | 2044 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [7 empty] | n | [12 empty] | 537-1 |  | 2044 |  |  | 520 |  | 2044 | [11 empty] | 13.7287 | 14 | 0.35646 | 728.6128 |  | 0.73075 | 1493.6563 |  | 2087.2493 |  | 4309.5185 | 4394.6746 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [7 empty] | n | [12 empty] | 524 |  | 2044 |  |  | 0 |  | 2044 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 2044 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Dining Area | Dining Area | [7 empty] | n | [10 empty] | Dining Area | 0.9099 |  |  | 3389 | Dining Area | 0.611 |  |  | 3389 | [27 empty] | 0
Dining Area531 | Dining Area535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 531 |  | 3389 |  |  | 535 |  | 3389 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Dining Area524 | Dining Area521 | [7 empty] | n | [12 empty] | 524 |  | 3389 |  |  | 521 |  | 3389 |  | 0.48745 | 1651.9735 |  | 0.33432 | 1133.0029 |  | 1888.8304 |  |  | 4673.8069 | 2.7457 | 3 | 0.17069 | 578.4763 |  | 0.031529 | 106.8523 |  | 480.561 |  | 1165.8896 | 1273.851 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Dining Area0 | Dining Area0 | [7 empty] | n | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Dining Area | Dining Area537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 3389 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Dining Area531 | Dining Area535 | [7 empty] | n | [10 empty] | ballast replacement |  | 531 |  | 3389 |  |  | 535 |  | 3389 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Dining Area524 | Dining Area521 | [7 empty] | n | [12 empty] | 524 |  | 3389 |  |  | 521 |  | 3389 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Dining Area0 | Dining Area0 | [7 empty] | n | [12 empty] | 0 |  | 3389 |  |  | 0 |  | 3389 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Dining Area | Dining Area537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 3389 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Classroom/Lecture/Training | Classroom/Lecture/Training | [7 empty] | n | [10 empty] | Classroom/Lecture/Training | 1.4154 |  |  | 37187 | Classroom/Lecture/Training | 1.1656 |  |  | 37187 | [27 empty] | 0
Classroom/Lecture/Training535 | Classroom/Lecture/Training535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 37187 |  |  | 535 |  | 37187 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Classroom/Lecture/Training537-2 | Classroom/Lecture/Training521 | [7 empty] | n | [12 empty] | 537-2 |  | 37187 |  |  | 521 |  | 37187 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 | [7 empty] | n | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Classroom/Lecture/Training | Classroom/Lecture/Training537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 37187 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Classroom/Lecture/Training535 | Classroom/Lecture/Training535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 37187 |  |  | 535 |  | 37187 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Classroom/Lecture/Training537-2 | Classroom/Lecture/Training521 | [7 empty] | n | [12 empty] | 537-2 |  | 37187 |  |  | 521 |  | 37187 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Classroom/Lecture/Training0 | Classroom/Lecture/Training0 | [7 empty] | n | [12 empty] | 0 |  | 37187 |  |  | 0 |  | 37187 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Classroom/Lecture/Training | Classroom/Lecture/Training537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 37187 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition | Corridor/Transition | [7 empty] | n | [10 empty] | Corridor/Transition | 0.5055 |  |  | 12073 | Corridor/Transition | 0.6204 |  |  | 12073 | [27 empty] | 0
Corridor/Transition530 | Corridor/Transition521 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 530 |  | 12073 |  |  | 521 |  | 12073 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 537-2 |  | 12073 |  |  | 0 |  | 12073 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [7 empty] | n | [17 empty] | 0 |  | 12073 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [7 empty] | n | [10 empty] | ballast replacement |  | 530 |  | 12073 |  |  | 521 |  | 12073 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 537-2 |  | 12073 |  |  | 0 |  | 12073 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [7 empty] | n | [12 empty] | 0 |  | 12073 |  |  | 0 |  | 12073 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [7 empty] | n | [17 empty] | 0 |  | 12073 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area | [7 empty] | n | [10 empty] | Gymnasium/Fitness-Fitness Area | 0.9099 |  |  | 3841 | Gymnasium/Fitness-Fitness Area | 0.6768 |  |  | 3841 | [27 empty] | 0
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 3841 |  |  | 535 |  | 3841 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [17 empty] | 0 |  | 3841 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 3841 |  |  | 535 |  | 3841 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [12 empty] | 0 |  | 3841 |  |  | 0 |  | 3841 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [7 empty] | n | [17 empty] | 0 |  | 3841 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Food Preparation | Food Preparation | [7 empty] | n | [10 empty] | Food Preparation | 1.2132 |  |  | 1808 | Food Preparation | 0.9306 |  |  | 1808 | [27 empty] | 0
Food Preparation530 | Food Preparation530 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 530 |  | 1808 |  |  | 530 |  | 1808 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Food Preparation | Food Preparation0 | [7 empty] | n | [17 empty] | 0 |  | 1808 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Food Preparation530 | Food Preparation530 | [7 empty] | n | [10 empty] | ballast replacement |  | 530 |  | 1808 |  |  | 530 |  | 1808 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Food Preparation0 | Food Preparation0 | [7 empty] | n | [12 empty] | 0 |  | 1808 |  |  | 0 |  | 1808 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Food Preparation | Food Preparation0 | [7 empty] | n | [17 empty] | 0 |  | 1808 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Library | Library | [7 empty] | n | [10 empty] | Library | 1.2132 |  |  | 4293 | Library | 0.8742 |  |  | 4293 | [27 empty] | 0
Library535 | Library535 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 4293 |  |  | 535 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Library520 | Library520 | [7 empty] | n | [12 empty] | 520 |  | 4293 |  |  | 520 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Library529 | Library0 | [7 empty] | n | [12 empty] | 529 |  | 4293 |  |  | 0 |  | 4293 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Library | Library0 | [7 empty] | n | [17 empty] | 0 |  | 4293 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Library535 | Library535 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 4293 |  |  | 535 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Library520 | Library520 | [7 empty] | n | [12 empty] | 520 |  | 4293 |  |  | 520 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Library529 | Library0 | [7 empty] | n | [12 empty] | 529 |  | 4293 |  |  | 0 |  | 4293 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Library | Library0 | [7 empty] | n | [17 empty] | 0 |  | 4293 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby | [7 empty] | n | [10 empty] | Lobby | 1.3143 |  |  | 1840 | Lobby | 0.846 |  |  | 1840 | [27 empty] | 0
Lobby534-2 | Lobby523 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 534-2 |  | 1840 |  |  | 523 |  | 1840 |  | 3.4547 | 6356.5709 |  | 0.52612 | 968.0639 |  | 3993.436 |  |  | 11318.0708 | 9.8847 | 10 | 0.030456 | 56.0382 |  | 0.049699 | 91.4465 |  | 134.9815 |  | 282.4662 | 285.7616 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby523 | Lobby521 | [7 empty] | n | [12 empty] | 523 |  | 1840 |  |  | 521 |  | 1840 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby521 | Lobby0 | [7 empty] | n | [12 empty] | 521 |  | 1840 |  |  | 0 |  | 1840 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 1840 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby534-2 | Lobby523 | [7 empty] | n | [10 empty] | ballast replacement |  | 534-2 |  | 1840 |  |  | 523 |  | 1840 | [11 empty] | 13.7287 | 14 | 0.27274 | 501.8345 |  | 0.55911 | 1028.7608 |  | 1437.6 |  | 2968.1953 | 3026.8469 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby523 | Lobby521 | [7 empty] | n | [12 empty] | 523 |  | 1840 |  |  | 521 |  | 1840 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby521 | Lobby0 | [7 empty] | n | [12 empty] | 521 |  | 1840 |  |  | 0 |  | 1840 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby534-2 | [7 empty] | n | [17 empty] | 534-2 |  | 1840 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical | [7 empty] | n | [10 empty] | Electrical/Mechanical | 1.5165 |  |  | 2712 | Electrical/Mechanical | 0.893 |  |  | 2712 | [27 empty] | 0
Electrical/Mechanical538 | Electrical/Mechanical538 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 538 |  | 2712 |  |  | 538 |  | 2712 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [7 empty] | n | [17 empty] | 0 |  | 2712 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [7 empty] | n | [10 empty] | ballast replacement |  | 538 |  | 2712 |  |  | 538 |  | 2712 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [7 empty] | n | [12 empty] | 0 |  | 2712 |  |  | 0 |  | 2712 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [7 empty] | n | [17 empty] | 0 |  | 2712 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed | [7 empty] | n | [10 empty] | Office-Enclosed | 1.1121 |  |  | 4745 | Office-Enclosed | 1.0434 |  |  | 4745 | [27 empty] | 0
Office-Enclosed535 | Office-Enclosed531 | [7 empty] | n | [10 empty] | replacement costs are for lamps |  | 535 |  | 4745 |  |  | 531 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [7 empty] | n | [12 empty] | 539 |  | 4745 |  |  | 539 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [7 empty] | n | [12 empty] | 537-2 |  | 4745 |  |  | 0 |  | 4745 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 4745 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [7 empty] | n | [10 empty] | ballast replacement |  | 535 |  | 4745 |  |  | 531 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [7 empty] | n | [12 empty] | 539 |  | 4745 |  |  | 539 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [7 empty] | n | [12 empty] | 537-2 |  | 4745 |  |  | 0 |  | 4745 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [7 empty] | n | [17 empty] | 537-1 |  | 4745 | [33 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
0
[18 empty] | Small_Hotel_Interior Lighting LPD |  | Small Hotel |  |  |  |  | Small Hotel
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms | [8 empty] | n | [9 empty] | Highway Lodging Guest Rooms | 1.1 |  | 3588 | 27933 | Highway Lodging Guest Rooms | 0.75 |  | 3588 | 27933 | [27 empty] | 0
Highway Lodging Guest Rooms524 | Highway Lodging Guest Rooms529 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 524 |  | 27933 |  |  | 529 |  | 27933 |  | 0.3851 | 10757.0452 |  | 0.26412 | 7377.6991 |  | 12299.3702 |  |  | 30434.1145 | 2.7457 | 3 | 0.13485 | 3766.8253 |  | 0.024909 | 695.783 |  | 3129.237 |  | 7591.8452 | 8294.8501 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Highway Lodging Guest Rooms520 | Highway Lodging Guest Rooms520 | [8 empty] | n | [11 empty] | 520 |  | 27933 |  |  | 520 |  | 27933 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 | [8 empty] | n | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms0 | [8 empty] | n | [16 empty] | 0 |  | 27933 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Highway Lodging Guest Rooms524 | Highway Lodging Guest Rooms529 | [8 empty] | n | [9 empty] | ballast replacement |  | 524 |  | 27933 |  |  | 529 |  | 27933 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Highway Lodging Guest Rooms520 | Highway Lodging Guest Rooms520 | [8 empty] | n | [11 empty] | 520 |  | 27933 |  |  | 520 |  | 27933 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Highway Lodging Guest Rooms0 | Highway Lodging Guest Rooms0 | [8 empty] | n | [11 empty] | 0 |  | 27933 |  |  | 0 |  | 27933 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Highway Lodging Guest Rooms | Highway Lodging Guest Rooms0 | [8 empty] | n | [16 empty] | 0 |  | 27933 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition | [8 empty] | n | [9 empty] | Corridor/Transition | 0.6475 |  | 8760 | 5668 | Corridor/Transition | 0.74514 |  | 8760 | 5668 | [27 empty] | 0
Corridor/Transition530 | Corridor/Transition521 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 5668 |  |  | 521 |  | 5668 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Corridor/Transition537-2 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 537-2 |  | 5668 |  |  | 0 |  | 5668 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition0 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition | Corridor/Transition527-2 | [8 empty] | n | [16 empty] | 0 |  | 5668 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Corridor/Transition530 | Corridor/Transition521 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 5668 |  |  | 521 |  | 5668 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Corridor/Transition537-2 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 537-2 |  | 5668 |  |  | 0 |  | 5668 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition0 | Corridor/Transition0 | [8 empty] | n | [11 empty] | 0 |  | 5668 |  |  | 0 |  | 5668 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Corridor/Transition | Corridor/Transition527-2 | [8 empty] | n | [16 empty] | 0 |  | 5668 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway | [8 empty] | n | [9 empty] | Stairway | 0.777 |  | 8760 | 1728 | Stairway | 0.77901 |  | 8760 | 1728
Stairway530 | Stairway530 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1728 |  |  | 530 |  | 1728 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway602 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 602 |  | 1728 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Stairway0 | Stairway0 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway | Stairway0 | [8 empty] | n | [16 empty] | 0 |  | 1728 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Stairway530 | Stairway530 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1728 |  |  | 530 |  | 1728 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway602 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 602 |  | 1728 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Stairway0 | Stairway0 | [8 empty] | n | [11 empty] | 0 |  | 1728 |  |  | 0 |  | 1728 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Stairway | Stairway0 | [8 empty] | n | [16 empty] | 0 |  | 1728 | [33 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby - Hotel | [8 empty] | n | [9 empty] | Lobby - Hotel | 1.4245 |  | 7170 | 1755 | Lobby - Hotel | 1.1967 |  | 7170 | 1755
Lobby - Hotel535 | Lobby - Hotel572 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 1755 |  |  | 572 |  | 1755 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lobby - Hotel572 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 572 |  | 1755 |  |  | 0 |  | 1755 |  | 0.46241 | 811.5244 |  | 1.0193 | 1788.8441 |  | 2117.613 |  |  | 4717.9815 | 0.23339 | 1 | 0.35435 | 621.8778 |  | 0.38948 | 683.5421 |  | 1136.7108 |  | 2442.1307 | 10463.8118 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby - Hotel524 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 524 |  | 1755 |  |  | 0 |  | 1755 |  | 0.33528 | 588.4132 |  | 0.22995 | 403.5621 |  | 672.7788 |  |  | 1664.7542 | 2.7457 | 3 | 0.11741 | 206.0463 |  | 0.021686 | 38.0595 |  | 171.1701 |  | 415.276 | 453.7305 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby | Lobby - Hotel527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 1755 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lobby - Hotel535 | Lobby - Hotel572 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 1755 |  |  | 572 |  | 1755 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lobby - Hotel572 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 572 |  | 1755 |  |  | 0 |  | 1755 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby - Hotel524 | Lobby - Hotel0 | [8 empty] | n | [11 empty] | 524 |  | 1755 |  |  | 0 |  | 1755 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lobby | Lobby - Hotel527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 1755 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Storage | Storage | [8 empty] | n | [9 empty] | Storage | 1.036 |  | 2148 | 1404 | Storage | 0.71127 |  | 2148 | 1404
Storage530 | Storage538 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1404 |  |  | 538 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Storage553 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage0 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage | Storage0 | [8 empty] | n | [16 empty] | 0 |  | 1404 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Storage530 | Storage538 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1404 |  |  | 538 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Storage553 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage0 | Storage0 | [8 empty] | n | [11 empty] | 0 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Storage | Storage0 | [8 empty] | n | [16 empty] | 0 |  | 1404 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Office-Enclosed | Office-Enclosed | [8 empty] | n | [9 empty] | Office-Enclosed | 1.4245 |  | 5722 | 1404 | Office-Enclosed | 1.2532 |  | 5722 | 1404
Office-Enclosed535 | Office-Enclosed531 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 1404 |  |  | 531 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [8 empty] | n | [11 empty] | 539 |  | 1404 |  |  | 539 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [8 empty] | n | [11 empty] | 537-2 |  | 1404 |  |  | 0 |  | 1404 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [8 empty] | n | [16 empty] | 537-1 |  | 1404 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed535 | Office-Enclosed531 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 1404 |  |  | 531 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed539 | Office-Enclosed539 | [8 empty] | n | [11 empty] | 539 |  | 1404 |  |  | 539 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Office-Enclosed537-2 | Office-Enclosed0 | [8 empty] | n | [11 empty] | 537-2 |  | 1404 |  |  | 0 |  | 1404 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Office-Enclosed | Office-Enclosed537-1 | [8 empty] | n | [16 empty] | 537-1 |  | 1404 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Hospital - Laundry-washing | Hospital - Laundry-washing | [8 empty] | n | [9 empty] | Hospital - Laundry/Washing | 0.777 |  | 3276 | 1053 | Hospital - Laundry/Washing | 0.6774 |  | 3276 | 1053
Hospital - Laundry-washing530 | Hospital - Laundry-washing530 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 530 |  | 1053 |  |  | 530 |  | 1053 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Hospital - Laundry-washing | Hospital - Laundry-washing0 | [8 empty] | n | [16 empty] | 0 |  | 1053 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Hospital - Laundry-washing530 | Hospital - Laundry-washing530 | [8 empty] | n | [9 empty] | ballast replacement |  | 530 |  | 1053 |  |  | 530 |  | 1053 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Hospital - Laundry-washing0 | Hospital - Laundry-washing0 | [8 empty] | n | [11 empty] | 0 |  | 1053 |  |  | 0 |  | 1053 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Hospital - Laundry-washing | Hospital - Laundry-washing0 | [8 empty] | n | [16 empty] | 0 |  | 1053 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose | [8 empty] | n | [9 empty] | Conference/Meeting/Multipurpose | 1.6835 |  | 4386 | 864 | Conference/Meeting/Multipurpose | 1.3887 |  | 4386 | 864
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 864 |  |  | 535 |  | 864 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [8 empty] | n | [11 empty] | 537-1 |  | 864 |  |  | 511 |  | 864 |  | 1.7484 | 1510.6286 |  | 1.0382 | 897.0132 |  | 1592.97 |  |  | 4000.6118 | 9.8847 | 10 | 0.056553 | 48.8617 |  | 0.092286 | 79.7355 |  | 117.6951 |  | 246.2923 | 249.1658 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [8 empty] | n | [11 empty] | 511 |  | 864 |  |  | 0 |  | 864 |  | 0.20642 | 178.3505 |  | 0.34237 | 295.8079 |  | 371.4213 |  |  | 845.5798 | 1.1532 | 2 | 0.11902 | 102.8353 |  | 0.0162 | 13.9968 |  | 79.9788 |  | 196.8109 | 341.3263 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [8 empty] | n | [18 empty] | 864 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Conference/Meeting/Multipurpose535 | Conference/Meeting/Multipurpose535 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 864 |  |  | 535 |  | 864 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose537-1 | Conference/Meeting/Multipurpose511 | [8 empty] | n | [11 empty] | 537-1 |  | 864 |  |  | 511 |  | 864 | [11 empty] | 13.7287 | 14 | 0.50644 | 437.5674 |  | 1.0382 | 897.0132 |  | 1253.4947 |  | 2588.0753 | 2639.2157 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Conference/Meeting/Multipurpose511 | Conference/Meeting/Multipurpose0 | [8 empty] | n | [11 empty] | 511 |  | 864 |  |  | 0 |  | 864 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Conference/Meeting/Multipurpose | Conference/Meeting/Multipurpose527-1 | [8 empty] | n | [16 empty] | 527-1 |  | 864 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Restrooms | Restrooms | [8 empty] | n | [9 empty] | Restrooms | 1.1655 |  | 8760 | 351 | Restrooms | 1.1064 |  | 8760 | 351
Restrooms521 | Restrooms604 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 521 |  | 351 |  |  | 604 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms537-1 | Restrooms520 | [8 empty] | n | [11 empty] | 537-1 |  | 351 |  |  | 520 |  | 351 |  | 1.5763 | 553.292 |  | 0.93603 | 328.5455 |  | 583.4508 |  |  | 1465.2883 | 9.8847 | 10 | 0.050987 | 17.8964 |  | 0.083203 | 29.2044 |  | 43.1077 |  | 90.2085 | 91.261 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Restrooms524 | Restrooms0 | [8 empty] | n | [11 empty] | 524 |  | 351 |  |  | 0 |  | 351 |  | 0.40055 | 140.5918 |  | 0.27471 | 96.4246 |  | 160.7496 |  |  | 397.7661 | 2.7457 | 3 | 0.14026 | 49.2314 |  | 0.025908 | 9.0937 |  | 40.8983 |  | 99.2235 | 108.4116 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms | Restrooms534-2 | [8 empty] | n | [16 empty] | 534-2 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Restrooms521 | Restrooms604 | [8 empty] | n | [9 empty] | ballast replacement |  | 521 |  | 351 |  |  | 604 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms537-1 | Restrooms520 | [8 empty] | n | [11 empty] | 537-1 |  | 351 |  |  | 520 |  | 351 | [11 empty] | 13.7287 | 14 | 0.4566 | 160.2661 |  | 0.93603 | 328.5455 |  | 459.1126 |  | 947.9242 | 966.6551 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Restrooms524 | Restrooms0 | [8 empty] | n | [11 empty] | 524 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 13.7287 | 14 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Restrooms | Restrooms534-2 | [8 empty] | n | [16 empty] | 534-2 |  | 351 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area | [8 empty] | n | [9 empty] | Gymnasium/Fitness-Fitness Area | 1.1655 |  | 5824 | 351 | Gymnasium/Fitness-Fitness Area | 0.81288 |  | 5824 | 351
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 535 |  | 351 |  |  | 535 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Gymnasium/Fitness-Fitness Area535 | Gymnasium/Fitness-Fitness Area535 | [8 empty] | n | [9 empty] | ballast replacement |  | 535 |  | 351 |  |  | 535 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area0 | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Gymnasium/Fitness-Fitness Area | Gymnasium/Fitness-Fitness Area0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom | [8 empty] | n | [9 empty] | Lounge/Recreation - Break room | 1.554 |  | 4128 | 351 | Lounge/Recreation - Break room | 0.82417 |  | 4128 | 351
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 537-1 |  | 351 |  |  | 521 |  | 351 |  | 1.749 | 613.9159 |  | 1.0386 | 364.544 |  | 647.3792 |  |  | 1625.8391 | 9.8847 | 10 | 0.056573 | 19.8573 |  | 0.09232 | 32.4043 |  | 47.831 |  | 100.0926 | 101.2604 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 521 |  | 351 |  |  | 0 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [8 empty] | n | [16 empty] | 527-2 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Lounge/Recreation - Breakroom537-1 | Lounge/Recreation - Breakroom521 | [8 empty] | n | [9 empty] | ballast replacement |  | 537-1 |  | 351 |  |  | 521 |  | 351 | [11 empty] | 13.7287 | 14 | 0.50663 | 177.8264 |  | 1.0386 | 364.544 |  | 509.4172 |  | 1051.7876 | 1072.5709 | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Lounge/Recreation - Breakroom572 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom521 | Lounge/Recreation - Breakroom0 | [8 empty] | n | [11 empty] | 521 |  | 351 |  |  | 0 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Lounge/Recreation - Breakroom | Lounge/Recreation - Breakroom527-2 | [8 empty] | n | [16 empty] | 527-2 |  | 351 | [33 empty] | #N/A |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | 0 | 0
Electrical/Mechanical | Electrical/Mechanical | [8 empty] | n | [9 empty] | Electrical/Mechanical | 1.9425 |  | 2148 | 351 | Electrical/Mechanical | 1.0725 |  | 2148 | 351
Electrical/Mechanical538 | Electrical/Mechanical538 | [8 empty] | n | [9 empty] | replacement costs are for lamps |  | 538 |  | 351 |  |  | 538 |  | 351 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 |  | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical | Electrical/Mechanical0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 |  | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Electrical/Mechanical538 | Electrical/Mechanical538 | [8 empty] | n | [9 empty] | ballast replacement |  | 538 |  | 351 |  |  | 538 |  | 351 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical0 | Electrical/Mechanical0 | [8 empty] | n | [11 empty] | 0 |  | 351 |  |  | 0 |  | 351 | [11 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | [10 empty] | #N/A | #N/A | 0 | 0 |  | 0 | 0 |  | 0 | 0 | #N/A | 0
Electrical/Mechanical | Electrical/Mechanical0 | [8 empty] | n | [16 empty] | 0 |  | 351 | [33 empty] | #N/A |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
[18 empty] | Mid-rise Apartment_Interior Lighting LPD |  | Mid-rise Apartment |  |  |  |  | Mid-rise Apartment
Office-Enclosed | Office-Enclosed | [9 empty] | n | [8 empty] | Office-Enclosed | 1.2166 |  | 3231 | 950 | Office-Enclosed | 0.86802 |  | 3231 | 950
Office-Enclosed535 | Office-Enclosed531 | [9 empty] | n | [8 empty] | replacement costs are for lamps |  | 535 |  | 950 |  |  | 531 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed539 | Office-Enclosed539 | [9 empty] | n | [10 empty] | 539 |  | 950 |  |  | 539 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed537-2 | Office-Enclosed0 | [9 empty] | n | [10 empty] | 537-2 |  | 950 |  |  | 0 |  | 950 |  | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | 0 | 0 | 0 | 0 |  | #N/A | #N/A |  | #N/A | #N/A | 0 | #N/A
Office-Enclosed | Office-Enclosed537-1 | [9 empty] | n | [15 empty] | 537-1 |  | 950 | [23 empty] | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  |  | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A
Office-Enclosed535 | Office-Enclosed531 | [9 empty] | n | [8 empty] | ballast replacement |  | 535 |  | 950 |  |  | 531 |  | 950 | [11 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | [10 empty] | #N/A | #N/A | #N/A | #N/A |  | #N/A | #N/A |  | #N/A | #N/A | #N/A | 0