## Building Summary
Item |  | Descriptions | [15 empty] | Data Source
Program
Building Prototype |  | Small Office | Medium Office | Large Office | Stand-alone Retail | Strip Mall | Primary School | Secondary School | Outpatient Healthcare | Hospital | Small Hotel | Large Hotel | Warehouse (non-refrigerated) | Quick Service Restaurant | Full Service Restaurant | Mid-rise Apartment | High-rise Apartment
Form
Building shape
Number of Floors |  | 1 | 3 | 12 (plus basement) | 1 | 1 | 1 | 2 | 3 | 5 (plus basement) | 4 | 6 above-ground floors plus one basement (284 ft x 75 ft) | 1 | 1 | 1 | 4 | 10
Window Fraction (Window-to-Wall Ratio) |  | 21.19% | 33% | 38.05% | 7.13% | 10.51% | 35% | 35% | 19.85% | 14.63% | 10.88% | 26.62% | 0.71% | 14% | 17.11% | 19.9% | 29.84%
Architecture
Exterior walls Construction | Above-Grade Wall Type | Wood-frame walls (2X4 16 in o.c.) 1in. Stucco + 5/8 in. gypsum board + wall Insulation+ 5/8 in. gypsum board | Steel-Frame Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in. | Mass (pre-cast concrete panel) 8 in. heavy-weight concrete + wall insulation + 0.5 in. gypsum board | Concrete Block Wall 8 in. CMU+Wall Insulation+0.5 in. gypsum board | Steel-framed Wall 1 in. Stucco + 0.625 in. gypsum board + wall insulation + 0.625 in. gypsum board | Steel-framed Walls (2x4, 16" OC) 0.75" stucco + 0.625" gypsum board + cavity insulation + 0.625" gypsum board | Steel-Framed Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in | Steel-Frame Walls (2X4 16IN OC) 0.4 in. Stucco+5/8 in. gypsum board + wall Insulation+5/8 in. | Mass (concrete blocks): 8 in. HW concrete+wall insulation+0.5 in. gypsum board | Steel-Frame Walls (2x4 16 in. OC) 1 in. Stucco + 5/8 in. gypsum board + wall Insulation + 5/8 in. gypsum board | Mass Wall 8 in. CMU, wall insulation and 0.5 in. gypsum board | Metal Building Wall Metal Surface + Wall Insulation + Gypsum Board | Wood-framed wall 1 in. stucco + 0.625 in. gypsum board + wall insulation + 0.625 in. gypsum board | Steel-framed Wall 1 in. Stucco + 0.625 in. gypsum board + wall insulation + 0.625 in. gypsum board | Steel-frame walls (2X4 16IN o.c.) 0.4 in. stucco+5/8 in. gypsum board + wall Insulation+5/8 in. gypsum board | Steel-frame walls (2X4 16 in o.c.) 0.4 in. stucco+5/8 in. gypsum board + wall Insulation+5/8 in. gypsum board
| Associated Space Conditioning Category | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Residential (Patient Rooms); Nonresidential (Others) | Residential (Guest Rooms); Nonresidential (Others) | Residential (Guest Rooms); Nonresidential (Others) | Nonresidential (Office); Semi-heated (Warehouse) | Nonresidential | Nonresidential | Nonresidential (Office, Corridors); Residential (Others) | Nonresidential (Office, Corridors); Residential (Others)
Roof Constuction | Roof Type | Attic roof with wood joist: Roof insulation + 5/8 in. gypsum board | Built-up roof: Roof membrane+roof insulation+metal decking | Built-up roof: Roof membrane+roof insulation+metal decking | Built-up roof: Roof membrane+roof insulation+metal decking | Built-up Roof: Roof membrane+Roof insulation+metal decking | Built-up roof Roof membrane + roof insulation + metal decking | Built-up Roof Roof membrane+Roof insulation+metal decking | Built-up roof: Roof membrane+roof insulation+metal decking | Built-up Roof: roof membrane+roof insulation+metal decking | Built-up roof: Roof membrane + roof insulation + metal decking | Insulation entirely above deck (Single-ply roof membrane, steel deck with rigid insulation) | Metal Building Roof Metal Surface + Roof Insulation | Unconditioned attic roof modeled with asphalt shingles and 0.625 in. gypsum board (no insulation). Ceiling between attic and conditioned zones modeled with wood-joist attic roof consisting of the following layers: insulation and 0.625 in. gypsum board | Unconditioned attic roof modeled with asphalt shingles and 0.625 in. gypsum board (no insulation). Ceiling between attic and conditioned zones modeled with wood-joist attic roof consisting of the following layers: insulation and 0.625 in. gypsum board | Built-up roof roof membrane+roof insulation+metal decking | Built-up roof roof membrane+roof insulation+metal decking
| Associated Space Conditioning Category | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential | Nonresidential; Semi-heated | Nonresidential | Nonresidential | Residential | Residential

## Climate Zone
No | Country | Thermal Zone | Thermal Climate Zone Name | Representative City | Weather Location | Weather File Name
1 | International | 0A | Extremely Hot Humid | Ho Chi Minh City, Vietnam | Ho Chi Minh City/Tan Son Nhat Airport, Vietnam | VNM_Ho.Chi.Minh.City-Tan.Son.Nhat.AP.489000_IWEC2.epw
2 | International | 0B | Extremely Hot Dry | Dubai, United Arab Emirates | Dubai International Airport, United Arab Emirates | ARE_Dubai.Intl.AP.411940_IWEC2.epw
3 | USA | 1A | Very Hot Humid | Miami, FL | Miami International Airport, Florida | USA_FL_Miami.Intl.AP.722020_TMY3.epw
4 | International | 1B | Very Hot Dry | New Delhi, India | New Delhi/Safdarjung Airport, Delhi, India | IND_Delhi_New.Delhi-Safdarjung.AP.421820_IWEC2.epw
5 | USA | 2A | Hot Humid | Tampa, FL | Tampa/MacDill AFB, Florida | USA_FL_Tampa-MacDill.AFB.747880_TMY3.epw
6 | USA | 2B | Hot Dry | Tucson, AZ | Tucson/Davis-Monthan AFB, Arizona | USA_AZ_Tucson-Davis-Monthan.AFB.722745_TMY3.epw
7 | USA | 3A | Warm Humid | Atlanta, GA | Atlanta/Hartsfield Jackson International Airport, Georgia | USA_GA_Atlanta-Hartsfield.Jackson.Intl.AP.722190_TMY3.epw
8 | USA | 3B | Warm Dry | El Paso, TX | El Paso International Airport, Texas | USA_TX_El.Paso.Intl.AP.722700_TMY3.epw
9 | USA | 3C | Warm Marine | San Diego, CA | San Diego/Brown Field Municipal Airport, California | USA_CA_San.Deigo-Brown.Field.Muni.AP.722904_TMY3.epw
10 | USA | 4A | Mixed Humid | New York, NY | New York/John F Kennedy International Airport, New York | USA_NY_New.York-John.F.Kennedy.Intl.AP.744860_TMY3.epw
11 | USA | 4B | Mixed Dry | Albuquerque, NM | Albuquerque International Sunport, New Mexico | USA_NM_Albuquerque.Intl.Sunport.723650_TMY3.epw
12 | USA | 4C | Mixed Marine | Seattle, WA | Seattle-Tacoma International Airport, Washington | USA_WA_Seattle-Tacoma.Intl.AP.727930_TMY3.epw
13 | USA | 5A | Cool Humid | Buffalo, NY | Buffalo Niagara International Airport, New York | USA_NY_Buffalo.Niagara.Intl.AP.725280_TMY3.epw
14 | USA | 5B | Cool Dry | Denver, CO | Denver/Aurora/Buckley AFB, Colorado | USA_CO_Denver-Aurora-Buckley.AFB.724695_TMY3.EPW
15 | USA | 5C | Cool Marine | Port Angeles, WA | Port Angeles/William R Fairchild International Airport, Washington | USA_WA_Port.Angeles-William.R.Fairchild.Intl.AP.727885_TMY3.epw
16 | USA | 6A | Cold Humid | Rochester, MN | Rochester International Airport, Minnesota | USA_MN_Rochester.Intl.AP.726440_TMY3.epw
17 | USA | 6B | Cold Dry | Great Falls, MO | Great Falls International Airport, Montana | USA_MT_Great.Falls.Intl.AP.727750_TMY3.epw
18 | USA | 7 | Very Cold | International Falls, MN | International Falls International Airport, Minnesota | USA_MN_International.Falls.Intl.AP.727470_TMY3.epw
19 | USA | 8 | Subarctic/Arctic | Fairbanks, AK | Fairbanks International Airport, Alaska | USA_AK_Fairbanks.Intl.AP.702610_TMY3.epw

## Zone and HVAC System Summary
Prototype Building | Prototype Building (raw_data) | Thermal Zone | Area [ft2] | Multipliers | Conditioned | HVAC System Type (90.1-2004) | HVAC System Name | Gross Wall Area [ft2] | Window Glass Area [ft2] | Space Type for LPD | Occupancy Category | Lighting Power Desnity [W/ft2] | Design Occupancy Density [people/1,000 ft2] | Electric Equipment [W/ft2] | Gas Equipment [W/ft2] | Total OSA Ventilation [cfm/ft2] |  |  | Exhaust Airflow [cfm/ft2] | Envelope Infiltration (Flow/Exterior Wall Area) [cfm/ft2] | Envelope Infiltration (Flow/Zone) [cfm/zone] | Infiltration Through Entrances [cfm/zone]
[12 empty] | 90.1-2004 |  |  |  | 90.1-2004 (62-1999) cfm/per | 90.1-2004 (62-1999) cfm/sf | 90.1-2004 (62-1999) cfm/zone
Small Office
Small Office | OfficeSmall | CORE_ZN | 1610.9253 | 1 | Yes | 4.2 PSZ-HP with gas auxiliary heat | PSZ-AC:1 | 0 | 0 | Weighted | Office space | 0.9914 | 5.0002 | 0.62988 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Small Office | OfficeSmall | PERIMETER_ZN_1 | 1221.1645 | 1 | Yes | 4.2 PSZ-HP with gas auxiliary heat | PSZ-AC:2 | 909.0114 | 222.0593 | Weighted | Office space | 0.9914 | 5.0002 | 0.62988 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 274.9997
Small Office | OfficeSmall | PERIMETER_ZN_2 | 724.4105 | 1 | Yes | 4.2 PSZ-HP with gas auxiliary heat | PSZ-AC:3 | 606.0076 | 120.0175 | Weighted | Office space | 0.9914 | 5.0002 | 0.62988 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Office | OfficeSmall | PERIMETER_ZN_3 | 1221.1645 | 1 | Yes | 4.2 PSZ-HP with gas auxiliary heat | PSZ-AC:4 | 909.0114 | 179.9724 | Weighted | Office space | 0.9914 | 5.0002 | 0.62988 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Office | OfficeSmall | PERIMETER_ZN_4 | 724.4105 | 1 | Yes | 4.2 PSZ-HP with gas auxiliary heat | PSZ-AC:5 | 606.0076 | 120.0175 | Weighted | Office space | 0.9914 | 5.0002 | 0.62988 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Office | OfficeSmall | ATTIC | 6113.6799 | 1 | No |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 423.9879 | 0
Small Office | OfficeSmall | Total | 5502.0751 |  |  |  |  | 3030.1455 | 642.0666 |  |  | 0.9914 | 5.0002 | 0.62988
Small Office | OfficeSmall | Conditioned Total | 5502.0751 |  |  |  |  | 3030.1455 | 642.0666 |  |  | 0.9914 | 5.0002 | 0.62988
Small Office | OfficeSmall | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Medium Office
Medium Office | OfficeMedium | CORE_BOTTOM | 10586.7262 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 0 | 0 | Weighted | Office space | 1.0244 | 5.0002 | 2.326 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Medium Office | OfficeMedium | TOPFLOOR_PLENUM | 17875.9316 | 1 | Yes | NA |  | 2183.3495 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | MIDFLOOR_PLENUM | 17875.9316 | 1 | Yes | NA |  | 2183.3495 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | FIRSTFLOOR_PLENUM | 17875.9316 | 1 | Yes | NA |  | 2183.3495 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | CORE_MID | 10586.7262 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 0 | 0 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Medium Office | OfficeMedium | CORE_TOP | 10586.7262 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 0 | 0 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_TOP_ZN_3 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_TOP_ZN_2 | 1412.8695 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74968 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_TOP_ZN_1 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_TOP_ZN_4 | 1412.7619 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_TOP | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_BOT_ZN_3 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_BOT_ZN_2 | 1412.8695 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74968 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_BOT_ZN_1 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 2209.9979
Medium Office | OfficeMedium | PERIMETER_BOT_ZN_4 | 1412.7619 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_BOT | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_MID_ZN_3 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_MID_ZN_2 | 1412.8695 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74968 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_MID_ZN_1 | 2231.787 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 1473.7932 | 702.4521 | Weighted | Office space | 1.0244 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | PERIMETER_MID_ZN_4 | 1412.7619 | 1 | Yes | 5.1 Packaged VAV with gas central heating and electric reheat | PACU_VAV_MID | 982.5288 | 468.3373 | Weighted | Office space | 1.0244 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Medium Office | OfficeMedium | Total | 53627.7949 |  |  |  |  | 14737.5013 | 7024.7364 |  |  | 1.0244 | 5.0002 | 1.0609
Medium Office | OfficeMedium | Conditioned Total | 53627.7949 |  |  |  |  | 14737.5013 | 7024.7364 |  |  | 1.0244 | 5.0002 | 1.0609
Medium Office | OfficeMedium | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Large Office
Large Office | OfficeLarge | BASEMENT | 29917.5066 | 1 | Yes | 12. SZ-CV-HW | CAV_BAS | 0 | 0 | Weighted | Office space | 1.0788 | 5.0002 | 0.44982 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Office | OfficeLarge | CORE_BOTTOM | 26867.9861 | 1 | Yes | 7. VAV with reheat | VAV_BOT WITH REHEAT | 0 | 0 | Weighted | Office space | 1.0788 | 5.0002 | 0.7497 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Office | OfficeLarge | CORE_MID | 26867.9861 | 10 | Yes | 7. VAV with reheat | VAV_MID WITH REHEAT | 0 | 0 | Weighted | Office space | 1.0788 | 5.0002 | 0.74969 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Office | OfficeLarge | CORE_TOP | 26867.9861 | 1 | Yes | 7. VAV with reheat | VAV_TOP WITH REHEAT | 0 | 0 | Weighted | Office space | 1.0788 | 5.0002 | 0.74969 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Office | OfficeLarge | PERIMETER_BOT_ZN_3 | 3373.5139 | 1 | Yes | 7. VAV with reheat | VAV_BOT WITH REHEAT | 2159.346 | 1247.536 | Weighted | Office space | 1.0788 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_BOT_ZN_2 | 2174.0925 | 1 | Yes | 7. VAV with reheat | VAV_BOT WITH REHEAT | 1439.564 | 831.6189 | Weighted | Office space | 1.0788 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_BOT_ZN_1 | 3373.6215 | 1 | Yes | 7. VAV with reheat | VAV_BOT WITH REHEAT | 2159.346 | 1247.536 | Weighted | Office space | 1.0788 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_BOT_ZN_4 | 2174.0925 | 1 | Yes | 7. VAV with reheat | VAV_BOT WITH REHEAT | 1439.564 | 831.6189 | Weighted | Office space | 1.0788 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_MID_ZN_3 | 3373.5139 | 10 | Yes | 7. VAV with reheat | VAV_MID WITH REHEAT | 2159.346 | 1247.536 | Weighted | Office space | 1.0788 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_MID_ZN_2 | 2174.0925 | 10 | Yes | 7. VAV with reheat | VAV_MID WITH REHEAT | 1439.564 | 831.6189 | Weighted | Office space | 1.0788 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_MID_ZN_1 | 3373.6215 | 10 | Yes | 7. VAV with reheat | VAV_MID WITH REHEAT | 2159.346 | 1247.536 | Weighted | Office space | 1.0788 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_MID_ZN_4 | 2174.0925 | 10 | Yes | 7. VAV with reheat | VAV_MID WITH REHEAT | 1439.564 | 831.6189 | Weighted | Office space | 1.0788 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_TOP_ZN_3 | 3373.5139 | 1 | Yes | 7. VAV with reheat | VAV_TOP WITH REHEAT | 2159.346 | 1247.536 | Weighted | Office space | 1.0788 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_TOP_ZN_2 | 2174.0925 | 1 | Yes | 7. VAV with reheat | VAV_TOP WITH REHEAT | 1439.564 | 831.6189 | Weighted | Office space | 1.0788 | 5.0002 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_TOP_ZN_1 | 3373.6215 | 1 | Yes | 7. VAV with reheat | VAV_TOP WITH REHEAT | 2159.346 | 1247.536 | Weighted | Office space | 1.0788 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | PERIMETER_TOP_ZN_4 | 2174.0925 | 1 | Yes | 7. VAV with reheat | VAV_TOP WITH REHEAT | 1439.564 | 831.6189 | Weighted | Office space | 1.0788 | 5.0002 | 0.74972 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | GROUNDFLOOR_PLENUM | 38352.9597 | 1 | Yes | NA |  | 3198.0623 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | MIDFLOOR_PLENUM | 38352.9597 | 10 | Yes | NA |  | 3198.0623 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | TOPFLOOR_PLENUM | 38352.9597 | 1 | Yes | NA |  | 3198.0623 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Large Office | OfficeLarge | DATACENTER_BOT_ZN_6 | 389.6532 | 1 | Yes | 14. WSHP (CRAC) | AIRLOOP DATACENTER BOT | 0 | 0 | Weighted | Office space | 1.38 | 5.0002 | 20.0019 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Office | OfficeLarge | DATACENTER_MID_ZN_6 | 389.6532 | 10 | Yes | 14. WSHP (CRAC) | AIRLOOP DATACENTER MID | 0 | 0 | Weighted | Office space | 1.38 | 5.0002 | 20.0019 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Office | OfficeLarge | DATACENTER_TOP_ZN_6 | 389.6532 | 1 | Yes | 14. WSHP (CRAC) | AIRLOOP DATACENTER TOP | 0 | 0 | Weighted | Office space | 1.38 | 5.0002 | 20.0019 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Office | OfficeLarge | DATACENTER_BASEMENT_ZN_6 | 8435.4532 | 1 | Yes | 14. WSHP (CRAC) | AIRLOOP DATACENTER BASEMENT | 0 | 0 | Weighted | Office space | 1.0788 | 5.0002 | 45.0044 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Office | OfficeLarge | Total | 498587.9383 |  |  |  |  | 86372.1169 | 49899.2876 |  |  | 1.0816 | 5.0002 | 1.661
Large Office | OfficeLarge | Conditioned Total | 498587.9383 |  |  |  |  | 86372.1169 | 49899.2876 |  |  | 1.0816 | 5.0002 | 1.661
Large Office | OfficeLarge | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Stand-alone Retail
Stand-alone Retail | RetailStandalone | BACK_SPACE | 4089.098 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC:1 | 4479.6123 | 0 | Weighted | Storage rooms | 0.83864 | 2.0001 | 0.74973 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Stand-alone Retail | RetailStandalone | CORE_RETAIL | 17227.4067 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC:2 | 3841.2054 | 0 | sales | Sales (except as below) | 1.7 | 15.0086 | 0.30008 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 0
Stand-alone Retail | RetailStandalone | POINT_OF_SALE | 1623.3038 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC:3 | 2042.9882 | 409.674 | sales | Sales (except as below) | 1.7 | 15.0086 | 1.9993 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 0
Stand-alone Retail | RetailStandalone | FRONT_RETAIL | 1623.3038 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC:4 | 2042.9882 | 409.674 | sales | Sales (except as below) | 1.7 | 15.0086 | 0.30008 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 0
Stand-alone Retail | RetailStandalone | FRONT_ENTRY | 129.1668 | 1 | Yes | 9. Heating and ventilation | Front_Entry Unit Heater | 262.4239 | 84.2813 | Weighted | Sales (except as below) | 1.02 | 15.0086 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 3005.9972
Stand-alone Retail | RetailStandalone | Total | 24692.279 |  |  |  |  | 12669.3256 | 903.6294 |  |  | 1.5538 | 12.8497 | 0.48467
Stand-alone Retail | RetailStandalone | Conditioned Total | 24692.279 |  |  |  |  | 12669.3256 | 903.6294 |  |  | 1.5538 | 12.8497 | 0.48467
Stand-alone Retail | RetailStandalone | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Strip Mall
Strip Mall | RetailStripmall | LGSTORE1 | 3750.0351 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_1:1 | 2974.0656 | 223.5662 | Weighted | Sales (except as below) | 2.4526 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 823.9992
Strip Mall | RetailStripmall | SMSTORE1 | 1874.9637 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_2:2 | 849.7023 | 111.7293 | Weighted | Sales (except as below) | 2.4774 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 470.9996
Strip Mall | RetailStripmall | SMSTORE2 | 1874.9637 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_3:3 | 849.7023 | 111.514 | Weighted | Sales (except as below) | 1.9 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 470.9996
Strip Mall | RetailStripmall | SMSTORE3 | 1874.9637 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_4:4 | 849.7023 | 111.514 | Weighted | Sales (except as below) | 1.9 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 470.9996
Strip Mall | RetailStripmall | SMSTORE4 | 1874.9637 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_5:5 | 849.7023 | 111.514 | Weighted | Sales (except as below) | 1.9 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 470.9996
Strip Mall | RetailStripmall | LGSTORE2 | 3750.0351 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_6:6 | 1699.5122 | 223.028 | Weighted | Sales (except as below) | 1.4752 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 823.9992
Strip Mall | RetailStripmall | SMSTORE5 | 1874.9637 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_7:7 | 849.7023 | 111.514 | Weighted | Sales (except as below) | 1.5 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 470.9996
Strip Mall | RetailStripmall | SMSTORE6 | 1874.9637 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_8:8 | 849.7023 | 111.514 | Weighted | Sales (except as below) | 1.5 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 470.9996
Strip Mall | RetailStripmall | SMSTORE7 | 1874.9637 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_9:9 | 849.7023 | 111.514 | Weighted | Sales (except as below) | 1.5 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 470.9996
Strip Mall | RetailStripmall | SMSTORE8 | 1874.9637 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_10:10 | 2124.3633 | 111.514 | Weighted | Sales (except as below) | 1.5 | 15.0086 | 0.39948 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 470.9996
Strip Mall | RetailStripmall | Total | 22499.9954 |  |  |  |  | 12746.0722 | 1339.0292 |  |  | 1.8361 | 15.0086 | 0.39948
Strip Mall | RetailStripmall | Conditioned Total | 22499.9954 |  |  |  |  | 12746.0722 | 1339.0292 |  |  | 1.8361 | 15.0086 | 0.39948
Strip Mall | RetailStripmall | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Primary School
Primary School | SchoolPrimary | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_1 | 861.112 | 301.3892 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_1 | 2281.9468 | 798.6814 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CORRIDOR_POD_1_ZN_1_FLR_1 | 2066.6688 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_1 | 129.1668 | 45.2084 | Weighted | Corridors (school) | 0.5092 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_1 | 861.112 | 301.3892 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_1 | 2281.9468 | 798.6814 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_2 | 861.112 | 301.3892 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_2 | 2281.9468 | 798.6814 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CORRIDOR_POD_2_ZN_1_FLR_1 | 2066.6688 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_2 | 129.1668 | 45.2084 | Weighted | Corridors (school) | 0.5092 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_2 | 861.112 | 301.3892 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_2 | 2281.9468 | 798.6814 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_3 | 861.112 | 301.3892 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_3 | 2281.9468 | 798.6814 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CORRIDOR_POD_3_ZN_1_FLR_1 | 2066.6688 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_3 | 129.1668 | 45.2084 | Weighted | Corridors (school) | 0.5092 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_3 | 861.112 | 300.851 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 3390.6285 | 1 | Yes | 5. Packaged VAV with reheat | VAV_POD_3 | 1506.946 | 527.4311 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | COMPUTER_CLASS_ZN_1_FLR_1 | 1743.7518 | 1 | Yes | 5. Packaged VAV with reheat | VAV_OTHER | 775.0008 | 271.2503 | Weighted | Classrooms (ages 5-8) | 1.4 | 24.974 | 1.8581 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | MAIN_CORRIDOR_ZN_1_FLR_1 | 5877.0894 | 1 | Yes | 5. Packaged VAV with reheat | VAV_OTHER | 387.5004 | 135.6251 | Weighted | Corridors (school) | 0.5092 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | LOBBY_ZN_1_FLR_1 | 1840.6269 | 1 | Yes | 5. Packaged VAV with reheat | VAV_OTHER | 818.0564 | 286.3197 | lobby - all other | Main entry lobbies (office bldgs) | 1.3 | 10.0003 | 0.37161 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 9204.9913
Primary School | SchoolPrimary | MECH_ZN_1_FLR_1 | 2712.5028 | 1 | Yes | 5. Packaged VAV with reheat | VAV_OTHER | 0 | 0 | electrical/mechanical | No requirement | 1.5 | 1.5001 | 0.92903 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | BATH_ZN_1_FLR_1 | 2045.141 | 1 | Yes | 5. Packaged VAV with reheat | VAV_OTHER | 430.556 | 150.6946 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.37161 | 0 | 0 | 0 | 0 | 0.2901 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | OFFICES_ZN_1_FLR_1 | 4746.8799 | 1 | Yes | 5. Packaged VAV with reheat | VAV_OTHER | 1808.3352 | 632.9173 | Weighted | Office space | 1.1 | 5.0002 | 1.0034 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | GYM_ZN_1_FLR_1 | 3842.7123 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_2:5 | 731.9452 | 256.1808 | Weighted | Gym, stadium (play area) | 1.24 | 29.9688 | 0.46452 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | KITCHEN_ZN_1_FLR_1 | 1808.3352 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_1:6 | 344.4448 | 120.5557 | kitchen | Kitchen | 1.2 | 14.9362 | 151.6884 | 12.3518 | 15 | 0.4 | 0 | 2.7653 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | CAFETERIA_ZN_1_FLR_1 | 3390.6285 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_2:7 | 1550.0016 | 542.5006 | dining - cafeteria/fast food | Cafeteria / fast food dining | 0.9 | 99.8958 | 2.3588 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 4294.7961 | 1 | Yes | 5. Packaged VAV with reheat | VAV_OTHER | 1722.224 | 602.7784 | Weighted | Libraries | 1.55 | 10.0003 | 1.3935 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Primary School | SchoolPrimary | Total | 73958.7569 |  |  |  |  | 27038.9168 | 9462.975 |  |  | 1.1952 | 21.2593 | 4.8126
Primary School | SchoolPrimary | Conditioned Total | 73958.7569 |  |  |  |  | 27038.9168 | 9462.975 |  |  | 1.1952 | 21.2593 | 4.8126
Primary School | SchoolPrimary | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Secondary School
Secondary School | SchoolSecondary | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORRIDOR_POD_1_ZN_1_FLR_1 | 3444.448 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 215.278 | 75.3473 | Weighted | Corridors (school) | 0.51262 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORRIDOR_POD_1_ZN_1_FLR_2 | 3444.448 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 215.278 | 75.3473 | Weighted | Corridors (school) | 0.51262 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_1 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORRIDOR_POD_2_ZN_1_FLR_1 | 3444.448 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 215.278 | 75.3473 | Weighted | Corridors (school) | 0.51262 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORRIDOR_POD_2_ZN_1_FLR_2 | 3444.448 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 215.278 | 75.3473 | Weighted | Corridors (school) | 0.51262 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_2 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 1.8581 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORRIDOR_POD_3_ZN_1_FLR_1 | 3444.448 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 215.278 | 75.3473 | Weighted | Corridors (school) | 0.51262 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORRIDOR_POD_3_ZN_1_FLR_2 | 3444.448 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 215.278 | 75.3473 | Weighted | Corridors (school) | 0.51262 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 1065.6261 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 861.112 | 301.3892 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 2281.9468 | 798.5737 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 5134.3803 | 1 | Yes | 7. VAV with reheat | VAV_POD_3 | 2281.9468 | 798.6814 | Weighted | Classrooms (age 9 plus) | 1.4 | 35.0578 | 1.8581 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MAIN_CORRIDOR_ZN_1_FLR_1 | 12270.846 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 1506.946 | 527.4311 | Weighted | Corridors (school) | 0.51262 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MAIN_CORRIDOR_ZN_1_FLR_2 | 12270.846 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 1506.946 | 527.4311 | Weighted | Corridors (school) | 0.51262 | 5.0002 | 0.37161 | 0 | 0 | 0.1 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | LOBBY_ZN_1_FLR_1 | 2260.419 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 645.834 | 226.0419 | lobby - all other | Main entry lobbies (office bldgs) | 1.3 | 10.0003 | 0.37161 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 15160.9857
Secondary School | SchoolSecondary | LOBBY_ZN_1_FLR_2 | 2260.419 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 645.834 | 226.0419 | lobby - all other | Main entry lobbies (office bldgs) | 1.3 | 10.0003 | 0.37161 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | BATHROOMS_ZN_1_FLR_1 | 2260.419 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 775.0008 | 271.2503 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.37161 | 0 | 0 | 0 | 0 | 0.26247 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | BATHROOMS_ZN_1_FLR_2 | 2260.419 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 775.0008 | 271.2503 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.37161 | 0 | 0 | 0 | 0 | 0.26247 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | OFFICES_ZN_1_FLR_1 | 5726.3948 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 2238.8912 | 783.6119 | Weighted | Office space | 1.1 | 5.0002 | 1.0034 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | OFFICES_ZN_1_FLR_2 | 5726.3948 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 2238.8912 | 783.6119 | Weighted | Office space | 1.1 | 5.0002 | 1.0034 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | GYM_ZN_1_FLR_1 | 21269.4664 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_1:5 | 0 | 0 | Weighted | Gym, stadium (play area) | 1.24 | 29.9688 | 0.46452 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | AUX_GYM_ZN_1_FLR_1 | 13433.3472 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_2:6 | 6544.4512 | 2290.5579 | Weighted | Gym, stadium (play area) | 1.24 | 29.9688 | 0.46452 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | AUDITORIUM_ZN_1_FLR_1 | 10634.7332 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_3:7 | 3272.2256 | 1145.279 | audience seating - auditorium | Auditorium seating area | 0.9 | 149.8438 | 0.46452 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | KITCHEN_ZN_1_FLR_1 | 2325.0024 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_4:8 | 387.5004 | 135.6251 | kitchen | Kitchen | 1.2 | 20.0222 | 177.4001 | 14.488 | 15 | 0.4 | 0 | 2.5791 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 9041.676 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 2540.2804 | 889.0981 | Weighted | Libraries | 1.55 | 10.0003 | 0.92903 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | CAFETERIA_ZN_1_FLR_1 | 6716.6736 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_5:9 | 2152.78 | 753.473 | dining - cafeteria/fast food | Cafeteria / fast food dining | 0.9 | 99.8958 | 7.147 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | MECH_ZN_1_FLR_1 | 3681.2538 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 0 | 0 | electrical/mechanical | No requirement | 1.5 | 1.5082 | 6.615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Secondary School | SchoolSecondary | MECH_ZN_1_FLR_2 | 3681.2538 | 1 | Yes | 7. VAV with reheat | VAV_OTHER | 0 | 0 | electrical/mechanical | No requirement | 1.5 | 1.5082 | 0.37161 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Secondary School | SchoolSecondary | Total | 210886.3288 |  |  |  |  | 64238.9552 | 22483.6343 |  |  | 1.1209 | 30.3605 | 2.9682
Secondary School | SchoolSecondary | Conditioned Total | 210886.3288 |  |  |  |  | 64238.9552 | 22483.6343 |  |  | 1.1209 | 30.3605 | 2.9682
Secondary School | SchoolSecondary | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Outpatient Healthcare
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 ANESTHESIA | 107.9619 | 1 | Yes | 7. VAV with reheat | AHU-1 | 89.9862 | 24.0035 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 2.0002 | 0 | 15 | 0 | 0 | 1.3738 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 BIO HAZ | 55.9723 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 CAFE | 420.0074 | 1 | Yes | 7. VAV with reheat | AHU-1 | 199.9933 | 96.014 | dining - cafeteria/fast food | Cafeteria / fast food dining | 0.9 | 99.8958 | 0.99964 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 CLEAN | 126.0453 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 2.0002 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 CLEAN WORK | 165.0106 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 2.0002 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 DICTATION | 126.0453 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 DRESSING ROOM | 44.9931 | 1 | Yes | 7. VAV with reheat | AHU-1 | 89.9862 | 24.9722 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 ELECTRICAL ROOM | 97.9515 | 1 | Yes | 7. VAV with reheat | AHU-1 | 69.9654 | 0 | exam/treatment | No requirement | 1.5 | 1.4999 | 5 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 ELEVATOR PUMP ROOM | 90.955 | 1 | Yes | 7. VAV with reheat | AHU-1 | 199.9933 | 0 | exam/treatment | No requirement | 1.5 | 1.4999 | 155.5909 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 HUMID | 54.0348 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 IT HALL | 140.0383 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 IT ROOM | 112.0522 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 LOBBY | 622.0458 | 1 | Yes | 7. VAV with reheat | AHU-1 | 220.0141 | 96.014 | lobby - all other | Main entry lobbies (office bldgs) | 1.3 | 10.0003 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 LOBBY HALL | 240.035 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 LOBBY TOILET | 54.0348 | 1 | Yes | 7. VAV with reheat | AHU-1 | 59.9549 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.5685 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 LOCKER ROOM | 660.0423 | 1 | Yes | 7. VAV with reheat | AHU-1 | 220.0141 | 59.9549 | lounge/breakroom - healthcare facility | Conference / meeting | 0.8 | 15.0086 | 2.9998 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 LOCKER ROOM HALL | 496.0005 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 LOUNGE | 360.0525 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | lounge/breakroom - healthcare facility | Conference / meeting | 0.8 | 15.0086 | 2.9998 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 MED GAS | 55.9723 | 1 | Yes | 7. VAV with reheat | AHU-1 | 150.0488 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 MRI CONTROL ROOM | 168.0245 | 1 | Yes | 7. VAV with reheat | AHU-1 | 50.0521 | 0 | imaging | Medical procedure | 0.4 | 20.0222 | 10.0001 | 0 | 15 | 0 | 0 | 2.0177 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 MRI HALL | 147.0349 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 MRI ROOM | 440.0282 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | imaging | Medical procedure | 0.4 | 20.0222 | 10.0001 | 0 | 15 | 0 | 0 | 2.0224 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 MRI TOILET | 54.0348 | 1 | Yes | 7. VAV with reheat | AHU-1 | 59.9549 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.5685 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 NOURISHMENT | 182.0175 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | nurses station | Lobbies | 1 | 15.0086 | 2.0002 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 NURSE HALL | 496.0005 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 NURSE JANITOR | 54.0348 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 NURSE STATION | 261.0246 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | nurses station | Lobbies | 1 | 15.0086 | 2.0002 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 NURSE TOILET | 54.0348 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.5685 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 OFFICE | 482.9762 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 OPERATING ROOM 1 | 460.0491 | 1 | Yes | 7. VAV with reheat | AHU-1 | 430.0178 | 96.014 | operating room | NA | 2.2 | 20.0222 | 10.996 | 0.64984 |  |  |  | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 OPERATING ROOM 2 | 479.9623 | 1 | Yes | 7. VAV with reheat | AHU-1 | 240.035 | 72.1181 | operating room | NA | 2.2 | 20.0222 | 10.996 | 0.64996 |  |  |  | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 OPERATING ROOM 3 | 475.9797 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | operating room | NA | 2.2 | 20.0222 | 10.996 | 0.64994 |  |  |  | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 PACU | 107.9619 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | recovery | NA | 0.8 | 20.0222 | 2.9998 | 0 |  |  |  | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 PRE-OP HALL | 527.9693 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 PRE-OP ROOM 1 | 189.0141 | 1 | Yes | 7. VAV with reheat | AHU-1 | 40.0417 | 0 | patient room | NA | 0.7 | 10.0003 | 2.0002 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 PRE-OP ROOM 2 | 337.9865 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | patient room | NA | 0.7 | 10.0003 | 2.0002 | 0 |  |  |  | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 PRE-OP TOILET | 54.0348 | 1 | Yes | 7. VAV with reheat | AHU-1 | 59.9549 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.5685 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 PROCEDURE ROOM | 285.0281 | 1 | Yes | 7. VAV with reheat | AHU-1 | 189.9828 | 59.9549 | exam/treatment | NA | 1.5 | 20.0222 | 2.9998 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 RECEPTION | 509.0248 | 1 | Yes | 7. VAV with reheat | AHU-1 | 130.0279 | 35.9514 | lobby - all other | Reception areas | 1.3 | 29.9688 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 RECEPTION HALL | 127.9828 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 RECOVERY ROOM | 540.0249 | 1 | Yes | 7. VAV with reheat | AHU-1 | 450.0387 | 96.014 | recovery | NA | 0.8 | 20.0222 | 2.9998 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 SCHEDULING | 119.0487 | 1 | Yes | 7. VAV with reheat | AHU-1 | 69.9654 | 7.9653 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 SCRUB | 83.9584 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 SOIL | 126.0453 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 2.0002 | 0 | 15 | 0 | 0 | 1.681 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 SOIL HOLD | 55.9723 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 2.0002 | 0 | 15 | 0 | 0 | 1.5142 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 SOIL WORK | 179.9724 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 2.0002 | 0 | 15 | 0 | 0 | 1.6483 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 STEP DOWN | 299.9899 | 1 | Yes | 7. VAV with reheat | AHU-1 | 369.9552 | 72.0105 | recovery | NA | 0.8 | 20.0222 | 2.9998 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 STERILE HALL | 616.018 | 1 | Yes | 7. VAV with reheat | AHU-1 | 79.9758 | 24.0035 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 STERILE STORAGE | 396.0039 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | Weighted | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 STORAGE | 919.9905 | 1 | Yes | 7. VAV with reheat | AHU-1 | 630.0111 | 89.9862 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 SUB-STERILE | 196.0106 | 1 | Yes | 7. VAV with reheat | AHU-1 | 140.0383 | 32.0764 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 UTILITY HALL | 255.9655 | 1 | Yes | 7. VAV with reheat | AHU-1 | 159.9516 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 UTILITY JANITOR | 41.9792 | 1 | Yes | 7. VAV with reheat | AHU-1 | 0 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 UTILITY ROOM | 360.0525 | 1 | Yes | 7. VAV with reheat | AHU-1 | 179.9724 | 24.0035 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 1 VESTIBULE | 72.0105 | 1 | Yes | 7. VAV with reheat | AHU-1 | 79.9758 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 2512.9976
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 CONFERENCE | 336.049 | 1 | Yes | 7. VAV with reheat | AHU-2 | 399.9865 | 96.014 | conference/meeting/multipurpose | Conference / meeting | 1.3 | 49.9479 | 0.99964 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 CONFERENCE TOILET | 64.0452 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.6542 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 DICTATION | 69.9654 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 1 | 360.0525 | 1 | Yes | 7. VAV with reheat | AHU-2 | 420.0074 | 96.014 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 2 | 540.0249 | 1 | Yes | 7. VAV with reheat | AHU-2 | 179.9724 | 40.0417 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 3 | 719.9973 | 1 | Yes | 7. VAV with reheat | AHU-2 | 240.035 | 64.0452 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 4 | 83.9584 | 1 | Yes | 7. VAV with reheat | AHU-2 | 69.9654 | 24.0035 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 5 | 350.042 | 1 | Yes | 7. VAV with reheat | AHU-2 | 250.0454 | 64.0452 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 6 | 224.9655 | 1 | Yes | 7. VAV with reheat | AHU-2 | 150.0488 | 44.9931 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 7 | 792.0078 | 1 | Yes | 7. VAV with reheat | AHU-2 | 240.035 | 59.9549 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 8 | 269.9586 | 1 | Yes | 7. VAV with reheat | AHU-2 | 179.9724 | 59.9549 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM 9 | 396.0039 | 1 | Yes | 7. VAV with reheat | AHU-2 | 120.0175 | 30.0313 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM HALL 1 | 179.9724 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM HALL 2 | 179.9724 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM HALL 3 | 179.9724 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM HALL 4 | 197.9481 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM HALL 5 | 197.9481 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 EXAM HALL 6 | 197.9481 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 JANITOR | 62.9688 | 1 | Yes | 7. VAV with reheat | AHU-2 | 159.9516 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 LOUNGE | 79.9758 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | lounge/breakroom - healthcare facility | Conference / meeting | 0.8 | 15.0086 | 2.9998 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 NURSE STATION 1 | 150.0488 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | nurses station | Lobbies | 1 | 15.0086 | 2.0002 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 NURSE STATION 2 | 179.9724 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | nurses station | Lobbies | 1 | 15.0086 | 2.0002 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 OFFICE | 560.0457 | 1 | Yes | 7. VAV with reheat | AHU-2 | 399.9865 | 96.1216 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 OFFICE HALL | 444.0109 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 RECEPTION | 984.0357 | 1 | Yes | 7. VAV with reheat | AHU-2 | 489.9727 | 179.9724 | lobby - all other | Reception areas | 1.3 | 29.9688 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 RECEPTION HALL | 564.0284 | 1 | Yes | 7. VAV with reheat | AHU-2 | 69.9654 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 RECEPTION TOILET | 126.0453 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.681 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 SCHEDULING 1 | 323.9934 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 SCHEDULING 2 | 341.9691 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 STORAGE 1 | 55.9723 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 STORAGE 2 | 120.0175 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 STORAGE 3 | 144.021 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 UTILITY | 126.0453 | 1 | Yes | 7. VAV with reheat | AHU-2 | 89.9862 | 24.0035 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 WORK | 1690.0399 | 1 | Yes | 7. VAV with reheat | AHU-2 | 259.9482 | 59.9549 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 0.90862 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 WORK HALL | 833.987 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 WORK TOILET | 54.0348 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.5685 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 2 X-RAY | 899.9697 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | imaging | Medical procedure | 0.4 | 20.0222 | 10.0001 | 0 | 15 | 0 | 0 | 2.0012 | 0 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 DRESSING ROOM | 41.9792 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 ELEVATOR HALL | 369.9552 | 1 | Yes | 7. VAV with reheat | AHU-2 | 40.0417 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 HUMID | 107.9619 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 JANITOR | 62.9688 | 1 | Yes | 7. VAV with reheat | AHU-2 | 159.9516 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 LOCKER | 120.0175 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | lounge/breakroom - healthcare facility | Conference / meeting | 0.8 | 15.0086 | 2.9998 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 LOUNGE | 758.9626 | 1 | Yes | 7. VAV with reheat | AHU-2 | 230.0245 | 59.9549 | lounge/breakroom - healthcare facility | Conference / meeting | 0.8 | 15.0086 | 2.9998 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 LOUNGE TOILET | 192.028 | 1 | Yes | 7. VAV with reheat | AHU-2 | 120.0175 | 44.9931 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.6551 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 MECHANICAL | 350.042 | 1 | Yes | 7. VAV with reheat | AHU-2 | 250.0454 | 64.0452 | exam/treatment | No requirement | 1.5 | 1.4999 | 5 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 MECHANICAL HALL | 299.9899 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 OFFICE | 3035.958 | 1 | Yes | 7. VAV with reheat | AHU-2 | 740.0181 | 210.0037 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 OFFICE HALL | 833.987 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 OFFICE TOILET | 54.0348 | 1 | Yes | 7. VAV with reheat | AHU-2 | 59.9549 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.5685 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 PHYSICAL THERAPY 1 | 1299.9562 | 1 | Yes | 7. VAV with reheat | AHU-2 | 850.0252 | 312.0455 | physical therapy | Physical therapy | 0.9 | 20.0222 | 1.5004 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 PHYSICAL THERAPY 2 | 592.0145 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | physical therapy | Physical therapy | 0.9 | 20.0222 | 1.5004 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 PHYSICAL THERAPY TOILET | 83.9584 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0.40041 | 0 | 0 | 0 | 0 | 1.7666 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 STORAGE 1 | 107.9619 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 STORAGE 2 | 83.9584 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 TREATMENT | 475.9797 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | exam/treatment | Medical procedure | 1.5 | 20.0222 | 1.1 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 UNDEVELOPED 1 | 2267.9537 | 1 | Yes | 7. VAV with reheat | AHU-2 | 719.9973 | 275.9864 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 1.1 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 UNDEVELOPED 2 | 1151.9526 | 1 | Yes | 7. VAV with reheat | AHU-2 | 560.0457 | 144.021 | storage 50 to 1000 sf - hospital | Storage rooms | 0.9 | 2.0001 | 1.1 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 UTILITY | 216.0315 | 1 | Yes | 7. VAV with reheat | AHU-2 | 0 | 0 | electrical/mechanical | Storage rooms | 1.5 | 2.0001 | 0.10034 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | FLOOR 3 WORK | 574.0388 | 1 | Yes | 7. VAV with reheat | AHU-2 | 409.997 | 96.1216 | office - enclosed <= 250 sf | Office space | 1.1 | 5.0002 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | NE STAIR | 168.0245 | 1 | Yes | 7. VAV with reheat | AHU-2 | 1050.0184 | 129.4897 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | NW ELEVATOR | 140.0383 | 1 | Yes | 7. VAV with reheat | AHU-2 | 809.9835 | 0 | Weighted | No requirement | 0.95728 | 1.4999 | 0.40041 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | NW STAIR | 192.028 | 1 | Yes | 7. VAV with reheat | AHU-2 | 1199.9596 | 120.0175 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | SW STAIR | 96.014 | 1 | Yes | 7. VAV with reheat | AHU-2 | 599.9798 | 11.9479 | Weighted | Corridors (public spaces) | 0.95728 | 5.0002 | 0.40041 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Outpatient Healthcare | OutPatientHealthCare | Total | 40945.9832 |  |  |  |  | 16719.9964 | 3319.1562 |  |  | 1.0802 | 11.5839 | 2.1309
Outpatient Healthcare | OutPatientHealthCare | Conditioned Total | 40945.9832 |  |  |  |  | 16719.9964 | 3319.1562 |  |  | 1.0802 | 11.5839 | 2.1309
Outpatient Healthcare | OutPatientHealthCare | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Hospital
Hospital | Hospital | BASEMENT | 40249.9895 | 1 | Yes | 7. VAV with reheat | VAV_1 | 0 | 0 | Weighted | Office space | 1.0758 | 2.4994 | 0.74973 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | ER_EXAM1_MULT4_FLR_1 | 299.9899 | 4 | Yes | 7. VAV with reheat | VAV_ER | 280.0767 | 0 | exam/treatment | Procedure | 1.5 | 19.9792 | 1.4995 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | ER_TRAUMA1_FLR_1 | 299.9899 | 1 | Yes | 7. VAV with reheat | VAV_ER | 490.0804 | 0 | exam/treatment | Procedure | 1.5 | 19.9792 | 3.9985 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | ER_EXAM3_MULT4_FLR_1 | 299.9899 | 4 | Yes | 7. VAV with reheat | VAV_ER | 210.0037 | 0 | exam/treatment | Procedure | 1.5 | 19.9792 | 1.4995 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | ER_TRAUMA2_FLR_1 | 299.9899 | 1 | Yes | 7. VAV with reheat | VAV_ER | 490.0804 | 0 | exam/treatment | Procedure | 1.5 | 19.9792 | 3.9985 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | ER_TRIAGE_MULT4_FLR_1 | 299.9899 | 4 | Yes | 7. VAV with reheat | VAV_ER | 280.0767 | 0 | exam/treatment | Procedure | 1.5 | 19.9792 | 1.9999 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OFFICE1_MULT4_FLR_1 | 150.0488 | 5 | Yes | 7. VAV with reheat | VAV_1 | 140.0383 | 31.8611 | office - enclosed <= 250 sf | Office space | 1.1 | 7.001 | 1.1 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | LOBBY_RECORDS_FLR_1 | 15874.7074 | 1 | Yes | 7. VAV with reheat | VAV_1 | 4410.8309 | 673.8201 | Weighted | Lobbies | 1.28 | 1.3329 | 0.10034 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | CORRIDOR_FLR_1 | 6124.982 | 1 | Yes | 7. VAV with reheat | VAV_1 | 980.2684 | 0 | Weighted | Corridors (public spaces) | 0.96551 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | ER_NURSESTN_LOBBY_FLR_1 | 13299.9825 | 1 | Yes | 7. VAV with reheat | VAV_1 | 1190.2721 | 327.2226 | Weighted | Reception areas | 1.12 | 1.3329 | 1.3592 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OR1_FLR_2 | 599.9798 | 1 | Yes | 7. VAV with reheat | VAV_OR | 700.1917 | 0 | operating room | Operating/Surgical Cystoscopic Rooms | 2.2 | 4.9975 | 3.9985 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OR2_MULT5_FLR_2 | 599.9798 | 5 | Yes | 7. VAV with reheat | VAV_OR | 280.0767 | 0 | operating room | Operating/Surgical Cystoscopic Rooms | 2.2 | 4.9975 | 3.9985 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OR3_FLR_2 | 599.9798 | 1 | Yes | 7. VAV with reheat | VAV_OR | 420.115 | 0 | operating room | Operating/Surgical Cystoscopic Rooms | 2.2 | 4.9975 | 3.9985 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OR4_FLR_2 | 2400.0268 | 1 | Yes | 7. VAV with reheat | VAV_OR | 0 | 0 | operating room | Operating/Surgical Cystoscopic Rooms | 2.2 | 4.9975 | 3.9985 | 0 | 0 | 0.5 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | IC_PATROOM1_MULT5_FLR_2 | 224.9655 | 5 | Yes | 7. VAV with reheat | VAV_ICU | 210.0037 | 52.8507 | recovery | Critical and Intensive Care | 0.8 | 4.9975 | 2.9989 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | IC_PATROOM2_FLR_2 | 299.9899 | 1 | Yes | 7. VAV with reheat | VAV_ICU | 490.0804 | 123.2467 | recovery | Critical and Intensive Care | 0.8 | 4.9975 | 2.9989 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | IC_PATROOM3_MULT6_FLR_2 | 224.9655 | 6 | Yes | 7. VAV with reheat | VAV_ICU | 210.0037 | 52.8507 | recovery | Critical and Intensive Care | 0.8 | 4.9975 | 2.9989 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | ICU_FLR_2 | 6651.6596 | 1 | Yes | 7. VAV with reheat | VAV_ICU | 2310.7941 | 269.5281 | recovery | Critical and Intensive Care | 0.8 | 4.9975 | 2.9989 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | ICU_NURSESTN_LOBBY_FLR_2 | 7198.5734 | 1 | Yes | 7. VAV with reheat | VAV_1 | 0 | 0 | Weighted | Reception areas | 1 | 1.3329 | 1.9993 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | CORRIDOR_FLR_2 | 6124.982 | 1 | Yes | 7. VAV with reheat | VAV_1 | 980.2684 | 0 | Weighted | Corridors (public spaces) | 0.96551 | 0.9996 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OR_NURSESTN_LOBBY_FLR_2 | 10899.9557 | 1 | Yes | 7. VAV with reheat | VAV_1 | 1960.5367 | 385.0247 | Weighted | Reception areas | 1.18 | 1.3329 | 1.0396 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM1_MULT10_FLR_3 | 224.9655 | 10 | Yes | 7. VAV with reheat | VAV_PATRMS | 210.0037 | 52.8507 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM2_FLR_3 | 375.0143 | 1 | Yes | 7. VAV with reheat | VAV_PATRMS | 560.1534 | 140.7918 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM3_MULT10_FLR_3 | 217.5384 | 10 | Yes | 7. VAV with reheat | VAV_PATRMS | 203.1148 | 51.0209 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM4_FLR_3 | 375.0143 | 1 | Yes | 7. VAV with reheat | VAV_PATRMS | 560.1534 | 140.7918 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM5_MULT10_FLR_3 | 224.9655 | 10 | Yes | 7. VAV with reheat | VAV_PATRMS | 210.0037 | 52.8507 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PHYSTHERAPY_FLR_3 | 5249.9846 | 1 | Yes | 7. VAV with reheat | VAV_2 | 0 | 0 | physical therapy | Physical therapy | 0.9 | 4.9975 | 1.4995 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM6_FLR_3 | 299.9899 | 1 | Yes | 7. VAV with reheat | VAV_PATRMS | 490.0804 | 123.2467 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM7_MULT10_FLR_3 | 217.5384 | 10 | Yes | 7. VAV with reheat | VAV_PATRMS | 203.1148 | 51.0209 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM8_FLR_3 | 299.9899 | 1 | Yes | 7. VAV with reheat | VAV_PATRMS | 490.0804 | 123.2467 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | NURSESTN_LOBBY_FLR_3 | 9749.9406 | 1 | Yes | 7. VAV with reheat | VAV_2 | 0 | 0 | Weighted | Reception areas | 1.18 | 1.3329 | 1.0396 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | LAB_FLR_3 | 2849.9578 | 1 | Yes | 7. VAV with reheat | VAV_LABS | 0 | 0 | laboratory | Science laboratories | 1.4 | 4.9975 | 3.9985 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | CORRIDOR_SE_FLR_3 | 6100.0098 | 1 | Yes | 7. VAV with reheat | VAV_2 | 490.0804 | 0 | Weighted | Corridors (public spaces) | 0.96551 | 0.9996 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | CORRIDOR_NW_FLR_3 | 6100.0098 | 1 | Yes | 7. VAV with reheat | VAV_2 | 490.0804 | 0 | Weighted | Corridors (public spaces) | 0.96551 | 0.9996 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM1_MULT10_FLR_4 | 224.9655 | 10 | Yes | 7. VAV with reheat | VAV_PATRMS | 210.0037 | 52.8507 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM2_FLR_4 | 375.0143 | 1 | Yes | 7. VAV with reheat | VAV_PATRMS | 560.1534 | 140.7918 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM3_MULT10_FLR_4 | 217.5384 | 10 | Yes | 7. VAV with reheat | VAV_PATRMS | 203.1148 | 51.0209 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM4_FLR_4 | 375.0143 | 1 | Yes | 7. VAV with reheat | VAV_PATRMS | 560.1534 | 140.7918 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM5_MULT10_FLR_4 | 224.9655 | 10 | Yes | 7. VAV with reheat | VAV_PATRMS | 210.0037 | 52.8507 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | RADIOLOGY_FLR_4 | 5249.9846 | 1 | Yes | 7. VAV with reheat | VAV_2 | 0 | 0 | imaging | Medical procedure | 0.4 | 4.9975 | 10 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM6_FLR_4 | 299.9899 | 1 | Yes | 7. VAV with reheat | VAV_PATRMS | 490.0804 | 123.2467 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM7_MULT10_FLR_4 | 217.5384 | 10 | Yes | 7. VAV with reheat | VAV_PATRMS | 203.1148 | 51.0209 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | PATROOM8_FLR_4 | 299.9899 | 1 | Yes | 7. VAV with reheat | VAV_PATRMS | 490.0804 | 123.2467 | patient room | Patient Room | 0.7 | 4.9975 | 1.9993 | 0 | 0 | 0.33333 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | NURSESTN_LOBBY_FLR_4 | 9749.9406 | 1 | Yes | 7. VAV with reheat | VAV_2 | 0 | 0 | Weighted | Reception areas | 1.18 | 1.3329 | 1.0396 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | LAB_FLR_4 | 2849.9578 | 1 | Yes | 7. VAV with reheat | VAV_LABS | 0 | 0 | laboratory | Science laboratories | 1.4 | 4.9975 | 3.9985 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | CORRIDOR_SE_FLR_4 | 6100.0098 | 1 | Yes | 7. VAV with reheat | VAV_2 | 490.0804 | 0 | Weighted | Corridors (public spaces) | 0.96551 | 0.9996 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | CORRIDOR_NW_FLR_4 | 6100.0098 | 1 | Yes | 7. VAV with reheat | VAV_2 | 490.0804 | 0 | Weighted | Corridors (public spaces) | 0.96551 | 0.9996 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | DINING_FLR_5 | 7499.9626 | 1 | Yes | 7. VAV with reheat | VAV_2 | 2450.6171 | 385.0247 | dining - cafeteria/fast food | Cafeteria / fast food dining | 0.9 | 10.0003 | 0.99964 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | NURSESTN_LOBBY_FLR_5 | 11199.9456 | 1 | Yes | 7. VAV with reheat | VAV_2 | 1120.3067 | 0 | Weighted | Reception areas | 1.18 | 1.3329 | 1.0396 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | KITCHEN_FLR_5 | 9999.986 | 1 | Yes | 12. SZ-CV-HW | CAV_KITCHEN | 2800.7668 | 0 | kitchen | Kitchen | 1.2 | 4.9975 | 22.7227 | 1.393 | 15 | 0.4 | 0 | 0.80094 | 0.20182 | 0 | 0
Hospital | Hospital | OFFICE1_FLR_5 | 750.2438 | 1 | Yes | 7. VAV with reheat | VAV_2 | 770.2647 | 193.6426 | Weighted | Office space | 1.1 | 6.9957 | 0.99964 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OFFICE2_MULT5_FLR_5 | 750.0286 | 5 | Yes | 7. VAV with reheat | VAV_2 | 350.042 | 88.0487 | office - enclosed <= 250 sf | Office space | 1.1 | 6.9957 | 0.99964 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OFFICE3_FLR_5 | 750.0286 | 1 | Yes | 7. VAV with reheat | VAV_2 | 770.157 | 193.6426 | office - enclosed <= 250 sf | Office space | 1.1 | 6.9957 | 0.99964 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | OFFICE4_MULT6_FLR_5 | 150.0488 | 6 | Yes | 7. VAV with reheat | VAV_2 | 140.0383 | 31.8611 | office - enclosed <= 250 sf | Office space | 1.1 | 7.001 | 0.99964 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | CORRIDOR_FLR_5 | 5400.0334 | 1 | Yes | 7. VAV with reheat | VAV_2 | 840.23 | 0 | Weighted | Corridors (public spaces) | 0.96551 | 0.9996 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Hospital | Hospital | Total | 241500.7979 |  |  |  |  | 55944.7244 | 9133.1691 |  |  | 1.0732 | 3.277 | 2.2202
Hospital | Hospital | Conditioned Total | 241500.7979 |  |  |  |  | 55944.7244 | 9133.1691 |  |  | 1.0732 | 3.277 | 2.2202
Hospital | Hospital | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Small Hotel
Small Hotel | HotelSmall | REARSTAIRSFLR1 | 216.0315 | 1 | Yes | 10. Heating and ventilation | RearStairsFlr1 Unit Heater | 385.0247 | 0 | stairwell | Corridors (public spaces) | 0.6 | 4.9975 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | CORRIDORFLR1 | 1620.0746 | 1 | Yes | 1.1 PTAC with electric heating | CorridorFlr1 PTAC | 351.9795 | 105.7015 | corridor - all other | Corridors (public spaces) | 0.49999 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 1939.9982
Small Hotel | HotelSmall | REARSTORAGEFLR1 | 216.0315 | 1 | No | NA |  | 385.0247 | 0 | Weighted |  | 0.8 | 1.9992 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTLOUNGEFLR1 | 1755.1615 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | SAC_FRONTLOUNGE | 1012.0219 | 159.6286 | lobby - all other | Lobbies/prefunction (hotel, motel, resort, dorm) | 1.3 | 30.1634 | 2.4211 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | RESTROOMFLR1 | 351.0108 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | SAC_RESTROOM | 143.0522 | 0 | restroom - all other | Restroom | 0.9 | 5.0002 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | MEETINGROOMFLR1 | 864.0183 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | SAC_MEETINGROOM | 351.9795 | 53.066 | conference/meeting/multipurpose | Conference / meeting | 1.3 | 49.6808 | 0.57414 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | MECHANICALROOMFLR1 | 351.0108 | 1 | Yes | 10. Heating and ventilation | MechanicalRoomFlr1 Unit Heater | 143.0522 | 0 | electrical/mechanical | No requirement | 1.5 | 1.5013 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM101 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 101 PTAC | 143.0522 | 17.6528 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM102 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 102 PTAC | 143.0522 | 17.6528 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM103 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 103 PTAC | 143.0522 | 17.6528 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM104 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 104 PTAC | 143.0522 | 17.6528 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM105 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 105 PTAC | 143.0522 | 17.6528 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | EMPLOYEELOUNGEFLR1 | 351.0108 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | SAC_EMPLOYEELOUNGE | 143.0522 | 17.6528 | lounge/breakroom - all other | Conference / meeting | 1.2 | 51.3277 | 1.9983 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | LAUNDRYROOMFLR1 | 1053.0323 | 1 | No | NA |  | 429.0491 | 53.066 | laundry/washing |  | 0.6 | 10.0003 | 40.6506 | 3.5374 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | ELEVATORCOREFLR1 | 161.9967 | 1 | No | NA |  | 65.9827 | 0 | PNNL Elevator Core |  | 0 | 1.4999 | 100.9154 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | EXERCISECENTERFLR1 | 351.0108 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | SAC_EXERCISECENTER | 143.0522 | 17.6528 | gymnasium exercise area | Health club/weight rooms | 0.9 | 19.9363 | 1.7271 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTOFFICEFLR1 | 1404.0431 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | SAC_FRONTOFFICE | 571.9936 | 70.7188 | Weighted | Office space | 1.1 | 7.1245 | 1.2802 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTSTAIRSFLR1 | 216.0315 | 1 | Yes | 10. Heating and ventilation | FrontStairsFlr1 Unit Heater | 385.0247 | 0 | stairwell | Corridors (public spaces) | 0.6 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTSTORAGEFLR1 | 134.9793 | 1 | No | NA |  | 55.0035 | 0 | Weighted |  | 0.8 | 2.0001 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | REARSTAIRSFLR2 | 216.0315 | 1 | Yes | 10. Heating and ventilation | RearStairsFlr2 Unit Heater | 315.0594 | 0 | stairwell | Corridors (public spaces) | 0.6 | 4.9975 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | CORRIDORFLR2 | 1350.0083 | 1 | Yes | 1.1 PTAC with electric heating | CorridorFlr2 PTAC | 197.9481 | 28.2014 | corridor - all other | Corridors (public spaces) | 0.49999 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | REARSTORAGEFLR2 | 216.0315 | 1 | No | NA |  | 315.0594 | 0 | Weighted |  | 0.8 | 1.9992 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM201 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 201 PTAC | 360.0525 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM202_205 | 1404.1508 | 1 | Yes | 1.1 PTAC with electric heating | 202_205 PTAC | 468.0144 | 71.0417 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM206_208 | 1134.0845 | 1 | Yes | 1.1 PTAC with electric heating | 206_208 PTAC | 378.0282 | 72.2258 | Weighted | Hotel suite | 1.1 | 3.9685 | 1.1049 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM209_212 | 1404.1508 | 1 | Yes | 1.1 PTAC with electric heating | 209_212 PTAC | 468.0144 | 71.0417 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM213 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 213 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM214 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 214 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM215_218 | 1404.0431 | 1 | Yes | 1.1 PTAC with electric heating | 215_218 PTAC | 468.0144 | 71.0417 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | ELEVATORCOREFLR2 | 161.9967 | 1 | No | NA |  | 54.0348 | 0 | PNNL Elevator Core |  | 0 | 1.4999 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM219 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 219 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM220_223 | 1404.0431 | 1 | Yes | 1.1 PTAC with electric heating | 220_223 PTAC | 468.0144 | 71.0417 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM224 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 224 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTSTORAGEFLR2 | 134.9793 | 1 | No | NA |  | 44.9931 | 0 | Weighted |  | 0.8 | 2.0001 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTSTAIRSFLR2 | 216.0315 | 1 | Yes | 10. Heating and ventilation | FrontStairsFlr2 Unit Heater | 314.9517 | 0 | stairwell | Corridors (public spaces) | 0.6 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | REARSTAIRSFLR3 | 216.0315 | 1 | Yes | 10. Heating and ventilation | RearStairsFlr3 Unit Heater | 315.0594 | 0 | stairwell | Corridors (public spaces) | 0.6 | 4.9975 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | CORRIDORFLR3 | 1350.0083 | 1 | Yes | 1.1 PTAC with electric heating | CorridorFlr3 PTAC | 197.9481 | 28.2014 | corridor - all other | Corridors (public spaces) | 0.49999 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | REARSTORAGEFLR3 | 216.0315 | 1 | No | NA |  | 315.0594 | 0 | stairwell |  | 0.8 | 1.9992 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM301 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 301 PTAC | 360.0525 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM302_305 | 1404.1508 | 1 | Yes | 1.1 PTAC with electric heating | 302_305 PTAC | 468.0144 | 70.8265 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM306_308 | 1134.0845 | 1 | Yes | 1.1 PTAC with electric heating | 306_308 PTAC | 378.0282 | 72.1181 | Weighted | Hotel suite | 1.1 | 3.9685 | 1.1049 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM309_312 | 1404.1508 | 1 | Yes | 1.1 PTAC with electric heating | 309_312 PTAC | 468.0144 | 70.8265 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM313 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 313 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM314 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 314 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM315_318 | 1404.0431 | 1 | Yes | 1.1 PTAC with electric heating | 315_318 PTAC | 468.0144 | 70.8265 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | ELEVATORCOREFLR3 | 161.9967 | 1 | No | NA |  | 54.0348 | 0 | PNNL Elevator Core |  | 0 | 1.4999 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM319 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 319 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM320_323 | 1404.0431 | 1 | Yes | 1.1 PTAC with electric heating | 320_323 PTAC | 468.0144 | 70.8265 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM324 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 324 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTSTORAGEFLR3 | 134.9793 | 1 | No | NA |  | 44.9931 | 0 | Weighted |  | 0.8 | 2.0001 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTSTAIRSFLR3 | 216.0315 | 1 | Yes | 10. Heating and ventilation | FrontStairsFlr3 Unit Heater | 314.9517 | 0 | stairwell | Corridors (public spaces) | 0.6 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | REARSTAIRSFLR4 | 216.0315 | 1 | Yes | 10. Heating and ventilation | RearStairsFlr4 Unit Heater | 315.0594 | 0 | stairwell | Corridors (public spaces) | 0.6 | 4.9975 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | CORRIDORFLR4 | 1350.0083 | 1 | Yes | 1.1 PTAC with electric heating | CorridorFlr4 PTAC | 197.9481 | 28.2014 | corridor - all other | Corridors (public spaces) | 0.49999 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | REARSTORAGEFLR4 | 216.0315 | 1 | No | NA |  | 315.0594 | 0 | Weighted |  | 0.8 | 1.9992 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM401 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 401 PTAC | 360.0525 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM402_405 | 1404.1508 | 1 | Yes | 1.1 PTAC with electric heating | 402_405 PTAC | 468.0144 | 70.8265 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM406_408 | 1134.0845 | 1 | Yes | 1.1 PTAC with electric heating | 406_408 PTAC | 378.0282 | 72.1181 | Weighted | Hotel suite | 1.1 | 3.9685 | 1.1049 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM409_412 | 1404.1508 | 1 | Yes | 1.1 PTAC with electric heating | 409_412 PTAC | 468.0144 | 70.8265 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM413 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 413 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM414 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 414 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM415_418 | 1404.0431 | 1 | Yes | 1.1 PTAC with electric heating | 415_418 PTAC | 468.0144 | 70.8265 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | ELEVATORCOREFLR4 | 161.9967 | 1 | No | NA |  | 54.0348 | 0 | PNNL Elevator Core |  | 0 | 1.4999 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM419 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 419 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM420_423 | 1404.0431 | 1 | Yes | 1.1 PTAC with electric heating | 420_423 PTAC | 468.0144 | 70.8265 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | GUESTROOM424 | 351.0108 | 1 | Yes | 1.1 PTAC with electric heating | 424 PTAC | 117.0036 | 17.7604 | Weighted | Hotel standard guestroom | 1.1 | 4.2734 | 1.1049 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTSTORAGEFLR4 | 134.9793 | 1 | No | NA |  | 44.9931 | 0 | Weighted |  | 0.8 | 2.0001 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | FRONTSTAIRSFLR4 | 216.0315 | 1 | Yes | 10. Heating and ventilation | FrontStairsFlr4 Unit Heater | 314.9517 | 0 | stairwell | Corridors (public spaces) | 0.6 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Small Hotel | HotelSmall | Total | 43201.7738 |  |  |  |  | 18240.2897 | 1983.7868 |  |  | 0.97575 | 6.9486 | 2.2484
Small Hotel | HotelSmall | Conditioned Total | 40096.4963 |  |  |  |  | 16063.1832 | 1930.7207 |  |  | 1.0075 | 7.1245 | 0.94729
Small Hotel | HotelSmall | Unconditioned Total | 3105.2775 |  |  |  |  | 2177.1064 | 53.066 |  |  | 0.56524 | 4.6083 | 19.0494
Large Hotel
Large Hotel | HotelLarge | BASEMENT | 21299.9282 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 0 | 0 | Weighted | Office space | 1.0282 | 5.0002 | 0.49982 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0
Large Hotel | HotelLarge | RETAIL_1_FLR_1 | 721.9348 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 740.9869 | 250.3683 | Weighted | Sales (except as below) | 1.5 | 15.0086 | 0.99964 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | RETAIL_2_FLR_1 | 836.0321 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 285.9968 | 0 | Weighted | Sales (except as below) | 1.5 | 15.0086 | 0.99964 | 0 | 0 | 0.3 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | MECH_FLR_1 | 1767.8629 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 675.9729 | 0 | electrical/mechanical | No requirement | 1.5 | 1.5001 | 0.49982 | 0 | 0 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | STORAGE_FLR_1 | 1019.9872 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 389.9761 | 0 | Weighted | Storage rooms | 0.8 | 2.0001 | 0.24991 | 0 | 0 | 0.15 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | LAUNDRY_FLR_1 | 840.0148 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 923.0044 | 0 | laundry/washing | Commercial laundry | 0.6 | 10.0003 | 55.5123 | 4.6249 | 25 | 0 | 0 | 0.60538 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | CAFE_FLR_1 | 2032.8702 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 1637.9427 | 705.0354 | dining - bar/lounge/leisure | Restaurant dining rooms | 1.4 | 69.852 | 0.49982 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | LOBBY_FLR_1 | 14081.2263 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 4680.0361 | 915.7926 | lobby - all other | Lobbies/prefunction (hotel, motel, resort, dorm) | 1.3 | 29.9688 | 0.74973 | 0 | 15 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_1_FLR_3 | 420.0074 | 4 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 430.0178 | 141.8682 | Weighted | Hotel suite | 1.1 | 3.5718 | 0.6271 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_2_FLR_3 | 420.0074 | 4 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 430.0178 | 141.8682 | Weighted | Hotel suite | 1.1 | 3.5718 | 0.6271 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_3_MULT19_FLR_3 | 263.9308 | 76 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 120.0175 | 39.6112 | Weighted | Hotel standard guestroom | 1.1 | 5.6821 | 0.97734 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_4_MULT19_FLR_3 | 264.0385 | 76 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 120.0175 | 39.6112 | Weighted | Hotel standard guestroom | 1.1 | 5.6821 | 0.97734 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_5_FLR_3 | 420.0074 | 4 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 430.0178 | 141.8682 | Weighted | Hotel suite | 1.1 | 3.5718 | 0.6271 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_6_FLR_3 | 420.0074 | 4 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 430.0178 | 141.8682 | Weighted | Hotel suite | 1.1 | 3.5718 | 0.6271 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | CORRIDOR_FLR_3 | 4191.4627 | 4 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 520.004 | 171.5766 | corridor - all other | Corridors (public spaces) | 0.49999 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_1_FLR_6 | 420.0074 | 1 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 430.0178 | 141.8682 | Weighted | Hotel suite | 1.1 | 3.5718 | 0.6271 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_2_FLR_6 | 420.0074 | 1 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 430.0178 | 141.8682 | Weighted | Hotel suite | 1.1 | 3.5718 | 0.6271 | 0 | 0 | 0 | 60 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | ROOM_3_MULT9_FLR_6 | 264.0385 | 9 | Yes | 16.1 Four-pipe fan-coil with DOAS | FLR_3_DOAS | 220.0141 | 72.5487 | Weighted | Hotel standard guestroom | 1.1 | 5.6821 | 0.97734 | 0 | 0 | 0 | 35 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | BANQUET_FLR_6 | 3569.9551 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 1050.0184 | 346.4899 | dining - bar/lounge/leisure | Restaurant dining rooms | 1.4 | 69.852 | 6.3007 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | DINING_FLR_6 | 3569.9551 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 1050.0184 | 346.4899 | dining - bar/lounge/leisure | Restaurant dining rooms | 1.4 | 69.852 | 6.3007 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | KITCHEN_FLR_6 | 1111.9109 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 940.0114 | 283.844 | kitchen | Kitchen | 1.2 | 19.9792 | 272.8019 | 20.8815 | 15 | 0.4 | 0 | 3.6016 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | CORRIDOR_FLR_6 | 4436.0185 | 1 | Yes | 7. VAV with reheat | VAV WITH REHEAT | 919.9905 | 303.542 | corridor - all other | Corridors (public spaces) | 0.49999 | 5.0002 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Large Hotel | HotelLarge | Total | 122119.567 |  |  |  |  | 43333.5239 | 13065.1142 |  |  | 1.0348 | 13.1405 | 3.8172
Large Hotel | HotelLarge | Conditioned Total | 122119.567 |  |  |  |  | 43333.5239 | 13065.1142 |  |  | 1.0348 | 13.1405 | 3.8172
Large Hotel | HotelLarge | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Warehouse (non-refrigerated)
Warehouse (non-refrigerated) | Warehouse | ZONE1 OFFICE | 2549.7526 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-OFFICE | 1609.8489 | 190.0905 | Weighted | Office space | 0.99579 | 5.0002 | 0.75007 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 611.9994
Warehouse (non-refrigerated) | Warehouse | ZONE2 FINE STORAGE | 14998.5259 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-FINE STORAGE | 8189.1751 | 0 | warehouse - fine storage | Warehouses | 1.4 | 2.0001 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0.20182 | 0 | 0
Warehouse (non-refrigerated) | Warehouse | ZONE3 BULK STORAGE | 34496.5773 | 1 | Yes | 9. Heating and ventilation | Zone3 Bulk Storage Unit Heater | 17078.3267 | 0 | warehouse - bulk storage | Warehouses | 0.9 | 2.0001 | 0.23771 | 0 | 0 | 0.05 | 0 | 0 | 0.42589 | 0 | 0
Warehouse (non-refrigerated) | Warehouse | Total | 52044.8558 |  |  |  |  | 26877.3507 | 190.0905 |  |  | 1.0488 | 2.1471 | 0.19431
Warehouse (non-refrigerated) | Warehouse | Conditioned Total | 52044.8558 |  |  |  |  | 26877.3507 | 190.0905 |  |  | 1.0488 | 2.1471 | 0.19431
Warehouse (non-refrigerated) | Warehouse | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Quick Service Restaurant
Quick Service Restaurant | RestaurantFastFood | DINING | 1250.4423 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_1:1 | 1000.3969 | 280.0767 | Weighted | Restaurant dining rooms | 0.86063 | 69.852 | 10.8499 | 0 | 20 | 0 | 0 | 1.4064 | 0.20182 | 0 | 1912.9982
Quick Service Restaurant | RestaurantFastFood | KITCHEN | 1250.4423 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_2:2 | 1000.3969 | 0 | Weighted | Kitchen | 1.1098 | 5.0164 | 99.7784 | 6.8302 | 15 | 0.4 | 0 | 2.6434 | 0.20182 | 0 | 0
Quick Service Restaurant | RestaurantFastFood | ATTIC | 2500.8845 | 1 | No |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 154.4664 | 0
Quick Service Restaurant | RestaurantFastFood | Total | 2500.8845 |  |  |  |  | 2000.9014 | 280.0767 |  |  | 0.98521 | 37.4609 | 55.3141
Quick Service Restaurant | RestaurantFastFood | Conditioned Total | 2500.8845 |  |  |  |  | 2000.9014 | 280.0767 |  |  | 0.98521 | 37.4609 | 55.3141
Quick Service Restaurant | RestaurantFastFood | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Full Service Restaurant
Full Service Restaurant | RestaurantSitDown | DINING | 4001.4798 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_1:1 | 1821.1442 | 507.7332 | Weighted | Restaurant dining rooms | 1.9168 | 69.852 | 6.032 | 0 | 20 | 0 | 0 | 1.3979 | 0.20182 | 0 | 1301.9988
Full Service Restaurant | RestaurantSitDown | KITCHEN | 1500.5953 | 1 | Yes | 3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant) | PSZ-AC_2:2 | 1146.6783 | 0 | Weighted | Kitchen | 1.0586 | 5.0164 | 98.7633 | 5.6037 | 15 | 0.4 | 0 | 3.996 | 0.20182 | 0 | 0
Full Service Restaurant | RestaurantSitDown | ATTIC | 5501.9675 | 1 | No |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 503.8697 | 0
Full Service Restaurant | RestaurantSitDown | Total | 5501.9675 |  |  |  |  | 2967.8225 | 507.7332 |  |  | 1.6827 | 52.1928 | 31.3223
Full Service Restaurant | RestaurantSitDown | Conditioned Total | 5501.9675 |  |  |  |  | 2967.8225 | 507.7332 |  |  | 1.6827 | 52.1928 | 31.3223
Full Service Restaurant | RestaurantSitDown | Unconditioned Total | 0 |  |  |  |  | 0 | 0 |  |  | 0 | 0 | 0
Mid-rise Apartment
Mid-rise Apartment | ApartmentMidRise | G SW APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT GSW | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | G NW APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT GNW | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | OFFICE | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT OFFICE | 629.9034 | 126.0453 | Weighted | Office space | 1.1 | 5.0002 | 0.61966 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | G NE APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT GNE | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | G N1 APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT GN1 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | G N2 APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT GN2 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | G S1 APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT GS1 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | G S2 APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT GS2 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | M SW APARTMENT | 949.9142 | 2 | Yes | 3. PSZ-AC | SPLIT MSW | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | M NW APARTMENT | 949.9142 | 2 | Yes | 3. PSZ-AC | SPLIT MNW | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | M SE APARTMENT | 949.9142 | 2 | Yes | 3. PSZ-AC | SPLIT MSE | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | M NE APARTMENT | 949.9142 | 2 | Yes | 3. PSZ-AC | SPLIT MNE | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | M N1 APARTMENT | 949.9142 | 2 | Yes | 3. PSZ-AC | SPLIT MN1 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | M N2 APARTMENT | 949.9142 | 2 | Yes | 3. PSZ-AC | SPLIT MN2 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | M S1 APARTMENT | 949.9142 | 2 | Yes | 3. PSZ-AC | SPLIT MS1 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | M S2 APARTMENT | 949.9142 | 2 | Yes | 3. PSZ-AC | SPLIT MS2 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T SW APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT TSW | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T NW APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT TNW | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T SE APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT TSE | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T NE APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT TNE | 629.9034 | 126.0453 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T N1 APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT TN1 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T N2 APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT TN2 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T S1 APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT TS1 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T S2 APARTMENT | 949.9142 | 1 | Yes | 3. PSZ-AC | SPLIT TS2 | 379.9657 | 75.9931 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | T CORRIDOR | 835.9245 | 1 | No |  |  | 110.0071 | 11.9479 | Weighted |  | 0.54054 | 5.0002 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | G CORRIDOR | 835.9245 | 1 | No |  |  | 110.0071 | 35.7361 | Weighted |  | 0.54054 | 5.0002 | 9.7786 | 0 |  |  |  | 0 | 0.20182 | 0 | 1102.999
Mid-rise Apartment | ApartmentMidRise | M CORRIDOR | 835.9245 | 2 | No |  |  | 110.0071 | 11.9479 | Weighted |  | 0.54054 | 5.0002 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
Mid-rise Apartment | ApartmentMidRise | Total | 33740.6286 |  |  |  |  | 16598.3644 | 3303.6562 |  |  | 1.4984 | 2.9335 | 0.80052
Mid-rise Apartment | ApartmentMidRise | Conditioned Total | 30397.0383 |  |  |  |  | 16158.4438 | 3231.9686 |  |  | 1.6037 | 2.7062 | 0.61966
Mid-rise Apartment | ApartmentMidRise | Unconditioned Total | 3343.6979 |  |  |  |  | 439.9206 | 71.6876 |  |  | 0.54054 | 5.0002 | 2.4447
High-rise Apartment
High-rise Apartment | ApartmentHighRise | G SW APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP G SW | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | G NW APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP G NW | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | OFFICE | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP OFFICE | 629.9034 | 189.0141 | Weighted | Office space | 1.1 | 5.0002 | 0.61966 | 0 | 20 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | G NE APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP G NE | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | G N1 APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP G N1 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | G N2 APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP G N2 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | G S1 APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP G S1 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | G S2 APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP G S2 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | G CORRIDOR | 835.9245 | 1 | No | NA |  | 110.0071 | 48.1146 | Weighted |  | 0.52499 | 5.0002 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 3228.997
High-rise Apartment | ApartmentHighRise | M SW APARTMENT | 949.9142 | 8 | Yes | 15. WSHP | AIRLOOP M SW | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | M NW APARTMENT | 949.9142 | 8 | Yes | 15. WSHP | AIRLOOP M NW | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | M SE APARTMENT | 949.9142 | 8 | Yes | 15. WSHP | AIRLOOP M SE | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | M NE APARTMENT | 949.9142 | 8 | Yes | 15. WSHP | AIRLOOP M NE | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | M N1 APARTMENT | 949.9142 | 8 | Yes | 15. WSHP | AIRLOOP M N1 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | M N2 APARTMENT | 949.9142 | 8 | Yes | 15. WSHP | AIRLOOP M N2 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | M S1 APARTMENT | 949.9142 | 8 | Yes | 15. WSHP | AIRLOOP M S1 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | M S2 APARTMENT | 949.9142 | 8 | Yes | 15. WSHP | AIRLOOP M S2 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | M CORRIDOR | 835.9245 | 8 | No | NA |  | 110.0071 | 24.0035 | Weighted |  | 0.52499 | 5.0002 | 0 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T SW APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP T SW | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T NW APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP T NW | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T SE APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP T SE | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T NE APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP T NE | 629.9034 | 189.0141 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T N1 APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP T N1 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T N2 APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP T N2 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T S1 APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP T S1 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T S2 APARTMENT | 949.9142 | 1 | Yes | 15. WSHP | AIRLOOP T S2 | 379.9657 | 113.9897 | PNNL Hardwired and Plugin | Residiential single bedroom apartment | 1.62 | 2.6318 | 0.61966 | 0 | 27.5 | 0 | 0 | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | T CORRIDOR | 835.9245 | 1 | No |  |  | 110.0071 | 24.0035 | Weighted |  | 0.52499 | 5.0002 | 20.7846 | 0 |  |  |  | 0 | 0.20182 | 0 | 0
High-rise Apartment | ApartmentHighRise | Total | 84351.0871 |  |  |  |  | 41495.0498 | 12382.6829 |  |  | 1.5056 | 2.8933 | 0.76423
High-rise Apartment | ApartmentHighRise | Conditioned Total | 75991.95 |  |  |  |  | 40395.1945 | 12118.5368 |  |  | 1.6135 | 2.6612 | 0.61966
High-rise Apartment | ApartmentHighRise | Unconditioned Total | 8359.0295 |  |  |  |  | 1099.8553 | 264.1461 |  |  | 0.52499 | 5.0002 | 2.0785

## Fenestration_Weights
| Type 1 |  | Type 2 |  |  | Type 3
Building Prototype | Fixed | Operable | Nonmetal | Metal - Fixed | Metal - Operable | Nonmetal | Curtain wall / Storefront | Metal - all other
Small Office | 96.88% | 3.117% | 2.475% | 95.75% | 1.777% | 2.475% | 64.84% | 32.69%
Medium Office | 96.88% | 3.117% | 2.475% | 95.75% | 1.777% | 2.475% | 64.84% | 32.69%
Large Office | 96.88% | 3.117% | 2.475% | 95.75% | 1.777% | 2.475% | 64.84% | 32.69%
Standalone Retail | 97.84% | 2.159% | 2.579% | 96.19% | 1.231% | 2.579% | 71.7% | 25.72%
Strip Mall | 97.84% | 2.159% | 2.579% | 96.19% | 1.231% | 2.579% | 71.7% | 25.72%
Primary School | 89.76% | 10.24% | 7.512% | 86.65% | 5.839% | 7.512% | 56.04% | 36.45%
Secondary School | 89.76% | 10.24% | 7.512% | 86.65% | 5.839% | 7.512% | 56.04% | 36.45%
Outpatient Healthcare | 95.94% | 4.063% | 3.111% | 94.57% | 2.316% | 3.111% | 61.51% | 35.38%
Hospital | 95.94% | 4.063% | 3.111% | 94.57% | 2.316% | 3.111% | 61.51% | 35.38%
Small Hotel | 92.05% | 7.952% | 5.808% | 89.66% | 4.533% | 5.808% | 57.22% | 36.97%
Large Hotel | 92.05% | 7.952% | 5.808% | 89.66% | 4.533% | 5.808% | 57.22% | 36.97%
Warehouse (non refrigerated) | 97.36% | 2.64% | 2.443% | 96.05% | 1.505% | 2.443% | 43.49% | 54.07%
Quick-Service Restaurant | 97.84% | 2.159% | 2.579% | 96.19% | 1.231% | 2.579% | 71.7% | 25.72%
Full-Service Restaurant | 97.84% | 2.159% | 2.579% | 96.19% | 1.231% | 2.579% | 71.7% | 25.72%
Mid-Rise Apartment | 75.39% | 24.61% | 17.28% | 68.69% | 14.03% | 17.28% | 36.1% | 46.62%
High-Rise Apartment | 75.39% | 24.61% | 17.28% | 68.69% | 14.03% | 17.28% | 36.1% | 46.62%
Datacenter | 97.36% | 2.64% | 2.443% | 96.05% | 1.505% | 2.443% | 43.49% | 54.07%
Supermarket | 97.84% | 2.159% | 2.579% | 96.19% | 1.231% | 2.579% | 71.7% | 25.72%
Assembly Building | 93.45% | 6.547% | 4.895% | 91.37% | 3.732% | 4.895% | 54.89% | 40.21%

## Schedule Summary
Prototype | Schedule | Space Type | Day of Week | 1 am | 2 am | 3 am | 4 am | 5 am | 6 am | 7 am | 8 am | 9 am | 10 am | 11 am | 12 pm | 1 pm | 2 pm | 3 pm | 4 pm | 5 pm | 6 pm | 7 pm | 8 pm | 9 pm | 10 pm | 11 pm | 12 am
OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.61039 | 1 | 1 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0
OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | Lighting | All | Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.23 | 0.42 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.42 | 0.42 | 0.32 | 0.32 | 0.23 | 0.18
OfficeSmall | Lighting | All | Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
OfficeSmall | Lighting | All | Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
OfficeSmall | Electric Equipment | All | Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | Electric Equipment | All | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | Electric Equipment | All | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OfficeSmall | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0.55 | 0.64 | 0.64 | 0.82 | 1 | 0.91 | 0.55 | 0.55 | 0.73 | 0.37 | 0.37 | 0.18 | 0.27 | 0.09 | 0 | 0
OfficeSmall | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Infiltration | All | Sun | bar: 1 am to 12 am
OfficeSmall | Cooling Set Point | All | Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | Cooling Set Point | All | Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | Cooling Set Point | All | Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | Heating Set Point | All | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | Heating Set Point | All | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | Heating Set Point | All | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.9757 | 0.95 | 0.51353 | 0.95 | 0.9757 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.30812 | 0.3 | 0.10271 | 0.1 | 0.10271 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | Lighting | All | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OfficeMedium | Lighting | All | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Lighting | All | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Electric Equipment | All | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
OfficeMedium | Electric Equipment | All | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeMedium | Electric Equipment | All | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeMedium | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeMedium | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeMedium | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0
OfficeMedium | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeMedium | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Infiltration | All | Sun | bar: 1 am to 12 am
OfficeMedium | Cooling Set Point | All | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Cooling Set Point | All | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Cooling Set Point | All | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Heating Set Point | All | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | Heating Set Point | All | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | Heating Set Point | All | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.99331 | 0.95 | 0.5228 | 0.95 | 0.99331 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.31368 | 0.3 | 0.10456 | 0.1 | 0.10456 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | Lighting | All (Except Data Center) | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OfficeLarge | Lighting | All (Except Data Center) | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Lighting | All (Except Data Center) | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeLarge | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeLarge | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeLarge | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
OfficeLarge | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
OfficeLarge | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeLarge | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Infiltration | All | Sun | bar: 1 am to 12 am
OfficeLarge | Cooling Set Point | All (Except Data Center) | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | Cooling Set Point | All (Except Data Center) | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | Cooling Set Point | All (Except Data Center) | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
RetailStandalone | Occupants | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
RetailStandalone | Occupants | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
RetailStandalone | Occupants | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
RetailStandalone | Lighting | All | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone | Lighting | All | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone | Lighting | All | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone | Electric Equipment | All | Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2
RetailStandalone | Electric Equipment | All | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
RetailStandalone | Electric Equipment | All | Sun | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
RetailStandalone | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStandalone | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
RetailStandalone | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStandalone | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0
RetailStandalone | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0
RetailStandalone | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0
RetailStandalone | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStandalone | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
RetailStandalone | Infiltration | All | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | Heating Set Point | All (Except Core_Retail) | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone | Heating Set Point | All (Except Core_Retail) | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone | Heating Set Point | All (Except Core_Retail) | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Occupants | Type 1 Store | Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.05
RetailStripmall | Occupants | Type 1 Store | Fri, Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.6 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2
RetailStripmall | Occupants | Type 1 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.4 | 0.3 | 0.6 | 0.6 | 0.4 | 0.4 | 0.3 | 0.2 | 0.05
RetailStripmall | Occupants | Type 2 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.3 | 0.2 | 0.2 | 0.5 | 0.5 | 0.2 | 0.05 | 0 | 0 | 0
RetailStripmall | Occupants | Type 2 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 0.05 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Occupants | Type 2 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Occupants | Type 3 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.71 | 0.5 | 0.69 | 0.54 | 0.71 | 0.34 | 0.26 | 0.11 | 0 | 0 | 0
RetailStripmall | Occupants | Type 3 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.58 | 0.71 | 0.74 | 0.77 | 0.8 | 0.74 | 0.54 | 0.11 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Occupants | Type 3 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.5 | 0.69 | 0.34 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Lighting | Type 1 Small Store | Mon - Fri | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.502
RetailStripmall | Lighting | Type 1 Small Store | Sat | 0.502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538
RetailStripmall | Lighting | Type 1 Small Store | Sun | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.502
RetailStripmall | Lighting | Type 1 Large Store | Mon - Fri | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.50075
RetailStripmall | Lighting | Type 1 Large Store | Sat | 0.50075 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142
RetailStripmall | Lighting | Type 1 Large Store | Sun | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.50075
RetailStripmall | Lighting | Type 2 Small Store | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 2 Small Store | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 2 Small Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 2 Large Store | Mon - Fri | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | Lighting | Type 2 Large Store | Sat | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | Lighting | Type 2 Large Store | Sun | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | Lighting | Type 3 Store | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 3 Store | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 3 Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 1 Store | Mon - Thu | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
RetailStripmall | Electric Equipment | Type 1 Store | Fri, Sat | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
RetailStripmall | Electric Equipment | Type 1 Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
RetailStripmall | Electric Equipment | Type 2 Store | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 2 Store | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 2 Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 3 Store | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 3 Store | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 3 Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | HVAC | Type 1 Store | Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | HVAC | Type 1 Store | Fri, Sat | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | HVAC | Type 1 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | HVAC | Type 2 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall | HVAC | Type 2 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall | HVAC | Type 2 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | HVAC | Type 3 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall | HVAC | Type 3 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall | HVAC | Type 3 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | SWH | Type 1 Store | Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.62 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall | SWH | Type 1 Store | Fri, Sat | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0.32 | 0.41 | 0.65 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall | SWH | Type 1 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.16 | 0.1
RetailStripmall | SWH | Type 2 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0
RetailStripmall | SWH | Type 2 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.62 | 0.6 | 0.5 | 0.48 | 0.47 | 0.34 | 0 | 0 | 0 | 0 | 0
RetailStripmall | SWH | Type 2 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.14 | 0.29 | 0.33 | 0.4 | 0.36 | 0.37 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | SWH | Type 3 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.25 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0
RetailStripmall | SWH | Type 3 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0 | 0 | 0 | 0 | 0
RetailStripmall | SWH | Type 3 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Infiltration | Type 1 Store | Mon - Thu | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Infiltration | Type 1 Store | Fri, Sat | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Infiltration | Type 1 Store | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Infiltration | Type 2 Store | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 2 Store | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 2 Store | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 3 Store | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 3 Store | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 3 Store | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Cooling Set Point | All | Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Cooling Set Point | All | Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Cooling Set Point | All | Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Heating Set Point | Type 1 Store | Mon - Thu | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Heating Set Point | Type 1 Store | Fri, Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Heating Set Point | Type 1 Store | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Heating Set Point | Type 2 Store | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 2 Store | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 2 Store | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 3 Store | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 3 Store | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 3 Store | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Lighting | All (Study Periods) | Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Study Periods) | Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Study Periods) | Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Summer Holiday) | Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Summer Holiday) | Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Summer Holiday) | Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Others (Study Periods) | Mon - Fri | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | Electric Equipment | Others (Study Periods) | Sat | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | Electric Equipment | Others (Study Periods) | Sun | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | Gas Equipment | Kitchen | Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | Gas Equipment | Kitchen | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | Gas Equipment | Kitchen | Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolPrimary | Infiltration | All | Sat | bar: 1 am to 12 am
SchoolPrimary | Infiltration | All | Sun | bar: 1 am to 12 am
SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Others | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | Cooling Set Point | Others | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | Cooling Set Point | Others | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Others | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Others | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Others | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Lighting | All (Study Periods) | Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Study Periods) | Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Study Periods) | Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Summer Holiday) | Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Summer Holiday) | Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Summer Holiday) | Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Others (Study Periods) | Mon - Fri | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | Electric Equipment | Others (Study Periods) | Sat | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | Electric Equipment | Others (Study Periods) | Sun | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | Gas Equipment | Kitchen | Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | Gas Equipment | Kitchen | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | Gas Equipment | Kitchen | Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolSecondary | Infiltration | All | Sat | bar: 1 am to 12 am
SchoolSecondary | Infiltration | All | Sun | bar: 1 am to 12 am
SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Mon - Fri | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Sat | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Sun | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | Cooling Set Point | Others | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | Cooling Set Point | Others | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | Cooling Set Point | Others | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Others | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Others | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Others | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0.9 | 0 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0 | 0.3 | 0.3 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | Occupants | Conference Room | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0.9 | 0.9 | 0 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Conference Room | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Conference Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | Occupants | Others | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Others | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Others | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | Lighting | All | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | Lighting | All | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | Lighting | All | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Electric Equipment | All | Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Electric Equipment | All | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Electric Equipment | All | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Gas Equipment | Operating Room | Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Gas Equipment | Operating Room | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Gas Equipment | Operating Room | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | HVAC | All | Mon - Fri | bar: 1 am to 12 am
OutPatientHealthCare | HVAC | All | Sat | bar: 1 am to 12 am
OutPatientHealthCare | HVAC | All | Sun | bar: 1 am to 12 am
OutPatientHealthCare | SWH | All | Mon - Fri | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
OutPatientHealthCare | SWH | All | Sat | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
OutPatientHealthCare | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.12 | 0.12
OutPatientHealthCare | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OutPatientHealthCare | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OutPatientHealthCare | Infiltration | All | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | Infiltration | All | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | Infiltration | All | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | Cooling Set Point | OR | Mon - Fri | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | OR | Sat | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | OR | Sun | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | Others | Mon - Fri | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | Others | Sat | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | Others | Sun | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Heating Set Point | OR | Mon - Fri | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | Heating Set Point | OR | Sat | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | Heating Set Point | OR | Sun | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | Heating Set Point | Others | Mon - Fri | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | Heating Set Point | Others | Sat | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | Heating Set Point | Others | Sun | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sun | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sun | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | HVAC | All | Mon - Fri | bar: 1 am to 12 am
Hospital | HVAC | All | Sat | bar: 1 am to 12 am
Hospital | HVAC | All | Sun | bar: 1 am to 12 am
Hospital | SWH | Office, Lobby, Clinic, OR | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0 | 0
Hospital | SWH | Office, Lobby, Clinic, OR | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hospital | SWH | Office, Lobby, Clinic, OR | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3
Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | Elevator | All | Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2
Hospital | Elevator | All | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Elevator | All | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Infiltration | All | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | Infiltration | All | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | Infiltration | All | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | Cooling Set Point | All | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | Cooling Set Point | All | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | Cooling Set Point | All | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | Heating Set Point | All | Mon - Fri | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Hospital | Heating Set Point | All | Sat | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Hospital | Heating Set Point | All | Sun | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelSmall | Occupants | Guest Rooms | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1
HotelSmall | Occupants | Guest Rooms | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelSmall | Occupants | Guest Rooms | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelSmall | Occupants | Office | Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | Occupants | Office | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | Occupants | Office | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | Occupants | Meeting Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0 | 0 | 0.05 | 0.5 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Meeting Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Meeting Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Exercise Center | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Occupants | Exercise Center | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Occupants | Exercise Center | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Occupants | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Employee Lounge | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Employee Lounge | Sat | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Employee Lounge | Sun | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Front Lounge, Restroom | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Occupants | Front Lounge, Restroom | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Occupants | Front Lounge, Restroom | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Lighting | Guest Rooms | Mon - Fri | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
HotelSmall | Lighting | Guest Rooms | Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelSmall | Lighting | Guest Rooms | Sun | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelSmall | Lighting | Office | Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | Lighting | Office | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | Lighting | Office | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Sat | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Sun | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | Lighting | Exercise Center | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Lighting | Exercise Center | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Lighting | Exercise Center | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Lighting | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Lighting | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Lighting | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Lighting | Corridors, Stairs, Restroom | Mon - Fri | bar: 1 am to 12 am
HotelSmall | Lighting | Corridors, Stairs, Restroom | Sat | bar: 1 am to 12 am
HotelSmall | Lighting | Corridors, Stairs, Restroom | Sun | bar: 1 am to 12 am
HotelSmall | Lighting | Storage, Mechanical room | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | Lighting | Storage, Mechanical room | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | Lighting | Storage, Mechanical room | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | Electric Equipment | Guest Rooms | Mon - Fri | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | Electric Equipment | Guest Rooms | Sat | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | Electric Equipment | Guest Rooms | Sun | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | Electric Equipment | Office | Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | Electric Equipment | Office | Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | Electric Equipment | Office | Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | Electric Equipment | Meeting Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Meeting Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Meeting Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Exercise Center | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | Electric Equipment | Exercise Center | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | Electric Equipment | Exercise Center | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | Electric Equipment | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Employee Lounge | Mon - Fri | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | Electric Equipment | Employee Lounge | Sat | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | Electric Equipment | Employee Lounge | Sun | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | Electric Equipment | Front Lounge | Mon - Fri | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | Electric Equipment | Front Lounge | Sat | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | Electric Equipment | Front Lounge | Sun | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | Gas Equipment | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Gas Equipment | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Gas Equipment | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | HVAC | All | Mon - Fri | bar: 1 am to 12 am
HotelSmall | HVAC | All | Sat | bar: 1 am to 12 am
HotelSmall | HVAC | All | Sun | bar: 1 am to 12 am
HotelSmall | SWH | Guest Rooms | Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
HotelSmall | SWH | Guest Rooms | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelSmall | SWH | Guest Rooms | Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelSmall | SWH | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | SWH | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | SWH | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | Infiltration | Guest Rooms | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Guest Rooms | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Guest Rooms | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Common Areas | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Common Areas | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Common Areas | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Cooling Set Point | Guest Rooms | Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Cooling Set Point | Guest Rooms | Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Cooling Set Point | Guest Rooms | Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Cooling Set Point | Common Area | Mon - Fri | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | Cooling Set Point | Common Area | Sat | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | Cooling Set Point | Common Area | Sun | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | Heating Set Point | Guest Rooms | Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Guest Rooms | Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Guest Rooms | Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Common Area | Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Common Area | Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Common Area | Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelLarge | Occupants | Guest Rooms | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1
HotelLarge | Occupants | Guest Rooms | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelLarge | Occupants | Guest Rooms | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelLarge | Occupants | Others | Mon - Fri | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
HotelLarge | Occupants | Others | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
HotelLarge | Occupants | Others | Sun | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
HotelLarge | Lighting | Guest Rooms | Mon - Fri | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
HotelLarge | Lighting | Guest Rooms | Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelLarge | Lighting | Guest Rooms | Sun | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelLarge | Lighting | Others | Mon - Fri | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | Lighting | Others | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | Lighting | Others | Sun | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | Electric Equipment | Guest Rooms | Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | Electric Equipment | Guest Rooms | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | Electric Equipment | Guest Rooms | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Electric Equipment | Others | Mon - Fri | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
HotelLarge | Electric Equipment | Others | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
HotelLarge | Electric Equipment | Others | Sun | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
HotelLarge | Gas Equipment | Kitchen | Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | Gas Equipment | Kitchen | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | Gas Equipment | Kitchen | Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | HVAC | All | Mon - Fri | bar: 1 am to 12 am
HotelLarge | HVAC | All | Sat | bar: 1 am to 12 am
HotelLarge | HVAC | All | Sun | bar: 1 am to 12 am
HotelLarge | SWH | Guest Rooms | Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
HotelLarge | SWH | Guest Rooms | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelLarge | SWH | Guest Rooms | Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelLarge | SWH | Kitchen | Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
HotelLarge | SWH | Kitchen | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
HotelLarge | SWH | Kitchen | Sun | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
HotelLarge | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | Infiltration | All | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | Infiltration | All | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | Infiltration | All | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | Cooling Set Point | Guest Rooms | Mon - Fri | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Cooling Set Point | Guest Rooms | Sat | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Cooling Set Point | Guest Rooms | Sun | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Cooling Set Point | Common Areas | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | Cooling Set Point | Common Areas | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | Cooling Set Point | Common Areas | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | Heating Set Point | Guest Rooms | Mon - Fri | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Heating Set Point | Guest Rooms | Sat | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Heating Set Point | Guest Rooms | Sun | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Heating Set Point | Common Areas | Mon - Fri | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelLarge | Heating Set Point | Common Areas | Sat | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelLarge | Heating Set Point | Common Areas | Sun | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Warehouse | Occupants | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Occupants | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Occupants | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Lighting | Office | Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | Lighting | Office | Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | Lighting | Office | Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | Lighting | Fine Sorage, Bulk Storage | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | Lighting | Fine Sorage, Bulk Storage | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | Lighting | Fine Sorage, Bulk Storage | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | Electric Equipment | Office | Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Electric Equipment | Office | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Electric Equipment | Office | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Electric Equipment | Bulk Storage | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Warehouse | Electric Equipment | Bulk Storage | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Warehouse | Electric Equipment | Bulk Storage | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | HVAC | All | Mon - Fri | bar: 1 am to 12 am
Warehouse | HVAC | All | Sat | bar: 1 am to 12 am
Warehouse | HVAC | All | Sun | bar: 1 am to 12 am
Warehouse | SWH | Office | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.101 | 0.399 | 0.501 | 0.501 | 0.696 | 0.9 | 0.798 | 0.696 | 0.798 | 0.297 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | SWH | Office | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.101 | 0.399 | 0.501 | 0.501 | 0.696 | 0.9 | 0.798 | 0.696 | 0.798 | 0.297 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | SWH | Office | Sun | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
Warehouse | Infiltration | Office, Fine Sorage | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Infiltration | Office, Fine Sorage | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Infiltration | Office, Fine Sorage | Sun | bar: 1 am to 12 am
Warehouse | Infiltration | Bulk Storage | Mon - Fri | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | Infiltration | Bulk Storage | Sat | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | Infiltration | Bulk Storage | Sun | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | Cooling Set Point | Office | Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
Warehouse | Cooling Set Point | Office | Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
Warehouse | Cooling Set Point | Office | Sun | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
Warehouse | Cooling Set Point | Fine Sorage | Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | Cooling Set Point | Fine Sorage | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | Cooling Set Point | Fine Sorage | Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | Heating Set Point | Office | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Heating Set Point | Office | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Heating Set Point | Office | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Heating Set Point | Fine Sorage | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Heating Set Point | Fine Sorage | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Heating Set Point | Fine Sorage | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Heating Set Point | Bulk Storage | Mon - Fri | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Warehouse | Heating Set Point | Bulk Storage | Sat | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Warehouse | Heating Set Point | Bulk Storage | Sun | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
RestaurantFastFood | Occupants | All | Mon - Fri | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
RestaurantFastFood | Occupants | All | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
RestaurantFastFood | Occupants | All | Sun | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
RestaurantFastFood | Lighting | All | Mon - Fri | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | Lighting | All | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | Lighting | All | Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantFastFood | Electric Equipment | All | Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Electric Equipment | All | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Electric Equipment | All | Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Gas Equipment | Kitchen | Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Gas Equipment | Kitchen | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Gas Equipment | Kitchen | Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | HVAC | All | Mon - Fri | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | HVAC | All | Sat | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | HVAC | All | Sun | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
RestaurantFastFood | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
RestaurantFastFood | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
RestaurantFastFood | Infiltration | All | Mon - Fri | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | Infiltration | All | Sat | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | Infiltration | All | Sun | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | Cooling Set Point | Dining | Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | Cooling Set Point | Dining | Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | Cooling Set Point | Dining | Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | Cooling Set Point | Kitchen | Mon - Fri | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | Cooling Set Point | Kitchen | Sat | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | Cooling Set Point | Kitchen | Sun | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | Heating Set Point | Dining | Mon - Fri | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | Heating Set Point | Dining | Sat | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | Heating Set Point | Dining | Sun | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | Heating Set Point | Kitchen | Mon - Fri | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | Heating Set Point | Kitchen | Sat | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | Heating Set Point | Kitchen | Sun | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantSitDown | Occupants | All | Mon - Fri | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
RestaurantSitDown | Occupants | All | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
RestaurantSitDown | Occupants | All | Sun | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
RestaurantSitDown | Lighting | All | Mon - Fri | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | Lighting | All | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | Lighting | All | Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantSitDown | Electric Equipment | All | Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Electric Equipment | All | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Electric Equipment | All | Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Gas Equipment | Kitchen | Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Gas Equipment | Kitchen | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Gas Equipment | Kitchen | Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | HVAC | All | Mon - Fri | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | HVAC | All | Sat | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | HVAC | All | Sun | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | SWH | All | Mon - Fri | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
RestaurantSitDown | SWH | All | Sat | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
RestaurantSitDown | SWH | All | Sun | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
RestaurantSitDown | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | Infiltration | All | Sun | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | Cooling Set Point | Dining | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | Cooling Set Point | Dining | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | Cooling Set Point | Dining | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | Cooling Set Point | Kitchen | Mon - Fri | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | Cooling Set Point | Kitchen | Sat | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | Cooling Set Point | Kitchen | Sun | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | Heating Set Point | Dining | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | Heating Set Point | Dining | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | Heating Set Point | Dining | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | Heating Set Point | Kitchen | Mon - Fri | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | Heating Set Point | Kitchen | Sat | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | Heating Set Point | Kitchen | Sun | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
ApartmentMidRise | Occupants | Apartment (Stay Home) | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Stay Home) | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Stay Home) | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Working) | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Working) | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Working) | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Occupants | Office | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | Occupants | Office | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | Occupants | Office | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | Lighting | Apartment | Mon - Fri | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | Lighting | Apartment | Sat | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | Lighting | Apartment | Sun | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | Lighting | Office | Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | Lighting | Office | Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | Lighting | Office | Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | Lighting | Corridor | Mon - Fri | bar: 1 am to 12 am
ApartmentMidRise | Lighting | Corridor | Sat | bar: 1 am to 12 am
ApartmentMidRise | Lighting | Corridor | Sun | bar: 1 am to 12 am
ApartmentMidRise | Electric Equipment | Apartment | Mon - Fri | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | Electric Equipment | Apartment | Sat | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | Electric Equipment | Apartment | Sun | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | Electric Equipment | Office | Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | Electric Equipment | Office | Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | Electric Equipment | Office | Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | HVAC | All | Mon - Fri | bar: 1 am to 12 am
ApartmentMidRise | HVAC | All | Sat | bar: 1 am to 12 am
ApartmentMidRise | HVAC | All | Sun | bar: 1 am to 12 am
ApartmentMidRise | SWH | All | Mon - Fri | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | SWH | All | Sat | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | SWH | All | Sun | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | Infiltration | All | Mon - Fri | bar: 1 am to 12 am
ApartmentMidRise | Infiltration | All | Sat | bar: 1 am to 12 am
ApartmentMidRise | Infiltration | All | Sun | bar: 1 am to 12 am
ApartmentMidRise | Cooling Set Point | Apartment | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | Cooling Set Point | Apartment | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | Cooling Set Point | Apartment | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | Cooling Set Point | Office | Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | Cooling Set Point | Office | Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | Cooling Set Point | Office | Sun | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | Heating Set Point | Apartment | Mon - Fri | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | Heating Set Point | Apartment | Sat | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | Heating Set Point | Apartment | Sun | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | Heating Set Point | Office | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | Heating Set Point | Office | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | Heating Set Point | Office | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | Occupants | Apartment (Stay Home) | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Stay Home) | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Stay Home) | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Working) | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Working) | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Working) | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Occupants | Office | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | Occupants | Office | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | Occupants | Office | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | Lighting | Apartment | Mon - Fri | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | Lighting | Apartment | Sat | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | Lighting | Apartment | Sun | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | Lighting | Office | Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | Lighting | Office | Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | Lighting | Office | Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | Lighting | Corridor | Mon - Fri | bar: 1 am to 12 am
ApartmentHighRise | Lighting | Corridor | Sat | bar: 1 am to 12 am
ApartmentHighRise | Lighting | Corridor | Sun | bar: 1 am to 12 am
ApartmentHighRise | Electric Equipment | Apartment | Mon - Fri | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | Electric Equipment | Apartment | Sat | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | Electric Equipment | Apartment | Sun | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | Electric Equipment | Office | Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | Electric Equipment | Office | Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | Electric Equipment | Office | Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | HVAC | All | Mon - Fri | bar: 1 am to 12 am
ApartmentHighRise | HVAC | All | Sat | bar: 1 am to 12 am
ApartmentHighRise | HVAC | All | Sun | bar: 1 am to 12 am
ApartmentHighRise | SWH | All | Mon - Fri | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | SWH | All | Sat | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | SWH | All | Sun | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | Infiltration | All | Mon - Fri | bar: 1 am to 12 am
ApartmentHighRise | Infiltration | All | Sat | bar: 1 am to 12 am
ApartmentHighRise | Infiltration | All | Sun | bar: 1 am to 12 am
ApartmentHighRise | Cooling Set Point | Apartment | Mon - Fri | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | Cooling Set Point | Apartment | Sat | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | Cooling Set Point | Apartment | Sun | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | Cooling Set Point | Office | Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | Cooling Set Point | Office | Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | Cooling Set Point | Office | Sun | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | Heating Set Point | Apartment | Mon - Fri | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | Heating Set Point | Apartment | Sat | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | Heating Set Point | Apartment | Sun | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | Heating Set Point | Office | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | Heating Set Point | Office | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | Heating Set Point | Office | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6

## HVAC System Type Dictionary
Source: ASHRAE Standard 90.1-2019 Table G3.1.1-4
System No. | System Type | Fan Control | Cooling Type (a) | Heating Type (a)
1. PTAC | Packaged terminal air conditioner | Constant volume | Direct expansion | Hot-water fossil fuel boiler
2. PTHP | Packaged terminal heat pump | Constant volume | Direct expansion | Electric heat pump
3. PSZ-AC | Packaged rooftop air conditioner | Constant volume | Direct expansion | Fossil fuel furnace
4. PSZ-HP | Packaged rooftop heat pump | Constant volume | Direct expansion | Electric heat pump
5. Packaged VAV with reheat | Packaged rooftop VAV with reheat | VAV | Direct expansion | Hot-water fossil fuel boiler
6. Packaged VAV with PFP boxes | Packaged rooftop VAV with parallel fan power boxes and reheat | VAV | Direct expansion | Electric resistance
7. VAV with reheat | VAV with reheat | VAV | Chilled water | Hot-water fossil fuel boiler
8. VAV with PFP boxes | VAV with parallel fan-powered boxes and reheat | VAV | Chilled water | Electric resistance
9. Heating and ventilation | Warm air furnace, gas fired | Constant volume | None | Fossil fuel furnace
10. Heating and ventilation | Warm air furnace, electric | Constant volume | None | Electric resistance
11. SZ–VAV | Single-zone VAV | VAV | Chilled water | See note (b).
12. SZ-CV-HW | Single-zone system | Constant volume | Chilled water | Hot-water fossil fuel boiler
13. SZ-CV-ER | Single-zone system | Constant volume | Chilled water | Electric resistance
14. WSHP (CRAC) | Water source heat pump (Computer room air conditioning unit) | Constant volume | Fluid cooler | Hot-water fossil fuel boiler
15. WSHP | Water source heat pump | Constant volume | Fluid cooler | Gas boiler
1.1 PTAC with electric heating | Packaged terminal air conditioner with electric heating | Constant volume | Direct expansion | Electric resistance
3.1 PSZ-AC-Two-speed-fan | Packaged rooftop air conditioner with two speed fan | Two-speed | Direct expansion | Fossil fuel furnace
3. PSZ-AC or 3.1 PSZ-AC-Two-speed-fan (size dependant)
4.1 PSZ-HP-Two-speed-fan | Packaged rooftop heat pump with two speed fan | Two-speed | Direct expansion | Electric heat pump
4.2 PSZ-HP with gas auxiliary heat | Packaged rooftop heat pump with gas auxiliary heat | Constant volume | Direct expansion | Electric heat pump
4. PSZ-HP or 4.1 PSZ-HP-Two-speed-fan (size dependant)
5.1 Packaged VAV with gas central heating and electric reheat | Packaged rooftop VAV with gas central heating and electric reheat | VAV | Direct expansion | Gas central heating and electric reheat
5.2 Packaged VAV with electric central heating and electric reheat | Packaged rooftop VAV with electric central heating and electric reheat | VAV | Direct expansion | Electric central heating and electric reheat
7.1 VAV with electric central heating and electric reheat | VAV with electric central heating and electric reheat | VAV | Chilled water | Electric resistance
7.2 VAV with hydronic central heating and electric reheat | VAV with hydronic central heating and electric reheat | VAV | Chilled water | Hot-water fossil fuel boiler for central heating and electric resistance for reheat
11.1 SZ–VAV with hydronic heating | Single-zone VAV | VAV | Chilled water | Hot-water fossil fuel boiler
11.2 SZ–VAV with electric heating | Single-zone VAV | VAV | Chilled water | Electric resistance
15.1 WSHP with electric boiler | Water source heat pump with electric boiler | Constant volume | Fluid cooler | Electric boiler
16. Four-pipe fan-coil | Four-pipe fan-coil | Constant volume | Chilled water | Hot-water fossil fuel boiler
16.1 Four-pipe fan-coil with DOAS | Four-pipe fan-coil with DOAS | Constant volume | Chilled water | Hot-water fossil fuel boiler
15.2 WSHP with MZ DOAS | Water source heat pump for conditioning, central DOAS for ventilation with ERV without DCV?
4.3 PSZ-HP with DOAS | Packaged rooftop heat pump with DOAS | Constant volume? | Direct expansion | Electric heat pump
No heating and cooling
ideal loads
a. For purchased chilled water and purchased heat, see G3.1.1.3.
b. For Climate Zones 0 through 3A, the heating type shall be electric resistance. For all other climate zones the heating type shall be hot-water fossil-fuel boiler.

## schedule_reorganized (hidden)
[9 empty] | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25
Prototype | Schedule | Space Type | Day of Week |  | Prototype | Schedule | Space Type | Day of Week | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | OfficeSmall-Occupants-All (Except Perimeter_mid_ZN_2)-Mon - Fri | OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.61039 | 1 | 1 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0
OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | OfficeSmall-Occupants-All (Except Perimeter_mid_ZN_2)-Sat | OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | OfficeSmall-Occupants-All (Except Perimeter_mid_ZN_2)-Sun | OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | Lighting | All | Mon - Fri | OfficeSmall-Lighting-All-Mon - Fri | OfficeSmall | Lighting | All | Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.23 | 0.42 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.42 | 0.42 | 0.32 | 0.32 | 0.23 | 0.18
OfficeSmall | Lighting | All | Sat | OfficeSmall-Lighting-All-Sat | OfficeSmall | Lighting | All | Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
OfficeSmall | Lighting | All | Sun | OfficeSmall-Lighting-All-Sun | OfficeSmall | Lighting | All | Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
OfficeSmall | Electric Equipment | All | Mon - Fri | OfficeSmall-Electric Equipment-All-Mon - Fri | OfficeSmall | Electric Equipment | All | Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | Electric Equipment | All | Sat | OfficeSmall-Electric Equipment-All-Sat | OfficeSmall | Electric Equipment | All | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | Electric Equipment | All | Sun | OfficeSmall-Electric Equipment-All-Sun | OfficeSmall | Electric Equipment | All | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | HVAC | All | Mon - Fri | OfficeSmall-HVAC-All-Mon - Fri | OfficeSmall | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OfficeSmall | HVAC | All | Sat | OfficeSmall-HVAC-All-Sat | OfficeSmall | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | HVAC | All | Sun | OfficeSmall-HVAC-All-Sun | OfficeSmall | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | SWH | All | Mon - Fri | OfficeSmall-SWH-All-Mon - Fri | OfficeSmall | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0.55 | 0.64 | 0.64 | 0.82 | 1 | 0.91 | 0.55 | 0.55 | 0.73 | 0.37 | 0.37 | 0.18 | 0.27 | 0.09 | 0 | 0
OfficeSmall | SWH | All | Sat | OfficeSmall-SWH-All-Sat | OfficeSmall | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | SWH | All | Sun | OfficeSmall-SWH-All-Sun | OfficeSmall | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | Infiltration | All | Mon - Fri | OfficeSmall-Infiltration-All-Mon - Fri | OfficeSmall | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Infiltration | All | Sat | OfficeSmall-Infiltration-All-Sat | OfficeSmall | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Infiltration | All | Sun | OfficeSmall-Infiltration-All-Sun | OfficeSmall | Infiltration | All | Sun | bar: 2 to 25
OfficeSmall | Cooling Set Point | All | Mon - Fri | OfficeSmall-Cooling Set Point-All-Mon - Fri | OfficeSmall | Cooling Set Point | All | Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | Cooling Set Point | All | Sat | OfficeSmall-Cooling Set Point-All-Sat | OfficeSmall | Cooling Set Point | All | Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | Cooling Set Point | All | Sun | OfficeSmall-Cooling Set Point-All-Sun | OfficeSmall | Cooling Set Point | All | Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | Heating Set Point | All | Mon - Fri | OfficeSmall-Heating Set Point-All-Mon - Fri | OfficeSmall | Heating Set Point | All | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | Heating Set Point | All | Sat | OfficeSmall-Heating Set Point-All-Sat | OfficeSmall | Heating Set Point | All | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | Heating Set Point | All | Sun | OfficeSmall-Heating Set Point-All-Sun | OfficeSmall | Heating Set Point | All | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | OfficeMedium-Occupants-All (Except Perimeter_mid_ZN_2)-Mon - Fri | OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.9757 | 0.95 | 0.51353 | 0.95 | 0.9757 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | OfficeMedium-Occupants-All (Except Perimeter_mid_ZN_2)-Sat | OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.30812 | 0.3 | 0.10271 | 0.1 | 0.10271 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | OfficeMedium-Occupants-All (Except Perimeter_mid_ZN_2)-Sun | OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | Lighting | All | Mon - Fri | OfficeMedium-Lighting-All-Mon - Fri | OfficeMedium | Lighting | All | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OfficeMedium | Lighting | All | Sat | OfficeMedium-Lighting-All-Sat | OfficeMedium | Lighting | All | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Lighting | All | Sun | OfficeMedium-Lighting-All-Sun | OfficeMedium | Lighting | All | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Electric Equipment | All | Mon - Fri | OfficeMedium-Electric Equipment-All-Mon - Fri | OfficeMedium | Electric Equipment | All | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
OfficeMedium | Electric Equipment | All | Sat | OfficeMedium-Electric Equipment-All-Sat | OfficeMedium | Electric Equipment | All | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeMedium | Electric Equipment | All | Sun | OfficeMedium-Electric Equipment-All-Sun | OfficeMedium | Electric Equipment | All | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeMedium | HVAC | All | Mon - Fri | OfficeMedium-HVAC-All-Mon - Fri | OfficeMedium | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeMedium | HVAC | All | Sat | OfficeMedium-HVAC-All-Sat | OfficeMedium | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | HVAC | All | Sun | OfficeMedium-HVAC-All-Sun | OfficeMedium | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | SWH | All | Mon - Fri | OfficeMedium-SWH-All-Mon - Fri | OfficeMedium | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeMedium | SWH | All | Sat | OfficeMedium-SWH-All-Sat | OfficeMedium | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0
OfficeMedium | SWH | All | Sun | OfficeMedium-SWH-All-Sun | OfficeMedium | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | Elevator | All | Mon - Fri | OfficeMedium-Elevator-All-Mon - Fri | OfficeMedium | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Elevator | All | Sat | OfficeMedium-Elevator-All-Sat | OfficeMedium | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Elevator | All | Sun | OfficeMedium-Elevator-All-Sun | OfficeMedium | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | Infiltration | All | Mon - Fri | OfficeMedium-Infiltration-All-Mon - Fri | OfficeMedium | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeMedium | Infiltration | All | Sat | OfficeMedium-Infiltration-All-Sat | OfficeMedium | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Infiltration | All | Sun | OfficeMedium-Infiltration-All-Sun | OfficeMedium | Infiltration | All | Sun | bar: 2 to 25
OfficeMedium | Cooling Set Point | All | Mon - Fri | OfficeMedium-Cooling Set Point-All-Mon - Fri | OfficeMedium | Cooling Set Point | All | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Cooling Set Point | All | Sat | OfficeMedium-Cooling Set Point-All-Sat | OfficeMedium | Cooling Set Point | All | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Cooling Set Point | All | Sun | OfficeMedium-Cooling Set Point-All-Sun | OfficeMedium | Cooling Set Point | All | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | Heating Set Point | All | Mon - Fri | OfficeMedium-Heating Set Point-All-Mon - Fri | OfficeMedium | Heating Set Point | All | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | Heating Set Point | All | Sat | OfficeMedium-Heating Set Point-All-Sat | OfficeMedium | Heating Set Point | All | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | Heating Set Point | All | Sun | OfficeMedium-Heating Set Point-All-Sun | OfficeMedium | Heating Set Point | All | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | OfficeLarge-Occupants-All (Except Perimeter_mid_ZN_2)-Mon - Fri | OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.99331 | 0.95 | 0.5228 | 0.95 | 0.99331 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | OfficeLarge-Occupants-All (Except Perimeter_mid_ZN_2)-Sat | OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.31368 | 0.3 | 0.10456 | 0.1 | 0.10456 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | OfficeLarge-Occupants-All (Except Perimeter_mid_ZN_2)-Sun | OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | Lighting | All (Except Data Center) | Mon - Fri | OfficeLarge-Lighting-All (Except Data Center)-Mon - Fri | OfficeLarge | Lighting | All (Except Data Center) | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OfficeLarge | Lighting | All (Except Data Center) | Sat | OfficeLarge-Lighting-All (Except Data Center)-Sat | OfficeLarge | Lighting | All (Except Data Center) | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Lighting | All (Except Data Center) | Sun | OfficeLarge-Lighting-All (Except Data Center)-Sun | OfficeLarge | Lighting | All (Except Data Center) | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Mon - Fri | OfficeLarge-Electric Equipment-All (Except Basement and Data Center)-Mon - Fri | OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Sat | OfficeLarge-Electric Equipment-All (Except Basement and Data Center)-Sat | OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Sun | OfficeLarge-Electric Equipment-All (Except Basement and Data Center)-Sun | OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeLarge | HVAC | All | Mon - Fri | OfficeLarge-HVAC-All-Mon - Fri | OfficeLarge | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeLarge | HVAC | All | Sat | OfficeLarge-HVAC-All-Sat | OfficeLarge | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | HVAC | All | Sun | OfficeLarge-HVAC-All-Sun | OfficeLarge | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | SWH | All | Mon - Fri | OfficeLarge-SWH-All-Mon - Fri | OfficeLarge | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeLarge | SWH | All | Sat | OfficeLarge-SWH-All-Sat | OfficeLarge | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
OfficeLarge | SWH | All | Sun | OfficeLarge-SWH-All-Sun | OfficeLarge | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
OfficeLarge | Elevator | All | Mon - Fri | OfficeLarge-Elevator-All-Mon - Fri | OfficeLarge | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | Elevator | All | Sat | OfficeLarge-Elevator-All-Sat | OfficeLarge | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | Elevator | All | Sun | OfficeLarge-Elevator-All-Sun | OfficeLarge | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | Infiltration | All | Mon - Fri | OfficeLarge-Infiltration-All-Mon - Fri | OfficeLarge | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeLarge | Infiltration | All | Sat | OfficeLarge-Infiltration-All-Sat | OfficeLarge | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Infiltration | All | Sun | OfficeLarge-Infiltration-All-Sun | OfficeLarge | Infiltration | All | Sun | bar: 2 to 25
OfficeLarge | Cooling Set Point | All (Except Data Center) | Mon - Fri | OfficeLarge-Cooling Set Point-All (Except Data Center)-Mon - Fri | OfficeLarge | Cooling Set Point | All (Except Data Center) | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | Cooling Set Point | All (Except Data Center) | Sat | OfficeLarge-Cooling Set Point-All (Except Data Center)-Sat | OfficeLarge | Cooling Set Point | All (Except Data Center) | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | Cooling Set Point | All (Except Data Center) | Sun | OfficeLarge-Cooling Set Point-All (Except Data Center)-Sun | OfficeLarge | Cooling Set Point | All (Except Data Center) | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Mon - Fri | OfficeLarge-Heating Set Point-All (Except Basement and Data Center)-Mon - Fri | OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Sat | OfficeLarge-Heating Set Point-All (Except Basement and Data Center)-Sat | OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Sun | OfficeLarge-Heating Set Point-All (Except Basement and Data Center)-Sun | OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
RetailStandalone | Occupants | All | Mon - Fri | RetailStandalone-Occupants-All-Mon - Fri | RetailStandalone | Occupants | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
RetailStandalone | Occupants | All | Sat | RetailStandalone-Occupants-All-Sat | RetailStandalone | Occupants | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
RetailStandalone | Occupants | All | Sun | RetailStandalone-Occupants-All-Sun | RetailStandalone | Occupants | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
RetailStandalone | Lighting | All | Mon - Fri | RetailStandalone-Lighting-All-Mon - Fri | RetailStandalone | Lighting | All | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone | Lighting | All | Sat | RetailStandalone-Lighting-All-Sat | RetailStandalone | Lighting | All | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone | Lighting | All | Sun | RetailStandalone-Lighting-All-Sun | RetailStandalone | Lighting | All | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone | Electric Equipment | All | Mon - Fri | RetailStandalone-Electric Equipment-All-Mon - Fri | RetailStandalone | Electric Equipment | All | Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2
RetailStandalone | Electric Equipment | All | Sat | RetailStandalone-Electric Equipment-All-Sat | RetailStandalone | Electric Equipment | All | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
RetailStandalone | Electric Equipment | All | Sun | RetailStandalone-Electric Equipment-All-Sun | RetailStandalone | Electric Equipment | All | Sun | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
RetailStandalone | HVAC | All | Mon - Fri | RetailStandalone-HVAC-All-Mon - Fri | RetailStandalone | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStandalone | HVAC | All | Sat | RetailStandalone-HVAC-All-Sat | RetailStandalone | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
RetailStandalone | HVAC | All | Sun | RetailStandalone-HVAC-All-Sun | RetailStandalone | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStandalone | SWH | All | Mon - Fri | RetailStandalone-SWH-All-Mon - Fri | RetailStandalone | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0
RetailStandalone | SWH | All | Sat | RetailStandalone-SWH-All-Sat | RetailStandalone | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0
RetailStandalone | SWH | All | Sun | RetailStandalone-SWH-All-Sun | RetailStandalone | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0
RetailStandalone | Infiltration | All | Mon - Fri | RetailStandalone-Infiltration-All-Mon - Fri | RetailStandalone | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStandalone | Infiltration | All | Sat | RetailStandalone-Infiltration-All-Sat | RetailStandalone | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
RetailStandalone | Infiltration | All | Sun | RetailStandalone-Infiltration-All-Sun | RetailStandalone | Infiltration | All | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Mon - Fri | RetailStandalone-Cooling Set Point-All (Except Front_Entry)-Mon - Fri | RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Sat | RetailStandalone-Cooling Set Point-All (Except Front_Entry)-Sat | RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Sun | RetailStandalone-Cooling Set Point-All (Except Front_Entry)-Sun | RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | Heating Set Point | All (Except Core_Retail) | Mon - Fri | RetailStandalone-Heating Set Point-All (Except Core_Retail)-Mon - Fri | RetailStandalone | Heating Set Point | All (Except Core_Retail) | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone | Heating Set Point | All (Except Core_Retail) | Sat | RetailStandalone-Heating Set Point-All (Except Core_Retail)-Sat | RetailStandalone | Heating Set Point | All (Except Core_Retail) | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone | Heating Set Point | All (Except Core_Retail) | Sun | RetailStandalone-Heating Set Point-All (Except Core_Retail)-Sun | RetailStandalone | Heating Set Point | All (Except Core_Retail) | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Occupants | Type 1 Store | Mon - Thu | RetailStripmall-Occupants-Type 1 Store-Mon - Thu | RetailStripmall | Occupants | Type 1 Store | Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.05
RetailStripmall | Occupants | Type 1 Store | Fri, Sat | RetailStripmall-Occupants-Type 1 Store-Fri, Sat | RetailStripmall | Occupants | Type 1 Store | Fri, Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.6 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2
RetailStripmall | Occupants | Type 1 Store | Sun | RetailStripmall-Occupants-Type 1 Store-Sun | RetailStripmall | Occupants | Type 1 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.4 | 0.3 | 0.6 | 0.6 | 0.4 | 0.4 | 0.3 | 0.2 | 0.05
RetailStripmall | Occupants | Type 2 Store | Mon - Fri | RetailStripmall-Occupants-Type 2 Store-Mon - Fri | RetailStripmall | Occupants | Type 2 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.3 | 0.2 | 0.2 | 0.5 | 0.5 | 0.2 | 0.05 | 0 | 0 | 0
RetailStripmall | Occupants | Type 2 Store | Sat | RetailStripmall-Occupants-Type 2 Store-Sat | RetailStripmall | Occupants | Type 2 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 0.05 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Occupants | Type 2 Store | Sun | RetailStripmall-Occupants-Type 2 Store-Sun | RetailStripmall | Occupants | Type 2 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Occupants | Type 3 Store | Mon - Fri | RetailStripmall-Occupants-Type 3 Store-Mon - Fri | RetailStripmall | Occupants | Type 3 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.71 | 0.5 | 0.69 | 0.54 | 0.71 | 0.34 | 0.26 | 0.11 | 0 | 0 | 0
RetailStripmall | Occupants | Type 3 Store | Sat | RetailStripmall-Occupants-Type 3 Store-Sat | RetailStripmall | Occupants | Type 3 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.58 | 0.71 | 0.74 | 0.77 | 0.8 | 0.74 | 0.54 | 0.11 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Occupants | Type 3 Store | Sun | RetailStripmall-Occupants-Type 3 Store-Sun | RetailStripmall | Occupants | Type 3 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.5 | 0.69 | 0.34 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Lighting | Type 1 Small Store | Mon - Fri | RetailStripmall-Lighting-Type 1 Small Store-Mon - Fri | RetailStripmall | Lighting | Type 1 Small Store | Mon - Fri | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.502
RetailStripmall | Lighting | Type 1 Small Store | Sat | RetailStripmall-Lighting-Type 1 Small Store-Sat | RetailStripmall | Lighting | Type 1 Small Store | Sat | 0.502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538
RetailStripmall | Lighting | Type 1 Small Store | Sun | RetailStripmall-Lighting-Type 1 Small Store-Sun | RetailStripmall | Lighting | Type 1 Small Store | Sun | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.502
RetailStripmall | Lighting | Type 1 Large Store | Mon - Fri | RetailStripmall-Lighting-Type 1 Large Store-Mon - Fri | RetailStripmall | Lighting | Type 1 Large Store | Mon - Fri | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.50075
RetailStripmall | Lighting | Type 1 Large Store | Sat | RetailStripmall-Lighting-Type 1 Large Store-Sat | RetailStripmall | Lighting | Type 1 Large Store | Sat | 0.50075 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142
RetailStripmall | Lighting | Type 1 Large Store | Sun | RetailStripmall-Lighting-Type 1 Large Store-Sun | RetailStripmall | Lighting | Type 1 Large Store | Sun | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.50075
RetailStripmall | Lighting | Type 2 Small Store | Mon - Fri | RetailStripmall-Lighting-Type 2 Small Store-Mon - Fri | RetailStripmall | Lighting | Type 2 Small Store | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 2 Small Store | Sat | RetailStripmall-Lighting-Type 2 Small Store-Sat | RetailStripmall | Lighting | Type 2 Small Store | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 2 Small Store | Sun | RetailStripmall-Lighting-Type 2 Small Store-Sun | RetailStripmall | Lighting | Type 2 Small Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 2 Large Store | Mon - Fri | RetailStripmall-Lighting-Type 2 Large Store-Mon - Fri | RetailStripmall | Lighting | Type 2 Large Store | Mon - Fri | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | Lighting | Type 2 Large Store | Sat | RetailStripmall-Lighting-Type 2 Large Store-Sat | RetailStripmall | Lighting | Type 2 Large Store | Sat | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | Lighting | Type 2 Large Store | Sun | RetailStripmall-Lighting-Type 2 Large Store-Sun | RetailStripmall | Lighting | Type 2 Large Store | Sun | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | Lighting | Type 3 Store | Mon - Fri | RetailStripmall-Lighting-Type 3 Store-Mon - Fri | RetailStripmall | Lighting | Type 3 Store | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 3 Store | Sat | RetailStripmall-Lighting-Type 3 Store-Sat | RetailStripmall | Lighting | Type 3 Store | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Lighting | Type 3 Store | Sun | RetailStripmall-Lighting-Type 3 Store-Sun | RetailStripmall | Lighting | Type 3 Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 1 Store | Mon - Thu | RetailStripmall-Electric Equipment-Type 1 Store-Mon - Thu | RetailStripmall | Electric Equipment | Type 1 Store | Mon - Thu | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
RetailStripmall | Electric Equipment | Type 1 Store | Fri, Sat | RetailStripmall-Electric Equipment-Type 1 Store-Fri, Sat | RetailStripmall | Electric Equipment | Type 1 Store | Fri, Sat | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
RetailStripmall | Electric Equipment | Type 1 Store | Sun | RetailStripmall-Electric Equipment-Type 1 Store-Sun | RetailStripmall | Electric Equipment | Type 1 Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
RetailStripmall | Electric Equipment | Type 2 Store | Mon - Fri | RetailStripmall-Electric Equipment-Type 2 Store-Mon - Fri | RetailStripmall | Electric Equipment | Type 2 Store | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 2 Store | Sat | RetailStripmall-Electric Equipment-Type 2 Store-Sat | RetailStripmall | Electric Equipment | Type 2 Store | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 2 Store | Sun | RetailStripmall-Electric Equipment-Type 2 Store-Sun | RetailStripmall | Electric Equipment | Type 2 Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 3 Store | Mon - Fri | RetailStripmall-Electric Equipment-Type 3 Store-Mon - Fri | RetailStripmall | Electric Equipment | Type 3 Store | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 3 Store | Sat | RetailStripmall-Electric Equipment-Type 3 Store-Sat | RetailStripmall | Electric Equipment | Type 3 Store | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Electric Equipment | Type 3 Store | Sun | RetailStripmall-Electric Equipment-Type 3 Store-Sun | RetailStripmall | Electric Equipment | Type 3 Store | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | HVAC | Type 1 Store | Mon - Thu | RetailStripmall-HVAC-Type 1 Store-Mon - Thu | RetailStripmall | HVAC | Type 1 Store | Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | HVAC | Type 1 Store | Fri, Sat | RetailStripmall-HVAC-Type 1 Store-Fri, Sat | RetailStripmall | HVAC | Type 1 Store | Fri, Sat | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | HVAC | Type 1 Store | Sun | RetailStripmall-HVAC-Type 1 Store-Sun | RetailStripmall | HVAC | Type 1 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | HVAC | Type 2 Store | Mon - Fri | RetailStripmall-HVAC-Type 2 Store-Mon - Fri | RetailStripmall | HVAC | Type 2 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall | HVAC | Type 2 Store | Sat | RetailStripmall-HVAC-Type 2 Store-Sat | RetailStripmall | HVAC | Type 2 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall | HVAC | Type 2 Store | Sun | RetailStripmall-HVAC-Type 2 Store-Sun | RetailStripmall | HVAC | Type 2 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | HVAC | Type 3 Store | Mon - Fri | RetailStripmall-HVAC-Type 3 Store-Mon - Fri | RetailStripmall | HVAC | Type 3 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall | HVAC | Type 3 Store | Sat | RetailStripmall-HVAC-Type 3 Store-Sat | RetailStripmall | HVAC | Type 3 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall | HVAC | Type 3 Store | Sun | RetailStripmall-HVAC-Type 3 Store-Sun | RetailStripmall | HVAC | Type 3 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | SWH | Type 1 Store | Mon - Thu | RetailStripmall-SWH-Type 1 Store-Mon - Thu | RetailStripmall | SWH | Type 1 Store | Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.62 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall | SWH | Type 1 Store | Fri, Sat | RetailStripmall-SWH-Type 1 Store-Fri, Sat | RetailStripmall | SWH | Type 1 Store | Fri, Sat | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0.32 | 0.41 | 0.65 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall | SWH | Type 1 Store | Sun | RetailStripmall-SWH-Type 1 Store-Sun | RetailStripmall | SWH | Type 1 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.16 | 0.1
RetailStripmall | SWH | Type 2 Store | Mon - Fri | RetailStripmall-SWH-Type 2 Store-Mon - Fri | RetailStripmall | SWH | Type 2 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0
RetailStripmall | SWH | Type 2 Store | Sat | RetailStripmall-SWH-Type 2 Store-Sat | RetailStripmall | SWH | Type 2 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.62 | 0.6 | 0.5 | 0.48 | 0.47 | 0.34 | 0 | 0 | 0 | 0 | 0
RetailStripmall | SWH | Type 2 Store | Sun | RetailStripmall-SWH-Type 2 Store-Sun | RetailStripmall | SWH | Type 2 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.14 | 0.29 | 0.33 | 0.4 | 0.36 | 0.37 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | SWH | Type 3 Store | Mon - Fri | RetailStripmall-SWH-Type 3 Store-Mon - Fri | RetailStripmall | SWH | Type 3 Store | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.25 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0
RetailStripmall | SWH | Type 3 Store | Sat | RetailStripmall-SWH-Type 3 Store-Sat | RetailStripmall | SWH | Type 3 Store | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0 | 0 | 0 | 0 | 0
RetailStripmall | SWH | Type 3 Store | Sun | RetailStripmall-SWH-Type 3 Store-Sun | RetailStripmall | SWH | Type 3 Store | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Infiltration | Type 1 Store | Mon - Thu | RetailStripmall-Infiltration-Type 1 Store-Mon - Thu | RetailStripmall | Infiltration | Type 1 Store | Mon - Thu | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Infiltration | Type 1 Store | Fri, Sat | RetailStripmall-Infiltration-Type 1 Store-Fri, Sat | RetailStripmall | Infiltration | Type 1 Store | Fri, Sat | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Infiltration | Type 1 Store | Sun | RetailStripmall-Infiltration-Type 1 Store-Sun | RetailStripmall | Infiltration | Type 1 Store | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Infiltration | Type 2 Store | Mon - Fri | RetailStripmall-Infiltration-Type 2 Store-Mon - Fri | RetailStripmall | Infiltration | Type 2 Store | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 2 Store | Sat | RetailStripmall-Infiltration-Type 2 Store-Sat | RetailStripmall | Infiltration | Type 2 Store | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 2 Store | Sun | RetailStripmall-Infiltration-Type 2 Store-Sun | RetailStripmall | Infiltration | Type 2 Store | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 3 Store | Mon - Fri | RetailStripmall-Infiltration-Type 3 Store-Mon - Fri | RetailStripmall | Infiltration | Type 3 Store | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 3 Store | Sat | RetailStripmall-Infiltration-Type 3 Store-Sat | RetailStripmall | Infiltration | Type 3 Store | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Infiltration | Type 3 Store | Sun | RetailStripmall-Infiltration-Type 3 Store-Sun | RetailStripmall | Infiltration | Type 3 Store | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Cooling Set Point | All | Mon - Fri | RetailStripmall-Cooling Set Point-All-Mon - Fri | RetailStripmall | Cooling Set Point | All | Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Cooling Set Point | All | Sat | RetailStripmall-Cooling Set Point-All-Sat | RetailStripmall | Cooling Set Point | All | Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Cooling Set Point | All | Sun | RetailStripmall-Cooling Set Point-All-Sun | RetailStripmall | Cooling Set Point | All | Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Heating Set Point | Type 1 Store | Mon - Thu | RetailStripmall-Heating Set Point-Type 1 Store-Mon - Thu | RetailStripmall | Heating Set Point | Type 1 Store | Mon - Thu | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Heating Set Point | Type 1 Store | Fri, Sat | RetailStripmall-Heating Set Point-Type 1 Store-Fri, Sat | RetailStripmall | Heating Set Point | Type 1 Store | Fri, Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Heating Set Point | Type 1 Store | Sun | RetailStripmall-Heating Set Point-Type 1 Store-Sun | RetailStripmall | Heating Set Point | Type 1 Store | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Heating Set Point | Type 2 Store | Mon - Fri | RetailStripmall-Heating Set Point-Type 2 Store-Mon - Fri | RetailStripmall | Heating Set Point | Type 2 Store | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 2 Store | Sat | RetailStripmall-Heating Set Point-Type 2 Store-Sat | RetailStripmall | Heating Set Point | Type 2 Store | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 2 Store | Sun | RetailStripmall-Heating Set Point-Type 2 Store-Sun | RetailStripmall | Heating Set Point | Type 2 Store | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 3 Store | Mon - Fri | RetailStripmall-Heating Set Point-Type 3 Store-Mon - Fri | RetailStripmall | Heating Set Point | Type 3 Store | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 3 Store | Sat | RetailStripmall-Heating Set Point-Type 3 Store-Sat | RetailStripmall | Heating Set Point | Type 3 Store | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Heating Set Point | Type 3 Store | Sun | RetailStripmall-Heating Set Point-Type 3 Store-Sun | RetailStripmall | Heating Set Point | Type 3 Store | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Computer Classroom (Study Periods)-Mon - Fri | SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Sat | SchoolPrimary-Occupants-Computer Classroom (Study Periods)-Sat | SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Sun | SchoolPrimary-Occupants-Computer Classroom (Study Periods)-Sun | SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Computer Classroom (Summer Holiday)-Mon - Fri | SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Sat | SchoolPrimary-Occupants-Computer Classroom (Summer Holiday)-Sat | SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Sun | SchoolPrimary-Occupants-Computer Classroom (Summer Holiday)-Sun | SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Office (Study Periods)-Mon - Fri | SchoolPrimary | Occupants | Office (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Study Periods) | Sat | SchoolPrimary-Occupants-Office (Study Periods)-Sat | SchoolPrimary | Occupants | Office (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Study Periods) | Sun | SchoolPrimary-Occupants-Office (Study Periods)-Sun | SchoolPrimary | Occupants | Office (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Office (Summer Holiday)-Mon - Fri | SchoolPrimary | Occupants | Office (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Summer Holiday) | Sat | SchoolPrimary-Occupants-Office (Summer Holiday)-Sat | SchoolPrimary | Occupants | Office (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Office (Summer Holiday) | Sun | SchoolPrimary-Occupants-Office (Summer Holiday)-Sun | SchoolPrimary | Occupants | Office (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Gym (Study Periods)-Mon - Fri | SchoolPrimary | Occupants | Gym (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Study Periods) | Sat | SchoolPrimary-Occupants-Gym (Study Periods)-Sat | SchoolPrimary | Occupants | Gym (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Study Periods) | Sun | SchoolPrimary-Occupants-Gym (Study Periods)-Sun | SchoolPrimary | Occupants | Gym (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Gym (Summer Holiday)-Mon - Fri | SchoolPrimary | Occupants | Gym (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Summer Holiday) | Sat | SchoolPrimary-Occupants-Gym (Summer Holiday)-Sat | SchoolPrimary | Occupants | Gym (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Gym (Summer Holiday) | Sun | SchoolPrimary-Occupants-Gym (Summer Holiday)-Sun | SchoolPrimary | Occupants | Gym (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Cafeteria (Study Periods)-Mon - Fri | SchoolPrimary | Occupants | Cafeteria (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Study Periods) | Sat | SchoolPrimary-Occupants-Cafeteria (Study Periods)-Sat | SchoolPrimary | Occupants | Cafeteria (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Study Periods) | Sun | SchoolPrimary-Occupants-Cafeteria (Study Periods)-Sun | SchoolPrimary | Occupants | Cafeteria (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Cafeteria (Summer Holiday)-Mon - Fri | SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Sat | SchoolPrimary-Occupants-Cafeteria (Summer Holiday)-Sat | SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Sun | SchoolPrimary-Occupants-Cafeteria (Summer Holiday)-Sun | SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Others (Study Periods)-Mon - Fri | SchoolPrimary | Occupants | Others (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Study Periods) | Sat | SchoolPrimary-Occupants-Others (Study Periods)-Sat | SchoolPrimary | Occupants | Others (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Study Periods) | Sun | SchoolPrimary-Occupants-Others (Study Periods)-Sun | SchoolPrimary | Occupants | Others (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Others (Summer Holiday)-Mon - Fri | SchoolPrimary | Occupants | Others (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Summer Holiday) | Sat | SchoolPrimary-Occupants-Others (Summer Holiday)-Sat | SchoolPrimary | Occupants | Others (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Occupants | Others (Summer Holiday) | Sun | SchoolPrimary-Occupants-Others (Summer Holiday)-Sun | SchoolPrimary | Occupants | Others (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Lighting | All (Study Periods) | Mon - Fri | SchoolPrimary-Lighting-All (Study Periods)-Mon - Fri | SchoolPrimary | Lighting | All (Study Periods) | Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Study Periods) | Sat | SchoolPrimary-Lighting-All (Study Periods)-Sat | SchoolPrimary | Lighting | All (Study Periods) | Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Study Periods) | Sun | SchoolPrimary-Lighting-All (Study Periods)-Sun | SchoolPrimary | Lighting | All (Study Periods) | Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Summer Holiday) | Mon - Fri | SchoolPrimary-Lighting-All (Summer Holiday)-Mon - Fri | SchoolPrimary | Lighting | All (Summer Holiday) | Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Summer Holiday) | Sat | SchoolPrimary-Lighting-All (Summer Holiday)-Sat | SchoolPrimary | Lighting | All (Summer Holiday) | Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Lighting | All (Summer Holiday) | Sun | SchoolPrimary-Lighting-All (Summer Holiday)-Sun | SchoolPrimary | Lighting | All (Summer Holiday) | Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Mon - Fri | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Mon - Fri | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sat | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Sat | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sun | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Sun | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Mon - Fri | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Mon - Fri | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sat | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Sat | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sun | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Sun | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | Electric Equipment | Others (Study Periods) | Mon - Fri | SchoolPrimary-Electric Equipment-Others (Study Periods)-Mon - Fri | SchoolPrimary | Electric Equipment | Others (Study Periods) | Mon - Fri | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | Electric Equipment | Others (Study Periods) | Sat | SchoolPrimary-Electric Equipment-Others (Study Periods)-Sat | SchoolPrimary | Electric Equipment | Others (Study Periods) | Sat | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | Electric Equipment | Others (Study Periods) | Sun | SchoolPrimary-Electric Equipment-Others (Study Periods)-Sun | SchoolPrimary | Electric Equipment | Others (Study Periods) | Sun | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Mon - Fri | SchoolPrimary-Electric Equipment-Others (Summer Holiday)-Mon - Fri | SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Sat | SchoolPrimary-Electric Equipment-Others (Summer Holiday)-Sat | SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Sun | SchoolPrimary-Electric Equipment-Others (Summer Holiday)-Sun | SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | Gas Equipment | Kitchen | Mon - Fri | SchoolPrimary-Gas Equipment-Kitchen-Mon - Fri | SchoolPrimary | Gas Equipment | Kitchen | Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | Gas Equipment | Kitchen | Sat | SchoolPrimary-Gas Equipment-Kitchen-Sat | SchoolPrimary | Gas Equipment | Kitchen | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | Gas Equipment | Kitchen | Sun | SchoolPrimary-Gas Equipment-Kitchen-Sun | SchoolPrimary | Gas Equipment | Kitchen | Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | HVAC | All | Mon - Fri | SchoolPrimary-HVAC-All-Mon - Fri | SchoolPrimary | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary | HVAC | All | Sat | SchoolPrimary-HVAC-All-Sat | SchoolPrimary | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | HVAC | All | Sun | SchoolPrimary-HVAC-All-Sun | SchoolPrimary | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Study Periods) | Mon - Fri | SchoolPrimary-SWH-All (Study Periods)-Mon - Fri | SchoolPrimary | SWH | All (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Study Periods) | Sat | SchoolPrimary-SWH-All (Study Periods)-Sat | SchoolPrimary | SWH | All (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Study Periods) | Sun | SchoolPrimary-SWH-All (Study Periods)-Sun | SchoolPrimary | SWH | All (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Summer Holiday) | Mon - Fri | SchoolPrimary-SWH-All (Summer Holiday)-Mon - Fri | SchoolPrimary | SWH | All (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Summer Holiday) | Sat | SchoolPrimary-SWH-All (Summer Holiday)-Sat | SchoolPrimary | SWH | All (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SWH | All (Summer Holiday) | Sun | SchoolPrimary-SWH-All (Summer Holiday)-Sun | SchoolPrimary | SWH | All (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Infiltration | All | Mon - Fri | SchoolPrimary-Infiltration-All-Mon - Fri | SchoolPrimary | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolPrimary | Infiltration | All | Sat | SchoolPrimary-Infiltration-All-Sat | SchoolPrimary | Infiltration | All | Sat | bar: 2 to 25
SchoolPrimary | Infiltration | All | Sun | SchoolPrimary-Infiltration-All-Sun | SchoolPrimary | Infiltration | All | Sun | bar: 2 to 25
SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Mon - Fri | SchoolPrimary-Cooling Set Point-Gym, Kitchen, Cafeteria-Mon - Fri | SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Sat | SchoolPrimary-Cooling Set Point-Gym, Kitchen, Cafeteria-Sat | SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Sun | SchoolPrimary-Cooling Set Point-Gym, Kitchen, Cafeteria-Sun | SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Mon - Fri | SchoolPrimary-Cooling Set Point-Mechanical Room, Bathroom-Mon - Fri | SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Sat | SchoolPrimary-Cooling Set Point-Mechanical Room, Bathroom-Sat | SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Sun | SchoolPrimary-Cooling Set Point-Mechanical Room, Bathroom-Sun | SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | Cooling Set Point | Others | Mon - Fri | SchoolPrimary-Cooling Set Point-Others-Mon - Fri | SchoolPrimary | Cooling Set Point | Others | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | Cooling Set Point | Others | Sat | SchoolPrimary-Cooling Set Point-Others-Sat | SchoolPrimary | Cooling Set Point | Others | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | Cooling Set Point | Others | Sun | SchoolPrimary-Cooling Set Point-Others-Sun | SchoolPrimary | Cooling Set Point | Others | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Mon - Fri | SchoolPrimary-Heating Set Point-Mechanical Room, Bathroom-Mon - Fri | SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Sat | SchoolPrimary-Heating Set Point-Mechanical Room, Bathroom-Sat | SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Sun | SchoolPrimary-Heating Set Point-Mechanical Room, Bathroom-Sun | SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Others | Mon - Fri | SchoolPrimary-Heating Set Point-Others-Mon - Fri | SchoolPrimary | Heating Set Point | Others | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Others | Sat | SchoolPrimary-Heating Set Point-Others-Sat | SchoolPrimary | Heating Set Point | Others | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | Heating Set Point | Others | Sun | SchoolPrimary-Heating Set Point-Others-Sun | SchoolPrimary | Heating Set Point | Others | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods)-Mon - Fri | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Sat | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods)-Sat | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Sun | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods)-Sun | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday)-Mon - Fri | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Sat | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday)-Sat | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Sun | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday)-Sun | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Office (Study Periods)-Mon - Fri | SchoolSecondary | Occupants | Office (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Study Periods) | Sat | SchoolSecondary-Occupants-Office (Study Periods)-Sat | SchoolSecondary | Occupants | Office (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Study Periods) | Sun | SchoolSecondary-Occupants-Office (Study Periods)-Sun | SchoolSecondary | Occupants | Office (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Office (Summer Holiday)-Mon - Fri | SchoolSecondary | Occupants | Office (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Summer Holiday) | Sat | SchoolSecondary-Occupants-Office (Summer Holiday)-Sat | SchoolSecondary | Occupants | Office (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Office (Summer Holiday) | Sun | SchoolSecondary-Occupants-Office (Summer Holiday)-Sun | SchoolSecondary | Occupants | Office (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Gym (Study Periods)-Mon - Fri | SchoolSecondary | Occupants | Gym (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Study Periods) | Sat | SchoolSecondary-Occupants-Gym (Study Periods)-Sat | SchoolSecondary | Occupants | Gym (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Study Periods) | Sun | SchoolSecondary-Occupants-Gym (Study Periods)-Sun | SchoolSecondary | Occupants | Gym (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Gym (Summer Holiday)-Mon - Fri | SchoolSecondary | Occupants | Gym (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Summer Holiday) | Sat | SchoolSecondary-Occupants-Gym (Summer Holiday)-Sat | SchoolSecondary | Occupants | Gym (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Gym (Summer Holiday) | Sun | SchoolSecondary-Occupants-Gym (Summer Holiday)-Sun | SchoolSecondary | Occupants | Gym (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Auditorium (Study Periods)-Mon - Fri | SchoolSecondary | Occupants | Auditorium (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Study Periods) | Sat | SchoolSecondary-Occupants-Auditorium (Study Periods)-Sat | SchoolSecondary | Occupants | Auditorium (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Study Periods) | Sun | SchoolSecondary-Occupants-Auditorium (Study Periods)-Sun | SchoolSecondary | Occupants | Auditorium (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Auditorium (Summer Holiday)-Mon - Fri | SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Sat | SchoolSecondary-Occupants-Auditorium (Summer Holiday)-Sat | SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Sun | SchoolSecondary-Occupants-Auditorium (Summer Holiday)-Sun | SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Cafeteria (Study Periods)-Mon - Fri | SchoolSecondary | Occupants | Cafeteria (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Study Periods) | Sat | SchoolSecondary-Occupants-Cafeteria (Study Periods)-Sat | SchoolSecondary | Occupants | Cafeteria (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Study Periods) | Sun | SchoolSecondary-Occupants-Cafeteria (Study Periods)-Sun | SchoolSecondary | Occupants | Cafeteria (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Cafeteria (Summer Holiday)-Mon - Fri | SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Sat | SchoolSecondary-Occupants-Cafeteria (Summer Holiday)-Sat | SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Sun | SchoolSecondary-Occupants-Cafeteria (Summer Holiday)-Sun | SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Others (Study Periods)-Mon - Fri | SchoolSecondary | Occupants | Others (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Study Periods) | Sat | SchoolSecondary-Occupants-Others (Study Periods)-Sat | SchoolSecondary | Occupants | Others (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Study Periods) | Sun | SchoolSecondary-Occupants-Others (Study Periods)-Sun | SchoolSecondary | Occupants | Others (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Others (Summer Holiday)-Mon - Fri | SchoolSecondary | Occupants | Others (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Summer Holiday) | Sat | SchoolSecondary-Occupants-Others (Summer Holiday)-Sat | SchoolSecondary | Occupants | Others (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Occupants | Others (Summer Holiday) | Sun | SchoolSecondary-Occupants-Others (Summer Holiday)-Sun | SchoolSecondary | Occupants | Others (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Lighting | All (Study Periods) | Mon - Fri | SchoolSecondary-Lighting-All (Study Periods)-Mon - Fri | SchoolSecondary | Lighting | All (Study Periods) | Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Study Periods) | Sat | SchoolSecondary-Lighting-All (Study Periods)-Sat | SchoolSecondary | Lighting | All (Study Periods) | Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Study Periods) | Sun | SchoolSecondary-Lighting-All (Study Periods)-Sun | SchoolSecondary | Lighting | All (Study Periods) | Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Summer Holiday) | Mon - Fri | SchoolSecondary-Lighting-All (Summer Holiday)-Mon - Fri | SchoolSecondary | Lighting | All (Summer Holiday) | Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Summer Holiday) | Sat | SchoolSecondary-Lighting-All (Summer Holiday)-Sat | SchoolSecondary | Lighting | All (Summer Holiday) | Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Lighting | All (Summer Holiday) | Sun | SchoolSecondary-Lighting-All (Summer Holiday)-Sun | SchoolSecondary | Lighting | All (Summer Holiday) | Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Mon - Fri | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Mon - Fri | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sat | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Sat | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sun | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Sun | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Mon - Fri | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Mon - Fri | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sat | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Sat | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sun | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Sun | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | Electric Equipment | Others (Study Periods) | Mon - Fri | SchoolSecondary-Electric Equipment-Others (Study Periods)-Mon - Fri | SchoolSecondary | Electric Equipment | Others (Study Periods) | Mon - Fri | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | Electric Equipment | Others (Study Periods) | Sat | SchoolSecondary-Electric Equipment-Others (Study Periods)-Sat | SchoolSecondary | Electric Equipment | Others (Study Periods) | Sat | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | Electric Equipment | Others (Study Periods) | Sun | SchoolSecondary-Electric Equipment-Others (Study Periods)-Sun | SchoolSecondary | Electric Equipment | Others (Study Periods) | Sun | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Mon - Fri | SchoolSecondary-Electric Equipment-Others (Summer Holiday)-Mon - Fri | SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Sat | SchoolSecondary-Electric Equipment-Others (Summer Holiday)-Sat | SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Sun | SchoolSecondary-Electric Equipment-Others (Summer Holiday)-Sun | SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | Gas Equipment | Kitchen | Mon - Fri | SchoolSecondary-Gas Equipment-Kitchen-Mon - Fri | SchoolSecondary | Gas Equipment | Kitchen | Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | Gas Equipment | Kitchen | Sat | SchoolSecondary-Gas Equipment-Kitchen-Sat | SchoolSecondary | Gas Equipment | Kitchen | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | Gas Equipment | Kitchen | Sun | SchoolSecondary-Gas Equipment-Kitchen-Sun | SchoolSecondary | Gas Equipment | Kitchen | Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | HVAC | All | Mon - Fri | SchoolSecondary-HVAC-All-Mon - Fri | SchoolSecondary | HVAC | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary | HVAC | All | Sat | SchoolSecondary-HVAC-All-Sat | SchoolSecondary | HVAC | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | HVAC | All | Sun | SchoolSecondary-HVAC-All-Sun | SchoolSecondary | HVAC | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Study Periods) | Mon - Fri | SchoolSecondary-SWH-All (Study Periods)-Mon - Fri | SchoolSecondary | SWH | All (Study Periods) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Study Periods) | Sat | SchoolSecondary-SWH-All (Study Periods)-Sat | SchoolSecondary | SWH | All (Study Periods) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Study Periods) | Sun | SchoolSecondary-SWH-All (Study Periods)-Sun | SchoolSecondary | SWH | All (Study Periods) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Summer Holiday) | Mon - Fri | SchoolSecondary-SWH-All (Summer Holiday)-Mon - Fri | SchoolSecondary | SWH | All (Summer Holiday) | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Summer Holiday) | Sat | SchoolSecondary-SWH-All (Summer Holiday)-Sat | SchoolSecondary | SWH | All (Summer Holiday) | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SWH | All (Summer Holiday) | Sun | SchoolSecondary-SWH-All (Summer Holiday)-Sun | SchoolSecondary | SWH | All (Summer Holiday) | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Elevator | All | Mon - Fri | SchoolSecondary-Elevator-All-Mon - Fri | SchoolSecondary | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | Elevator | All | Sat | SchoolSecondary-Elevator-All-Sat | SchoolSecondary | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | Elevator | All | Sun | SchoolSecondary-Elevator-All-Sun | SchoolSecondary | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | Infiltration | All | Mon - Fri | SchoolSecondary-Infiltration-All-Mon - Fri | SchoolSecondary | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolSecondary | Infiltration | All | Sat | SchoolSecondary-Infiltration-All-Sat | SchoolSecondary | Infiltration | All | Sat | bar: 2 to 25
SchoolSecondary | Infiltration | All | Sun | SchoolSecondary-Infiltration-All-Sun | SchoolSecondary | Infiltration | All | Sun | bar: 2 to 25
SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Mon - Fri | SchoolSecondary-Cooling Set Point-Bathrooms, Mechanical Rooms-Mon - Fri | SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Mon - Fri | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Sat | SchoolSecondary-Cooling Set Point-Bathrooms, Mechanical Rooms-Sat | SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Sat | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Sun | SchoolSecondary-Cooling Set Point-Bathrooms, Mechanical Rooms-Sun | SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Sun | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | Cooling Set Point | Others | Mon - Fri | SchoolSecondary-Cooling Set Point-Others-Mon - Fri | SchoolSecondary | Cooling Set Point | Others | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | Cooling Set Point | Others | Sat | SchoolSecondary-Cooling Set Point-Others-Sat | SchoolSecondary | Cooling Set Point | Others | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | Cooling Set Point | Others | Sun | SchoolSecondary-Cooling Set Point-Others-Sun | SchoolSecondary | Cooling Set Point | Others | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Mon - Fri | SchoolSecondary-Heating Set Point-Bathrooms, Mechanical Rooms-Mon - Fri | SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Sat | SchoolSecondary-Heating Set Point-Bathrooms, Mechanical Rooms-Sat | SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Sun | SchoolSecondary-Heating Set Point-Bathrooms, Mechanical Rooms-Sun | SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Mon - Fri | SchoolSecondary-Heating Set Point-Gym, Auditorium, Kitchen, Cafeteria-Mon - Fri | SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Sat | SchoolSecondary-Heating Set Point-Gym, Auditorium, Kitchen, Cafeteria-Sat | SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Sun | SchoolSecondary-Heating Set Point-Gym, Auditorium, Kitchen, Cafeteria-Sun | SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Others | Mon - Fri | SchoolSecondary-Heating Set Point-Others-Mon - Fri | SchoolSecondary | Heating Set Point | Others | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Others | Sat | SchoolSecondary-Heating Set Point-Others-Sat | SchoolSecondary | Heating Set Point | Others | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | Heating Set Point | Others | Sun | SchoolSecondary-Heating Set Point-Others-Sun | SchoolSecondary | Heating Set Point | Others | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Mon - Fri | OutPatientHealthCare-Occupants-Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work-Mon - Fri | OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0.9 | 0 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Sat | OutPatientHealthCare-Occupants-Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work-Sat | OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0 | 0.3 | 0.3 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Sun | OutPatientHealthCare-Occupants-Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work-Sun | OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | Occupants | Conference Room | Mon - Fri | OutPatientHealthCare-Occupants-Conference Room-Mon - Fri | OutPatientHealthCare | Occupants | Conference Room | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0.9 | 0.9 | 0 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Conference Room | Sat | OutPatientHealthCare-Occupants-Conference Room-Sat | OutPatientHealthCare | Occupants | Conference Room | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Conference Room | Sun | OutPatientHealthCare-Occupants-Conference Room-Sun | OutPatientHealthCare | Occupants | Conference Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | Occupants | Others | Mon - Fri | OutPatientHealthCare-Occupants-Others-Mon - Fri | OutPatientHealthCare | Occupants | Others | Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Others | Sat | OutPatientHealthCare-Occupants-Others-Sat | OutPatientHealthCare | Occupants | Others | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Occupants | Others | Sun | OutPatientHealthCare-Occupants-Others-Sun | OutPatientHealthCare | Occupants | Others | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | Lighting | All | Mon - Fri | OutPatientHealthCare-Lighting-All-Mon - Fri | OutPatientHealthCare | Lighting | All | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | Lighting | All | Sat | OutPatientHealthCare-Lighting-All-Sat | OutPatientHealthCare | Lighting | All | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | Lighting | All | Sun | OutPatientHealthCare-Lighting-All-Sun | OutPatientHealthCare | Lighting | All | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Electric Equipment | All | Mon - Fri | OutPatientHealthCare-Electric Equipment-All-Mon - Fri | OutPatientHealthCare | Electric Equipment | All | Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Electric Equipment | All | Sat | OutPatientHealthCare-Electric Equipment-All-Sat | OutPatientHealthCare | Electric Equipment | All | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Electric Equipment | All | Sun | OutPatientHealthCare-Electric Equipment-All-Sun | OutPatientHealthCare | Electric Equipment | All | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Gas Equipment | Operating Room | Mon - Fri | OutPatientHealthCare-Gas Equipment-Operating Room-Mon - Fri | OutPatientHealthCare | Gas Equipment | Operating Room | Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Gas Equipment | Operating Room | Sat | OutPatientHealthCare-Gas Equipment-Operating Room-Sat | OutPatientHealthCare | Gas Equipment | Operating Room | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | Gas Equipment | Operating Room | Sun | OutPatientHealthCare-Gas Equipment-Operating Room-Sun | OutPatientHealthCare | Gas Equipment | Operating Room | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | HVAC | All | Mon - Fri | OutPatientHealthCare-HVAC-All-Mon - Fri | OutPatientHealthCare | HVAC | All | Mon - Fri | bar: 2 to 25
OutPatientHealthCare | HVAC | All | Sat | OutPatientHealthCare-HVAC-All-Sat | OutPatientHealthCare | HVAC | All | Sat | bar: 2 to 25
OutPatientHealthCare | HVAC | All | Sun | OutPatientHealthCare-HVAC-All-Sun | OutPatientHealthCare | HVAC | All | Sun | bar: 2 to 25
OutPatientHealthCare | SWH | All | Mon - Fri | OutPatientHealthCare-SWH-All-Mon - Fri | OutPatientHealthCare | SWH | All | Mon - Fri | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
OutPatientHealthCare | SWH | All | Sat | OutPatientHealthCare-SWH-All-Sat | OutPatientHealthCare | SWH | All | Sat | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
OutPatientHealthCare | SWH | All | Sun | OutPatientHealthCare-SWH-All-Sun | OutPatientHealthCare | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | Elevator | All | Mon - Fri | OutPatientHealthCare-Elevator-All-Mon - Fri | OutPatientHealthCare | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.12 | 0.12
OutPatientHealthCare | Elevator | All | Sat | OutPatientHealthCare-Elevator-All-Sat | OutPatientHealthCare | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OutPatientHealthCare | Elevator | All | Sun | OutPatientHealthCare-Elevator-All-Sun | OutPatientHealthCare | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OutPatientHealthCare | Infiltration | All | Mon - Fri | OutPatientHealthCare-Infiltration-All-Mon - Fri | OutPatientHealthCare | Infiltration | All | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | Infiltration | All | Sat | OutPatientHealthCare-Infiltration-All-Sat | OutPatientHealthCare | Infiltration | All | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | Infiltration | All | Sun | OutPatientHealthCare-Infiltration-All-Sun | OutPatientHealthCare | Infiltration | All | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | Cooling Set Point | OR | Mon - Fri | OutPatientHealthCare-Cooling Set Point-OR-Mon - Fri | OutPatientHealthCare | Cooling Set Point | OR | Mon - Fri | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | OR | Sat | OutPatientHealthCare-Cooling Set Point-OR-Sat | OutPatientHealthCare | Cooling Set Point | OR | Sat | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | OR | Sun | OutPatientHealthCare-Cooling Set Point-OR-Sun | OutPatientHealthCare | Cooling Set Point | OR | Sun | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | Others | Mon - Fri | OutPatientHealthCare-Cooling Set Point-Others-Mon - Fri | OutPatientHealthCare | Cooling Set Point | Others | Mon - Fri | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | Others | Sat | OutPatientHealthCare-Cooling Set Point-Others-Sat | OutPatientHealthCare | Cooling Set Point | Others | Sat | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Cooling Set Point | Others | Sun | OutPatientHealthCare-Cooling Set Point-Others-Sun | OutPatientHealthCare | Cooling Set Point | Others | Sun | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | Heating Set Point | OR | Mon - Fri | OutPatientHealthCare-Heating Set Point-OR-Mon - Fri | OutPatientHealthCare | Heating Set Point | OR | Mon - Fri | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | Heating Set Point | OR | Sat | OutPatientHealthCare-Heating Set Point-OR-Sat | OutPatientHealthCare | Heating Set Point | OR | Sat | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | Heating Set Point | OR | Sun | OutPatientHealthCare-Heating Set Point-OR-Sun | OutPatientHealthCare | Heating Set Point | OR | Sun | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | Heating Set Point | Others | Mon - Fri | OutPatientHealthCare-Heating Set Point-Others-Mon - Fri | OutPatientHealthCare | Heating Set Point | Others | Mon - Fri | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | Heating Set Point | Others | Sat | OutPatientHealthCare-Heating Set Point-Others-Sat | OutPatientHealthCare | Heating Set Point | Others | Sat | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | Heating Set Point | Others | Sun | OutPatientHealthCare-Heating Set Point-Others-Sun | OutPatientHealthCare | Heating Set Point | Others | Sun | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Mon - Fri | Hospital-Occupants-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Mon - Fri | Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sat | Hospital-Occupants-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Sat | Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sun | Hospital-Occupants-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Sun | Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Mon - Fri | Hospital-Occupants-ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Mon - Fri | Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sat | Hospital-Occupants-ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Sat | Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sun | Hospital-Occupants-ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Sun | Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sun | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Mon - Fri | Hospital-Lighting-Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology-Mon - Fri | Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Sat | Hospital-Lighting-Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology-Sat | Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Sun | Hospital-Lighting-Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology-Sun | Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Mon - Fri | Hospital-Lighting-ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen-Mon - Fri | Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Sat | Hospital-Lighting-ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen-Sat | Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Sun | Hospital-Lighting-ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen-Sun | Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Mon - Fri | Hospital-Electric Equipment-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Mon - Fri | Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sat | Hospital-Electric Equipment-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Sat | Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sun | Hospital-Electric Equipment-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Sun | Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Mon - Fri | Hospital-Electric Equipment-ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Mon - Fri | Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sat | Hospital-Electric Equipment-ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Sat | Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sun | Hospital-Electric Equipment-ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Sun | Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sun | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | HVAC | All | Mon - Fri | Hospital-HVAC-All-Mon - Fri | Hospital | HVAC | All | Mon - Fri | bar: 2 to 25
Hospital | HVAC | All | Sat | Hospital-HVAC-All-Sat | Hospital | HVAC | All | Sat | bar: 2 to 25
Hospital | HVAC | All | Sun | Hospital-HVAC-All-Sun | Hospital | HVAC | All | Sun | bar: 2 to 25
Hospital | SWH | Office, Lobby, Clinic, OR | Mon - Fri | Hospital-SWH-Office, Lobby, Clinic, OR-Mon - Fri | Hospital | SWH | Office, Lobby, Clinic, OR | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0 | 0
Hospital | SWH | Office, Lobby, Clinic, OR | Sat | Hospital-SWH-Office, Lobby, Clinic, OR-Sat | Hospital | SWH | Office, Lobby, Clinic, OR | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hospital | SWH | Office, Lobby, Clinic, OR | Sun | Hospital-SWH-Office, Lobby, Clinic, OR-Sun | Hospital | SWH | Office, Lobby, Clinic, OR | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Mon - Fri | Hospital-SWH-ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen-Mon - Fri | Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3
Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Sat | Hospital-SWH-ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen-Sat | Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Sun | Hospital-SWH-ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen-Sun | Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | Elevator | All | Mon - Fri | Hospital-Elevator-All-Mon - Fri | Hospital | Elevator | All | Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2
Hospital | Elevator | All | Sat | Hospital-Elevator-All-Sat | Hospital | Elevator | All | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Elevator | All | Sun | Hospital-Elevator-All-Sun | Hospital | Elevator | All | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Infiltration | All | Mon - Fri | Hospital-Infiltration-All-Mon - Fri | Hospital | Infiltration | All | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | Infiltration | All | Sat | Hospital-Infiltration-All-Sat | Hospital | Infiltration | All | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | Infiltration | All | Sun | Hospital-Infiltration-All-Sun | Hospital | Infiltration | All | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | Cooling Set Point | All | Mon - Fri | Hospital-Cooling Set Point-All-Mon - Fri | Hospital | Cooling Set Point | All | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | Cooling Set Point | All | Sat | Hospital-Cooling Set Point-All-Sat | Hospital | Cooling Set Point | All | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | Cooling Set Point | All | Sun | Hospital-Cooling Set Point-All-Sun | Hospital | Cooling Set Point | All | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | Heating Set Point | All | Mon - Fri | Hospital-Heating Set Point-All-Mon - Fri | Hospital | Heating Set Point | All | Mon - Fri | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Hospital | Heating Set Point | All | Sat | Hospital-Heating Set Point-All-Sat | Hospital | Heating Set Point | All | Sat | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Hospital | Heating Set Point | All | Sun | Hospital-Heating Set Point-All-Sun | Hospital | Heating Set Point | All | Sun | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelSmall | Occupants | Guest Rooms | Mon - Fri | HotelSmall-Occupants-Guest Rooms-Mon - Fri | HotelSmall | Occupants | Guest Rooms | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1
HotelSmall | Occupants | Guest Rooms | Sat | HotelSmall-Occupants-Guest Rooms-Sat | HotelSmall | Occupants | Guest Rooms | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelSmall | Occupants | Guest Rooms | Sun | HotelSmall-Occupants-Guest Rooms-Sun | HotelSmall | Occupants | Guest Rooms | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelSmall | Occupants | Office | Mon - Fri | HotelSmall-Occupants-Office-Mon - Fri | HotelSmall | Occupants | Office | Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | Occupants | Office | Sat | HotelSmall-Occupants-Office-Sat | HotelSmall | Occupants | Office | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | Occupants | Office | Sun | HotelSmall-Occupants-Office-Sun | HotelSmall | Occupants | Office | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | Occupants | Meeting Room | Mon - Fri | HotelSmall-Occupants-Meeting Room-Mon - Fri | HotelSmall | Occupants | Meeting Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0 | 0 | 0.05 | 0.5 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Meeting Room | Sat | HotelSmall-Occupants-Meeting Room-Sat | HotelSmall | Occupants | Meeting Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Meeting Room | Sun | HotelSmall-Occupants-Meeting Room-Sun | HotelSmall | Occupants | Meeting Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Exercise Center | Mon - Fri | HotelSmall-Occupants-Exercise Center-Mon - Fri | HotelSmall | Occupants | Exercise Center | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Occupants | Exercise Center | Sat | HotelSmall-Occupants-Exercise Center-Sat | HotelSmall | Occupants | Exercise Center | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Occupants | Exercise Center | Sun | HotelSmall-Occupants-Exercise Center-Sun | HotelSmall | Occupants | Exercise Center | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Occupants | Laundry Room | Mon - Fri | HotelSmall-Occupants-Laundry Room-Mon - Fri | HotelSmall | Occupants | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Laundry Room | Sat | HotelSmall-Occupants-Laundry Room-Sat | HotelSmall | Occupants | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Laundry Room | Sun | HotelSmall-Occupants-Laundry Room-Sun | HotelSmall | Occupants | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Employee Lounge | Mon - Fri | HotelSmall-Occupants-Employee Lounge-Mon - Fri | HotelSmall | Occupants | Employee Lounge | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Employee Lounge | Sat | HotelSmall-Occupants-Employee Lounge-Sat | HotelSmall | Occupants | Employee Lounge | Sat | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Employee Lounge | Sun | HotelSmall-Occupants-Employee Lounge-Sun | HotelSmall | Occupants | Employee Lounge | Sun | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Occupants | Front Lounge, Restroom | Mon - Fri | HotelSmall-Occupants-Front Lounge, Restroom-Mon - Fri | HotelSmall | Occupants | Front Lounge, Restroom | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Occupants | Front Lounge, Restroom | Sat | HotelSmall-Occupants-Front Lounge, Restroom-Sat | HotelSmall | Occupants | Front Lounge, Restroom | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Occupants | Front Lounge, Restroom | Sun | HotelSmall-Occupants-Front Lounge, Restroom-Sun | HotelSmall | Occupants | Front Lounge, Restroom | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Lighting | Guest Rooms | Mon - Fri | HotelSmall-Lighting-Guest Rooms-Mon - Fri | HotelSmall | Lighting | Guest Rooms | Mon - Fri | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
HotelSmall | Lighting | Guest Rooms | Sat | HotelSmall-Lighting-Guest Rooms-Sat | HotelSmall | Lighting | Guest Rooms | Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelSmall | Lighting | Guest Rooms | Sun | HotelSmall-Lighting-Guest Rooms-Sun | HotelSmall | Lighting | Guest Rooms | Sun | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelSmall | Lighting | Office | Mon - Fri | HotelSmall-Lighting-Office-Mon - Fri | HotelSmall | Lighting | Office | Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | Lighting | Office | Sat | HotelSmall-Lighting-Office-Sat | HotelSmall | Lighting | Office | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | Lighting | Office | Sun | HotelSmall-Lighting-Office-Sun | HotelSmall | Lighting | Office | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Mon - Fri | HotelSmall-Lighting-Meeting Room, Employee Lounge, Front Lounge-Mon - Fri | HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Sat | HotelSmall-Lighting-Meeting Room, Employee Lounge, Front Lounge-Sat | HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Sat | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Sun | HotelSmall-Lighting-Meeting Room, Employee Lounge, Front Lounge-Sun | HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Sun | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | Lighting | Exercise Center | Mon - Fri | HotelSmall-Lighting-Exercise Center-Mon - Fri | HotelSmall | Lighting | Exercise Center | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Lighting | Exercise Center | Sat | HotelSmall-Lighting-Exercise Center-Sat | HotelSmall | Lighting | Exercise Center | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Lighting | Exercise Center | Sun | HotelSmall-Lighting-Exercise Center-Sun | HotelSmall | Lighting | Exercise Center | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | Lighting | Laundry Room | Mon - Fri | HotelSmall-Lighting-Laundry Room-Mon - Fri | HotelSmall | Lighting | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Lighting | Laundry Room | Sat | HotelSmall-Lighting-Laundry Room-Sat | HotelSmall | Lighting | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Lighting | Laundry Room | Sun | HotelSmall-Lighting-Laundry Room-Sun | HotelSmall | Lighting | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Lighting | Corridors, Stairs, Restroom | Mon - Fri | HotelSmall-Lighting-Corridors, Stairs, Restroom-Mon - Fri | HotelSmall | Lighting | Corridors, Stairs, Restroom | Mon - Fri | bar: 2 to 25
HotelSmall | Lighting | Corridors, Stairs, Restroom | Sat | HotelSmall-Lighting-Corridors, Stairs, Restroom-Sat | HotelSmall | Lighting | Corridors, Stairs, Restroom | Sat | bar: 2 to 25
HotelSmall | Lighting | Corridors, Stairs, Restroom | Sun | HotelSmall-Lighting-Corridors, Stairs, Restroom-Sun | HotelSmall | Lighting | Corridors, Stairs, Restroom | Sun | bar: 2 to 25
HotelSmall | Lighting | Storage, Mechanical room | Mon - Fri | HotelSmall-Lighting-Storage, Mechanical room-Mon - Fri | HotelSmall | Lighting | Storage, Mechanical room | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | Lighting | Storage, Mechanical room | Sat | HotelSmall-Lighting-Storage, Mechanical room-Sat | HotelSmall | Lighting | Storage, Mechanical room | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | Lighting | Storage, Mechanical room | Sun | HotelSmall-Lighting-Storage, Mechanical room-Sun | HotelSmall | Lighting | Storage, Mechanical room | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | Electric Equipment | Guest Rooms | Mon - Fri | HotelSmall-Electric Equipment-Guest Rooms-Mon - Fri | HotelSmall | Electric Equipment | Guest Rooms | Mon - Fri | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | Electric Equipment | Guest Rooms | Sat | HotelSmall-Electric Equipment-Guest Rooms-Sat | HotelSmall | Electric Equipment | Guest Rooms | Sat | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | Electric Equipment | Guest Rooms | Sun | HotelSmall-Electric Equipment-Guest Rooms-Sun | HotelSmall | Electric Equipment | Guest Rooms | Sun | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | Electric Equipment | Office | Mon - Fri | HotelSmall-Electric Equipment-Office-Mon - Fri | HotelSmall | Electric Equipment | Office | Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | Electric Equipment | Office | Sat | HotelSmall-Electric Equipment-Office-Sat | HotelSmall | Electric Equipment | Office | Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | Electric Equipment | Office | Sun | HotelSmall-Electric Equipment-Office-Sun | HotelSmall | Electric Equipment | Office | Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | Electric Equipment | Meeting Room | Mon - Fri | HotelSmall-Electric Equipment-Meeting Room-Mon - Fri | HotelSmall | Electric Equipment | Meeting Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Meeting Room | Sat | HotelSmall-Electric Equipment-Meeting Room-Sat | HotelSmall | Electric Equipment | Meeting Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Meeting Room | Sun | HotelSmall-Electric Equipment-Meeting Room-Sun | HotelSmall | Electric Equipment | Meeting Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Exercise Center | Mon - Fri | HotelSmall-Electric Equipment-Exercise Center-Mon - Fri | HotelSmall | Electric Equipment | Exercise Center | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | Electric Equipment | Exercise Center | Sat | HotelSmall-Electric Equipment-Exercise Center-Sat | HotelSmall | Electric Equipment | Exercise Center | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | Electric Equipment | Exercise Center | Sun | HotelSmall-Electric Equipment-Exercise Center-Sun | HotelSmall | Electric Equipment | Exercise Center | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | Electric Equipment | Laundry Room | Mon - Fri | HotelSmall-Electric Equipment-Laundry Room-Mon - Fri | HotelSmall | Electric Equipment | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Laundry Room | Sat | HotelSmall-Electric Equipment-Laundry Room-Sat | HotelSmall | Electric Equipment | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Laundry Room | Sun | HotelSmall-Electric Equipment-Laundry Room-Sun | HotelSmall | Electric Equipment | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Electric Equipment | Employee Lounge | Mon - Fri | HotelSmall-Electric Equipment-Employee Lounge-Mon - Fri | HotelSmall | Electric Equipment | Employee Lounge | Mon - Fri | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | Electric Equipment | Employee Lounge | Sat | HotelSmall-Electric Equipment-Employee Lounge-Sat | HotelSmall | Electric Equipment | Employee Lounge | Sat | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | Electric Equipment | Employee Lounge | Sun | HotelSmall-Electric Equipment-Employee Lounge-Sun | HotelSmall | Electric Equipment | Employee Lounge | Sun | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | Electric Equipment | Front Lounge | Mon - Fri | HotelSmall-Electric Equipment-Front Lounge-Mon - Fri | HotelSmall | Electric Equipment | Front Lounge | Mon - Fri | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | Electric Equipment | Front Lounge | Sat | HotelSmall-Electric Equipment-Front Lounge-Sat | HotelSmall | Electric Equipment | Front Lounge | Sat | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | Electric Equipment | Front Lounge | Sun | HotelSmall-Electric Equipment-Front Lounge-Sun | HotelSmall | Electric Equipment | Front Lounge | Sun | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | Gas Equipment | Laundry Room | Mon - Fri | HotelSmall-Gas Equipment-Laundry Room-Mon - Fri | HotelSmall | Gas Equipment | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Gas Equipment | Laundry Room | Sat | HotelSmall-Gas Equipment-Laundry Room-Sat | HotelSmall | Gas Equipment | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Gas Equipment | Laundry Room | Sun | HotelSmall-Gas Equipment-Laundry Room-Sun | HotelSmall | Gas Equipment | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | HVAC | All | Mon - Fri | HotelSmall-HVAC-All-Mon - Fri | HotelSmall | HVAC | All | Mon - Fri | bar: 2 to 25
HotelSmall | HVAC | All | Sat | HotelSmall-HVAC-All-Sat | HotelSmall | HVAC | All | Sat | bar: 2 to 25
HotelSmall | HVAC | All | Sun | HotelSmall-HVAC-All-Sun | HotelSmall | HVAC | All | Sun | bar: 2 to 25
HotelSmall | SWH | Guest Rooms | Mon - Fri | HotelSmall-SWH-Guest Rooms-Mon - Fri | HotelSmall | SWH | Guest Rooms | Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
HotelSmall | SWH | Guest Rooms | Sat | HotelSmall-SWH-Guest Rooms-Sat | HotelSmall | SWH | Guest Rooms | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelSmall | SWH | Guest Rooms | Sun | HotelSmall-SWH-Guest Rooms-Sun | HotelSmall | SWH | Guest Rooms | Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelSmall | SWH | Laundry Room | Mon - Fri | HotelSmall-SWH-Laundry Room-Mon - Fri | HotelSmall | SWH | Laundry Room | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | SWH | Laundry Room | Sat | HotelSmall-SWH-Laundry Room-Sat | HotelSmall | SWH | Laundry Room | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | SWH | Laundry Room | Sun | HotelSmall-SWH-Laundry Room-Sun | HotelSmall | SWH | Laundry Room | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Elevator | All | Mon - Fri | HotelSmall-Elevator-All-Mon - Fri | HotelSmall | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | Elevator | All | Sat | HotelSmall-Elevator-All-Sat | HotelSmall | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | Elevator | All | Sun | HotelSmall-Elevator-All-Sun | HotelSmall | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | Infiltration | Guest Rooms | Mon - Fri | HotelSmall-Infiltration-Guest Rooms-Mon - Fri | HotelSmall | Infiltration | Guest Rooms | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Guest Rooms | Sat | HotelSmall-Infiltration-Guest Rooms-Sat | HotelSmall | Infiltration | Guest Rooms | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Guest Rooms | Sun | HotelSmall-Infiltration-Guest Rooms-Sun | HotelSmall | Infiltration | Guest Rooms | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Common Areas | Mon - Fri | HotelSmall-Infiltration-Common Areas-Mon - Fri | HotelSmall | Infiltration | Common Areas | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Common Areas | Sat | HotelSmall-Infiltration-Common Areas-Sat | HotelSmall | Infiltration | Common Areas | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Infiltration | Common Areas | Sun | HotelSmall-Infiltration-Common Areas-Sun | HotelSmall | Infiltration | Common Areas | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | Cooling Set Point | Guest Rooms | Mon - Fri | HotelSmall-Cooling Set Point-Guest Rooms-Mon - Fri | HotelSmall | Cooling Set Point | Guest Rooms | Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Cooling Set Point | Guest Rooms | Sat | HotelSmall-Cooling Set Point-Guest Rooms-Sat | HotelSmall | Cooling Set Point | Guest Rooms | Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Cooling Set Point | Guest Rooms | Sun | HotelSmall-Cooling Set Point-Guest Rooms-Sun | HotelSmall | Cooling Set Point | Guest Rooms | Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Cooling Set Point | Common Area | Mon - Fri | HotelSmall-Cooling Set Point-Common Area-Mon - Fri | HotelSmall | Cooling Set Point | Common Area | Mon - Fri | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | Cooling Set Point | Common Area | Sat | HotelSmall-Cooling Set Point-Common Area-Sat | HotelSmall | Cooling Set Point | Common Area | Sat | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | Cooling Set Point | Common Area | Sun | HotelSmall-Cooling Set Point-Common Area-Sun | HotelSmall | Cooling Set Point | Common Area | Sun | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | Heating Set Point | Guest Rooms | Mon - Fri | HotelSmall-Heating Set Point-Guest Rooms-Mon - Fri | HotelSmall | Heating Set Point | Guest Rooms | Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Guest Rooms | Sat | HotelSmall-Heating Set Point-Guest Rooms-Sat | HotelSmall | Heating Set Point | Guest Rooms | Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Guest Rooms | Sun | HotelSmall-Heating Set Point-Guest Rooms-Sun | HotelSmall | Heating Set Point | Guest Rooms | Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Common Area | Mon - Fri | HotelSmall-Heating Set Point-Common Area-Mon - Fri | HotelSmall | Heating Set Point | Common Area | Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Common Area | Sat | HotelSmall-Heating Set Point-Common Area-Sat | HotelSmall | Heating Set Point | Common Area | Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Heating Set Point | Common Area | Sun | HotelSmall-Heating Set Point-Common Area-Sun | HotelSmall | Heating Set Point | Common Area | Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelLarge | Occupants | Guest Rooms | Mon - Fri | HotelLarge-Occupants-Guest Rooms-Mon - Fri | HotelLarge | Occupants | Guest Rooms | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1
HotelLarge | Occupants | Guest Rooms | Sat | HotelLarge-Occupants-Guest Rooms-Sat | HotelLarge | Occupants | Guest Rooms | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelLarge | Occupants | Guest Rooms | Sun | HotelLarge-Occupants-Guest Rooms-Sun | HotelLarge | Occupants | Guest Rooms | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelLarge | Occupants | Others | Mon - Fri | HotelLarge-Occupants-Others-Mon - Fri | HotelLarge | Occupants | Others | Mon - Fri | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
HotelLarge | Occupants | Others | Sat | HotelLarge-Occupants-Others-Sat | HotelLarge | Occupants | Others | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
HotelLarge | Occupants | Others | Sun | HotelLarge-Occupants-Others-Sun | HotelLarge | Occupants | Others | Sun | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
HotelLarge | Lighting | Guest Rooms | Mon - Fri | HotelLarge-Lighting-Guest Rooms-Mon - Fri | HotelLarge | Lighting | Guest Rooms | Mon - Fri | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
HotelLarge | Lighting | Guest Rooms | Sat | HotelLarge-Lighting-Guest Rooms-Sat | HotelLarge | Lighting | Guest Rooms | Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelLarge | Lighting | Guest Rooms | Sun | HotelLarge-Lighting-Guest Rooms-Sun | HotelLarge | Lighting | Guest Rooms | Sun | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelLarge | Lighting | Others | Mon - Fri | HotelLarge-Lighting-Others-Mon - Fri | HotelLarge | Lighting | Others | Mon - Fri | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | Lighting | Others | Sat | HotelLarge-Lighting-Others-Sat | HotelLarge | Lighting | Others | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | Lighting | Others | Sun | HotelLarge-Lighting-Others-Sun | HotelLarge | Lighting | Others | Sun | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | Electric Equipment | Guest Rooms | Mon - Fri | HotelLarge-Electric Equipment-Guest Rooms-Mon - Fri | HotelLarge | Electric Equipment | Guest Rooms | Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | Electric Equipment | Guest Rooms | Sat | HotelLarge-Electric Equipment-Guest Rooms-Sat | HotelLarge | Electric Equipment | Guest Rooms | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | Electric Equipment | Guest Rooms | Sun | HotelLarge-Electric Equipment-Guest Rooms-Sun | HotelLarge | Electric Equipment | Guest Rooms | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Mon - Fri | HotelLarge-Electric Equipment-Kitchen, Dining, Banquet-Mon - Fri | HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Sat | HotelLarge-Electric Equipment-Kitchen, Dining, Banquet-Sat | HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Sun | HotelLarge-Electric Equipment-Kitchen, Dining, Banquet-Sun | HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Electric Equipment | Others | Mon - Fri | HotelLarge-Electric Equipment-Others-Mon - Fri | HotelLarge | Electric Equipment | Others | Mon - Fri | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
HotelLarge | Electric Equipment | Others | Sat | HotelLarge-Electric Equipment-Others-Sat | HotelLarge | Electric Equipment | Others | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
HotelLarge | Electric Equipment | Others | Sun | HotelLarge-Electric Equipment-Others-Sun | HotelLarge | Electric Equipment | Others | Sun | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
HotelLarge | Gas Equipment | Kitchen | Mon - Fri | HotelLarge-Gas Equipment-Kitchen-Mon - Fri | HotelLarge | Gas Equipment | Kitchen | Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | Gas Equipment | Kitchen | Sat | HotelLarge-Gas Equipment-Kitchen-Sat | HotelLarge | Gas Equipment | Kitchen | Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | Gas Equipment | Kitchen | Sun | HotelLarge-Gas Equipment-Kitchen-Sun | HotelLarge | Gas Equipment | Kitchen | Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | HVAC | All | Mon - Fri | HotelLarge-HVAC-All-Mon - Fri | HotelLarge | HVAC | All | Mon - Fri | bar: 2 to 25
HotelLarge | HVAC | All | Sat | HotelLarge-HVAC-All-Sat | HotelLarge | HVAC | All | Sat | bar: 2 to 25
HotelLarge | HVAC | All | Sun | HotelLarge-HVAC-All-Sun | HotelLarge | HVAC | All | Sun | bar: 2 to 25
HotelLarge | SWH | Guest Rooms | Mon - Fri | HotelLarge-SWH-Guest Rooms-Mon - Fri | HotelLarge | SWH | Guest Rooms | Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
HotelLarge | SWH | Guest Rooms | Sat | HotelLarge-SWH-Guest Rooms-Sat | HotelLarge | SWH | Guest Rooms | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelLarge | SWH | Guest Rooms | Sun | HotelLarge-SWH-Guest Rooms-Sun | HotelLarge | SWH | Guest Rooms | Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelLarge | SWH | Kitchen | Mon - Fri | HotelLarge-SWH-Kitchen-Mon - Fri | HotelLarge | SWH | Kitchen | Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
HotelLarge | SWH | Kitchen | Sat | HotelLarge-SWH-Kitchen-Sat | HotelLarge | SWH | Kitchen | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
HotelLarge | SWH | Kitchen | Sun | HotelLarge-SWH-Kitchen-Sun | HotelLarge | SWH | Kitchen | Sun | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
HotelLarge | Elevator | All | Mon - Fri | HotelLarge-Elevator-All-Mon - Fri | HotelLarge | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | Elevator | All | Sat | HotelLarge-Elevator-All-Sat | HotelLarge | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | Elevator | All | Sun | HotelLarge-Elevator-All-Sun | HotelLarge | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | Infiltration | All | Mon - Fri | HotelLarge-Infiltration-All-Mon - Fri | HotelLarge | Infiltration | All | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | Infiltration | All | Sat | HotelLarge-Infiltration-All-Sat | HotelLarge | Infiltration | All | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | Infiltration | All | Sun | HotelLarge-Infiltration-All-Sun | HotelLarge | Infiltration | All | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | Cooling Set Point | Guest Rooms | Mon - Fri | HotelLarge-Cooling Set Point-Guest Rooms-Mon - Fri | HotelLarge | Cooling Set Point | Guest Rooms | Mon - Fri | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Cooling Set Point | Guest Rooms | Sat | HotelLarge-Cooling Set Point-Guest Rooms-Sat | HotelLarge | Cooling Set Point | Guest Rooms | Sat | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Cooling Set Point | Guest Rooms | Sun | HotelLarge-Cooling Set Point-Guest Rooms-Sun | HotelLarge | Cooling Set Point | Guest Rooms | Sun | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Cooling Set Point | Common Areas | Mon - Fri | HotelLarge-Cooling Set Point-Common Areas-Mon - Fri | HotelLarge | Cooling Set Point | Common Areas | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | Cooling Set Point | Common Areas | Sat | HotelLarge-Cooling Set Point-Common Areas-Sat | HotelLarge | Cooling Set Point | Common Areas | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | Cooling Set Point | Common Areas | Sun | HotelLarge-Cooling Set Point-Common Areas-Sun | HotelLarge | Cooling Set Point | Common Areas | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | Heating Set Point | Guest Rooms | Mon - Fri | HotelLarge-Heating Set Point-Guest Rooms-Mon - Fri | HotelLarge | Heating Set Point | Guest Rooms | Mon - Fri | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Heating Set Point | Guest Rooms | Sat | HotelLarge-Heating Set Point-Guest Rooms-Sat | HotelLarge | Heating Set Point | Guest Rooms | Sat | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Heating Set Point | Guest Rooms | Sun | HotelLarge-Heating Set Point-Guest Rooms-Sun | HotelLarge | Heating Set Point | Guest Rooms | Sun | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Heating Set Point | Common Areas | Mon - Fri | HotelLarge-Heating Set Point-Common Areas-Mon - Fri | HotelLarge | Heating Set Point | Common Areas | Mon - Fri | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelLarge | Heating Set Point | Common Areas | Sat | HotelLarge-Heating Set Point-Common Areas-Sat | HotelLarge | Heating Set Point | Common Areas | Sat | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelLarge | Heating Set Point | Common Areas | Sun | HotelLarge-Heating Set Point-Common Areas-Sun | HotelLarge | Heating Set Point | Common Areas | Sun | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Warehouse | Occupants | All | Mon - Fri | Warehouse-Occupants-All-Mon - Fri | Warehouse | Occupants | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Occupants | All | Sat | Warehouse-Occupants-All-Sat | Warehouse | Occupants | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Occupants | All | Sun | Warehouse-Occupants-All-Sun | Warehouse | Occupants | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Lighting | Office | Mon - Fri | Warehouse-Lighting-Office-Mon - Fri | Warehouse | Lighting | Office | Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | Lighting | Office | Sat | Warehouse-Lighting-Office-Sat | Warehouse | Lighting | Office | Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | Lighting | Office | Sun | Warehouse-Lighting-Office-Sun | Warehouse | Lighting | Office | Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | Lighting | Fine Sorage, Bulk Storage | Mon - Fri | Warehouse-Lighting-Fine Sorage, Bulk Storage-Mon - Fri | Warehouse | Lighting | Fine Sorage, Bulk Storage | Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | Lighting | Fine Sorage, Bulk Storage | Sat | Warehouse-Lighting-Fine Sorage, Bulk Storage-Sat | Warehouse | Lighting | Fine Sorage, Bulk Storage | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | Lighting | Fine Sorage, Bulk Storage | Sun | Warehouse-Lighting-Fine Sorage, Bulk Storage-Sun | Warehouse | Lighting | Fine Sorage, Bulk Storage | Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | Electric Equipment | Office | Mon - Fri | Warehouse-Electric Equipment-Office-Mon - Fri | Warehouse | Electric Equipment | Office | Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Electric Equipment | Office | Sat | Warehouse-Electric Equipment-Office-Sat | Warehouse | Electric Equipment | Office | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Electric Equipment | Office | Sun | Warehouse-Electric Equipment-Office-Sun | Warehouse | Electric Equipment | Office | Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Electric Equipment | Bulk Storage | Mon - Fri | Warehouse-Electric Equipment-Bulk Storage-Mon - Fri | Warehouse | Electric Equipment | Bulk Storage | Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Warehouse | Electric Equipment | Bulk Storage | Sat | Warehouse-Electric Equipment-Bulk Storage-Sat | Warehouse | Electric Equipment | Bulk Storage | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Warehouse | Electric Equipment | Bulk Storage | Sun | Warehouse-Electric Equipment-Bulk Storage-Sun | Warehouse | Electric Equipment | Bulk Storage | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | HVAC | All | Mon - Fri | Warehouse-HVAC-All-Mon - Fri | Warehouse | HVAC | All | Mon - Fri | bar: 2 to 25
Warehouse | HVAC | All | Sat | Warehouse-HVAC-All-Sat | Warehouse | HVAC | All | Sat | bar: 2 to 25
Warehouse | HVAC | All | Sun | Warehouse-HVAC-All-Sun | Warehouse | HVAC | All | Sun | bar: 2 to 25
Warehouse | SWH | Office | Mon - Fri | Warehouse-SWH-Office-Mon - Fri | Warehouse | SWH | Office | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.101 | 0.399 | 0.501 | 0.501 | 0.696 | 0.9 | 0.798 | 0.696 | 0.798 | 0.297 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | SWH | Office | Sat | Warehouse-SWH-Office-Sat | Warehouse | SWH | Office | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.101 | 0.399 | 0.501 | 0.501 | 0.696 | 0.9 | 0.798 | 0.696 | 0.798 | 0.297 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | SWH | Office | Sun | Warehouse-SWH-Office-Sun | Warehouse | SWH | Office | Sun | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
Warehouse | Infiltration | Office, Fine Sorage | Mon - Fri | Warehouse-Infiltration-Office, Fine Sorage-Mon - Fri | Warehouse | Infiltration | Office, Fine Sorage | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Infiltration | Office, Fine Sorage | Sat | Warehouse-Infiltration-Office, Fine Sorage-Sat | Warehouse | Infiltration | Office, Fine Sorage | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Infiltration | Office, Fine Sorage | Sun | Warehouse-Infiltration-Office, Fine Sorage-Sun | Warehouse | Infiltration | Office, Fine Sorage | Sun | bar: 2 to 25
Warehouse | Infiltration | Bulk Storage | Mon - Fri | Warehouse-Infiltration-Bulk Storage-Mon - Fri | Warehouse | Infiltration | Bulk Storage | Mon - Fri | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | Infiltration | Bulk Storage | Sat | Warehouse-Infiltration-Bulk Storage-Sat | Warehouse | Infiltration | Bulk Storage | Sat | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | Infiltration | Bulk Storage | Sun | Warehouse-Infiltration-Bulk Storage-Sun | Warehouse | Infiltration | Bulk Storage | Sun | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | Cooling Set Point | Office | Mon - Fri | Warehouse-Cooling Set Point-Office-Mon - Fri | Warehouse | Cooling Set Point | Office | Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
Warehouse | Cooling Set Point | Office | Sat | Warehouse-Cooling Set Point-Office-Sat | Warehouse | Cooling Set Point | Office | Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
Warehouse | Cooling Set Point | Office | Sun | Warehouse-Cooling Set Point-Office-Sun | Warehouse | Cooling Set Point | Office | Sun | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
Warehouse | Cooling Set Point | Fine Sorage | Mon - Fri | Warehouse-Cooling Set Point-Fine Sorage-Mon - Fri | Warehouse | Cooling Set Point | Fine Sorage | Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | Cooling Set Point | Fine Sorage | Sat | Warehouse-Cooling Set Point-Fine Sorage-Sat | Warehouse | Cooling Set Point | Fine Sorage | Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | Cooling Set Point | Fine Sorage | Sun | Warehouse-Cooling Set Point-Fine Sorage-Sun | Warehouse | Cooling Set Point | Fine Sorage | Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | Heating Set Point | Office | Mon - Fri | Warehouse-Heating Set Point-Office-Mon - Fri | Warehouse | Heating Set Point | Office | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Heating Set Point | Office | Sat | Warehouse-Heating Set Point-Office-Sat | Warehouse | Heating Set Point | Office | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Heating Set Point | Office | Sun | Warehouse-Heating Set Point-Office-Sun | Warehouse | Heating Set Point | Office | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Heating Set Point | Fine Sorage | Mon - Fri | Warehouse-Heating Set Point-Fine Sorage-Mon - Fri | Warehouse | Heating Set Point | Fine Sorage | Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Heating Set Point | Fine Sorage | Sat | Warehouse-Heating Set Point-Fine Sorage-Sat | Warehouse | Heating Set Point | Fine Sorage | Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Heating Set Point | Fine Sorage | Sun | Warehouse-Heating Set Point-Fine Sorage-Sun | Warehouse | Heating Set Point | Fine Sorage | Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Heating Set Point | Bulk Storage | Mon - Fri | Warehouse-Heating Set Point-Bulk Storage-Mon - Fri | Warehouse | Heating Set Point | Bulk Storage | Mon - Fri | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Warehouse | Heating Set Point | Bulk Storage | Sat | Warehouse-Heating Set Point-Bulk Storage-Sat | Warehouse | Heating Set Point | Bulk Storage | Sat | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Warehouse | Heating Set Point | Bulk Storage | Sun | Warehouse-Heating Set Point-Bulk Storage-Sun | Warehouse | Heating Set Point | Bulk Storage | Sun | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
RestaurantFastFood | Occupants | All | Mon - Fri | RestaurantFastFood-Occupants-All-Mon - Fri | RestaurantFastFood | Occupants | All | Mon - Fri | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
RestaurantFastFood | Occupants | All | Sat | RestaurantFastFood-Occupants-All-Sat | RestaurantFastFood | Occupants | All | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
RestaurantFastFood | Occupants | All | Sun | RestaurantFastFood-Occupants-All-Sun | RestaurantFastFood | Occupants | All | Sun | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
RestaurantFastFood | Lighting | All | Mon - Fri | RestaurantFastFood-Lighting-All-Mon - Fri | RestaurantFastFood | Lighting | All | Mon - Fri | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | Lighting | All | Sat | RestaurantFastFood-Lighting-All-Sat | RestaurantFastFood | Lighting | All | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | Lighting | All | Sun | RestaurantFastFood-Lighting-All-Sun | RestaurantFastFood | Lighting | All | Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantFastFood | Electric Equipment | All | Mon - Fri | RestaurantFastFood-Electric Equipment-All-Mon - Fri | RestaurantFastFood | Electric Equipment | All | Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Electric Equipment | All | Sat | RestaurantFastFood-Electric Equipment-All-Sat | RestaurantFastFood | Electric Equipment | All | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Electric Equipment | All | Sun | RestaurantFastFood-Electric Equipment-All-Sun | RestaurantFastFood | Electric Equipment | All | Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Gas Equipment | Kitchen | Mon - Fri | RestaurantFastFood-Gas Equipment-Kitchen-Mon - Fri | RestaurantFastFood | Gas Equipment | Kitchen | Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Gas Equipment | Kitchen | Sat | RestaurantFastFood-Gas Equipment-Kitchen-Sat | RestaurantFastFood | Gas Equipment | Kitchen | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | Gas Equipment | Kitchen | Sun | RestaurantFastFood-Gas Equipment-Kitchen-Sun | RestaurantFastFood | Gas Equipment | Kitchen | Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | HVAC | All | Mon - Fri | RestaurantFastFood-HVAC-All-Mon - Fri | RestaurantFastFood | HVAC | All | Mon - Fri | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | HVAC | All | Sat | RestaurantFastFood-HVAC-All-Sat | RestaurantFastFood | HVAC | All | Sat | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | HVAC | All | Sun | RestaurantFastFood-HVAC-All-Sun | RestaurantFastFood | HVAC | All | Sun | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | SWH | All | Mon - Fri | RestaurantFastFood-SWH-All-Mon - Fri | RestaurantFastFood | SWH | All | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
RestaurantFastFood | SWH | All | Sat | RestaurantFastFood-SWH-All-Sat | RestaurantFastFood | SWH | All | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
RestaurantFastFood | SWH | All | Sun | RestaurantFastFood-SWH-All-Sun | RestaurantFastFood | SWH | All | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
RestaurantFastFood | Infiltration | All | Mon - Fri | RestaurantFastFood-Infiltration-All-Mon - Fri | RestaurantFastFood | Infiltration | All | Mon - Fri | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | Infiltration | All | Sat | RestaurantFastFood-Infiltration-All-Sat | RestaurantFastFood | Infiltration | All | Sat | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | Infiltration | All | Sun | RestaurantFastFood-Infiltration-All-Sun | RestaurantFastFood | Infiltration | All | Sun | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | Cooling Set Point | Dining | Mon - Fri | RestaurantFastFood-Cooling Set Point-Dining-Mon - Fri | RestaurantFastFood | Cooling Set Point | Dining | Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | Cooling Set Point | Dining | Sat | RestaurantFastFood-Cooling Set Point-Dining-Sat | RestaurantFastFood | Cooling Set Point | Dining | Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | Cooling Set Point | Dining | Sun | RestaurantFastFood-Cooling Set Point-Dining-Sun | RestaurantFastFood | Cooling Set Point | Dining | Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | Cooling Set Point | Kitchen | Mon - Fri | RestaurantFastFood-Cooling Set Point-Kitchen-Mon - Fri | RestaurantFastFood | Cooling Set Point | Kitchen | Mon - Fri | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | Cooling Set Point | Kitchen | Sat | RestaurantFastFood-Cooling Set Point-Kitchen-Sat | RestaurantFastFood | Cooling Set Point | Kitchen | Sat | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | Cooling Set Point | Kitchen | Sun | RestaurantFastFood-Cooling Set Point-Kitchen-Sun | RestaurantFastFood | Cooling Set Point | Kitchen | Sun | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | Heating Set Point | Dining | Mon - Fri | RestaurantFastFood-Heating Set Point-Dining-Mon - Fri | RestaurantFastFood | Heating Set Point | Dining | Mon - Fri | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | Heating Set Point | Dining | Sat | RestaurantFastFood-Heating Set Point-Dining-Sat | RestaurantFastFood | Heating Set Point | Dining | Sat | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | Heating Set Point | Dining | Sun | RestaurantFastFood-Heating Set Point-Dining-Sun | RestaurantFastFood | Heating Set Point | Dining | Sun | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | Heating Set Point | Kitchen | Mon - Fri | RestaurantFastFood-Heating Set Point-Kitchen-Mon - Fri | RestaurantFastFood | Heating Set Point | Kitchen | Mon - Fri | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | Heating Set Point | Kitchen | Sat | RestaurantFastFood-Heating Set Point-Kitchen-Sat | RestaurantFastFood | Heating Set Point | Kitchen | Sat | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | Heating Set Point | Kitchen | Sun | RestaurantFastFood-Heating Set Point-Kitchen-Sun | RestaurantFastFood | Heating Set Point | Kitchen | Sun | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantSitDown | Occupants | All | Mon - Fri | RestaurantSitDown-Occupants-All-Mon - Fri | RestaurantSitDown | Occupants | All | Mon - Fri | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
RestaurantSitDown | Occupants | All | Sat | RestaurantSitDown-Occupants-All-Sat | RestaurantSitDown | Occupants | All | Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
RestaurantSitDown | Occupants | All | Sun | RestaurantSitDown-Occupants-All-Sun | RestaurantSitDown | Occupants | All | Sun | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
RestaurantSitDown | Lighting | All | Mon - Fri | RestaurantSitDown-Lighting-All-Mon - Fri | RestaurantSitDown | Lighting | All | Mon - Fri | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | Lighting | All | Sat | RestaurantSitDown-Lighting-All-Sat | RestaurantSitDown | Lighting | All | Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | Lighting | All | Sun | RestaurantSitDown-Lighting-All-Sun | RestaurantSitDown | Lighting | All | Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantSitDown | Electric Equipment | All | Mon - Fri | RestaurantSitDown-Electric Equipment-All-Mon - Fri | RestaurantSitDown | Electric Equipment | All | Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Electric Equipment | All | Sat | RestaurantSitDown-Electric Equipment-All-Sat | RestaurantSitDown | Electric Equipment | All | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Electric Equipment | All | Sun | RestaurantSitDown-Electric Equipment-All-Sun | RestaurantSitDown | Electric Equipment | All | Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Gas Equipment | Kitchen | Mon - Fri | RestaurantSitDown-Gas Equipment-Kitchen-Mon - Fri | RestaurantSitDown | Gas Equipment | Kitchen | Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Gas Equipment | Kitchen | Sat | RestaurantSitDown-Gas Equipment-Kitchen-Sat | RestaurantSitDown | Gas Equipment | Kitchen | Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Gas Equipment | Kitchen | Sun | RestaurantSitDown-Gas Equipment-Kitchen-Sun | RestaurantSitDown | Gas Equipment | Kitchen | Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | HVAC | All | Mon - Fri | RestaurantSitDown-HVAC-All-Mon - Fri | RestaurantSitDown | HVAC | All | Mon - Fri | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | HVAC | All | Sat | RestaurantSitDown-HVAC-All-Sat | RestaurantSitDown | HVAC | All | Sat | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | HVAC | All | Sun | RestaurantSitDown-HVAC-All-Sun | RestaurantSitDown | HVAC | All | Sun | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | SWH | All | Mon - Fri | RestaurantSitDown-SWH-All-Mon - Fri | RestaurantSitDown | SWH | All | Mon - Fri | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
RestaurantSitDown | SWH | All | Sat | RestaurantSitDown-SWH-All-Sat | RestaurantSitDown | SWH | All | Sat | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
RestaurantSitDown | SWH | All | Sun | RestaurantSitDown-SWH-All-Sun | RestaurantSitDown | SWH | All | Sun | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
RestaurantSitDown | Infiltration | All | Mon - Fri | RestaurantSitDown-Infiltration-All-Mon - Fri | RestaurantSitDown | Infiltration | All | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | Infiltration | All | Sat | RestaurantSitDown-Infiltration-All-Sat | RestaurantSitDown | Infiltration | All | Sat | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | Infiltration | All | Sun | RestaurantSitDown-Infiltration-All-Sun | RestaurantSitDown | Infiltration | All | Sun | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | Cooling Set Point | Dining | Mon - Fri | RestaurantSitDown-Cooling Set Point-Dining-Mon - Fri | RestaurantSitDown | Cooling Set Point | Dining | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | Cooling Set Point | Dining | Sat | RestaurantSitDown-Cooling Set Point-Dining-Sat | RestaurantSitDown | Cooling Set Point | Dining | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | Cooling Set Point | Dining | Sun | RestaurantSitDown-Cooling Set Point-Dining-Sun | RestaurantSitDown | Cooling Set Point | Dining | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | Cooling Set Point | Kitchen | Mon - Fri | RestaurantSitDown-Cooling Set Point-Kitchen-Mon - Fri | RestaurantSitDown | Cooling Set Point | Kitchen | Mon - Fri | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | Cooling Set Point | Kitchen | Sat | RestaurantSitDown-Cooling Set Point-Kitchen-Sat | RestaurantSitDown | Cooling Set Point | Kitchen | Sat | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | Cooling Set Point | Kitchen | Sun | RestaurantSitDown-Cooling Set Point-Kitchen-Sun | RestaurantSitDown | Cooling Set Point | Kitchen | Sun | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | Heating Set Point | Dining | Mon - Fri | RestaurantSitDown-Heating Set Point-Dining-Mon - Fri | RestaurantSitDown | Heating Set Point | Dining | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | Heating Set Point | Dining | Sat | RestaurantSitDown-Heating Set Point-Dining-Sat | RestaurantSitDown | Heating Set Point | Dining | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | Heating Set Point | Dining | Sun | RestaurantSitDown-Heating Set Point-Dining-Sun | RestaurantSitDown | Heating Set Point | Dining | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | Heating Set Point | Kitchen | Mon - Fri | RestaurantSitDown-Heating Set Point-Kitchen-Mon - Fri | RestaurantSitDown | Heating Set Point | Kitchen | Mon - Fri | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | Heating Set Point | Kitchen | Sat | RestaurantSitDown-Heating Set Point-Kitchen-Sat | RestaurantSitDown | Heating Set Point | Kitchen | Sat | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | Heating Set Point | Kitchen | Sun | RestaurantSitDown-Heating Set Point-Kitchen-Sun | RestaurantSitDown | Heating Set Point | Kitchen | Sun | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
ApartmentMidRise | Occupants | Apartment (Stay Home) | Mon - Fri | ApartmentMidRise-Occupants-Apartment (Stay Home)-Mon - Fri | ApartmentMidRise | Occupants | Apartment (Stay Home) | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Stay Home) | Sat | ApartmentMidRise-Occupants-Apartment (Stay Home)-Sat | ApartmentMidRise | Occupants | Apartment (Stay Home) | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Stay Home) | Sun | ApartmentMidRise-Occupants-Apartment (Stay Home)-Sun | ApartmentMidRise | Occupants | Apartment (Stay Home) | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Working) | Mon - Fri | ApartmentMidRise-Occupants-Apartment (Working)-Mon - Fri | ApartmentMidRise | Occupants | Apartment (Working) | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Working) | Sat | ApartmentMidRise-Occupants-Apartment (Working)-Sat | ApartmentMidRise | Occupants | Apartment (Working) | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Occupants | Apartment (Working) | Sun | ApartmentMidRise-Occupants-Apartment (Working)-Sun | ApartmentMidRise | Occupants | Apartment (Working) | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Occupants | Office | Mon - Fri | ApartmentMidRise-Occupants-Office-Mon - Fri | ApartmentMidRise | Occupants | Office | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | Occupants | Office | Sat | ApartmentMidRise-Occupants-Office-Sat | ApartmentMidRise | Occupants | Office | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | Occupants | Office | Sun | ApartmentMidRise-Occupants-Office-Sun | ApartmentMidRise | Occupants | Office | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | Lighting | Apartment | Mon - Fri | ApartmentMidRise-Lighting-Apartment-Mon - Fri | ApartmentMidRise | Lighting | Apartment | Mon - Fri | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | Lighting | Apartment | Sat | ApartmentMidRise-Lighting-Apartment-Sat | ApartmentMidRise | Lighting | Apartment | Sat | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | Lighting | Apartment | Sun | ApartmentMidRise-Lighting-Apartment-Sun | ApartmentMidRise | Lighting | Apartment | Sun | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | Lighting | Office | Mon - Fri | ApartmentMidRise-Lighting-Office-Mon - Fri | ApartmentMidRise | Lighting | Office | Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | Lighting | Office | Sat | ApartmentMidRise-Lighting-Office-Sat | ApartmentMidRise | Lighting | Office | Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | Lighting | Office | Sun | ApartmentMidRise-Lighting-Office-Sun | ApartmentMidRise | Lighting | Office | Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | Lighting | Corridor | Mon - Fri | ApartmentMidRise-Lighting-Corridor-Mon - Fri | ApartmentMidRise | Lighting | Corridor | Mon - Fri | bar: 2 to 25
ApartmentMidRise | Lighting | Corridor | Sat | ApartmentMidRise-Lighting-Corridor-Sat | ApartmentMidRise | Lighting | Corridor | Sat | bar: 2 to 25
ApartmentMidRise | Lighting | Corridor | Sun | ApartmentMidRise-Lighting-Corridor-Sun | ApartmentMidRise | Lighting | Corridor | Sun | bar: 2 to 25
ApartmentMidRise | Electric Equipment | Apartment | Mon - Fri | ApartmentMidRise-Electric Equipment-Apartment-Mon - Fri | ApartmentMidRise | Electric Equipment | Apartment | Mon - Fri | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | Electric Equipment | Apartment | Sat | ApartmentMidRise-Electric Equipment-Apartment-Sat | ApartmentMidRise | Electric Equipment | Apartment | Sat | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | Electric Equipment | Apartment | Sun | ApartmentMidRise-Electric Equipment-Apartment-Sun | ApartmentMidRise | Electric Equipment | Apartment | Sun | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | Electric Equipment | Office | Mon - Fri | ApartmentMidRise-Electric Equipment-Office-Mon - Fri | ApartmentMidRise | Electric Equipment | Office | Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | Electric Equipment | Office | Sat | ApartmentMidRise-Electric Equipment-Office-Sat | ApartmentMidRise | Electric Equipment | Office | Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | Electric Equipment | Office | Sun | ApartmentMidRise-Electric Equipment-Office-Sun | ApartmentMidRise | Electric Equipment | Office | Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | HVAC | All | Mon - Fri | ApartmentMidRise-HVAC-All-Mon - Fri | ApartmentMidRise | HVAC | All | Mon - Fri | bar: 2 to 25
ApartmentMidRise | HVAC | All | Sat | ApartmentMidRise-HVAC-All-Sat | ApartmentMidRise | HVAC | All | Sat | bar: 2 to 25
ApartmentMidRise | HVAC | All | Sun | ApartmentMidRise-HVAC-All-Sun | ApartmentMidRise | HVAC | All | Sun | bar: 2 to 25
ApartmentMidRise | SWH | All | Mon - Fri | ApartmentMidRise-SWH-All-Mon - Fri | ApartmentMidRise | SWH | All | Mon - Fri | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | SWH | All | Sat | ApartmentMidRise-SWH-All-Sat | ApartmentMidRise | SWH | All | Sat | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | SWH | All | Sun | ApartmentMidRise-SWH-All-Sun | ApartmentMidRise | SWH | All | Sun | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | Elevator | All | Mon - Fri | ApartmentMidRise-Elevator-All-Mon - Fri | ApartmentMidRise | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | Elevator | All | Sat | ApartmentMidRise-Elevator-All-Sat | ApartmentMidRise | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | Elevator | All | Sun | ApartmentMidRise-Elevator-All-Sun | ApartmentMidRise | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | Infiltration | All | Mon - Fri | ApartmentMidRise-Infiltration-All-Mon - Fri | ApartmentMidRise | Infiltration | All | Mon - Fri | bar: 2 to 25
ApartmentMidRise | Infiltration | All | Sat | ApartmentMidRise-Infiltration-All-Sat | ApartmentMidRise | Infiltration | All | Sat | bar: 2 to 25
ApartmentMidRise | Infiltration | All | Sun | ApartmentMidRise-Infiltration-All-Sun | ApartmentMidRise | Infiltration | All | Sun | bar: 2 to 25
ApartmentMidRise | Cooling Set Point | Apartment | Mon - Fri | ApartmentMidRise-Cooling Set Point-Apartment-Mon - Fri | ApartmentMidRise | Cooling Set Point | Apartment | Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | Cooling Set Point | Apartment | Sat | ApartmentMidRise-Cooling Set Point-Apartment-Sat | ApartmentMidRise | Cooling Set Point | Apartment | Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | Cooling Set Point | Apartment | Sun | ApartmentMidRise-Cooling Set Point-Apartment-Sun | ApartmentMidRise | Cooling Set Point | Apartment | Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | Cooling Set Point | Office | Mon - Fri | ApartmentMidRise-Cooling Set Point-Office-Mon - Fri | ApartmentMidRise | Cooling Set Point | Office | Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | Cooling Set Point | Office | Sat | ApartmentMidRise-Cooling Set Point-Office-Sat | ApartmentMidRise | Cooling Set Point | Office | Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | Cooling Set Point | Office | Sun | ApartmentMidRise-Cooling Set Point-Office-Sun | ApartmentMidRise | Cooling Set Point | Office | Sun | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | Heating Set Point | Apartment | Mon - Fri | ApartmentMidRise-Heating Set Point-Apartment-Mon - Fri | ApartmentMidRise | Heating Set Point | Apartment | Mon - Fri | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | Heating Set Point | Apartment | Sat | ApartmentMidRise-Heating Set Point-Apartment-Sat | ApartmentMidRise | Heating Set Point | Apartment | Sat | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | Heating Set Point | Apartment | Sun | ApartmentMidRise-Heating Set Point-Apartment-Sun | ApartmentMidRise | Heating Set Point | Apartment | Sun | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | Heating Set Point | Office | Mon - Fri | ApartmentMidRise-Heating Set Point-Office-Mon - Fri | ApartmentMidRise | Heating Set Point | Office | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | Heating Set Point | Office | Sat | ApartmentMidRise-Heating Set Point-Office-Sat | ApartmentMidRise | Heating Set Point | Office | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | Heating Set Point | Office | Sun | ApartmentMidRise-Heating Set Point-Office-Sun | ApartmentMidRise | Heating Set Point | Office | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | Occupants | Apartment (Stay Home) | Mon - Fri | ApartmentHighRise-Occupants-Apartment (Stay Home)-Mon - Fri | ApartmentHighRise | Occupants | Apartment (Stay Home) | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Stay Home) | Sat | ApartmentHighRise-Occupants-Apartment (Stay Home)-Sat | ApartmentHighRise | Occupants | Apartment (Stay Home) | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Stay Home) | Sun | ApartmentHighRise-Occupants-Apartment (Stay Home)-Sun | ApartmentHighRise | Occupants | Apartment (Stay Home) | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Working) | Mon - Fri | ApartmentHighRise-Occupants-Apartment (Working)-Mon - Fri | ApartmentHighRise | Occupants | Apartment (Working) | Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Working) | Sat | ApartmentHighRise-Occupants-Apartment (Working)-Sat | ApartmentHighRise | Occupants | Apartment (Working) | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Occupants | Apartment (Working) | Sun | ApartmentHighRise-Occupants-Apartment (Working)-Sun | ApartmentHighRise | Occupants | Apartment (Working) | Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Occupants | Office | Mon - Fri | ApartmentHighRise-Occupants-Office-Mon - Fri | ApartmentHighRise | Occupants | Office | Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | Occupants | Office | Sat | ApartmentHighRise-Occupants-Office-Sat | ApartmentHighRise | Occupants | Office | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | Occupants | Office | Sun | ApartmentHighRise-Occupants-Office-Sun | ApartmentHighRise | Occupants | Office | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | Lighting | Apartment | Mon - Fri | ApartmentHighRise-Lighting-Apartment-Mon - Fri | ApartmentHighRise | Lighting | Apartment | Mon - Fri | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | Lighting | Apartment | Sat | ApartmentHighRise-Lighting-Apartment-Sat | ApartmentHighRise | Lighting | Apartment | Sat | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | Lighting | Apartment | Sun | ApartmentHighRise-Lighting-Apartment-Sun | ApartmentHighRise | Lighting | Apartment | Sun | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | Lighting | Office | Mon - Fri | ApartmentHighRise-Lighting-Office-Mon - Fri | ApartmentHighRise | Lighting | Office | Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | Lighting | Office | Sat | ApartmentHighRise-Lighting-Office-Sat | ApartmentHighRise | Lighting | Office | Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | Lighting | Office | Sun | ApartmentHighRise-Lighting-Office-Sun | ApartmentHighRise | Lighting | Office | Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | Lighting | Corridor | Mon - Fri | ApartmentHighRise-Lighting-Corridor-Mon - Fri | ApartmentHighRise | Lighting | Corridor | Mon - Fri | bar: 2 to 25
ApartmentHighRise | Lighting | Corridor | Sat | ApartmentHighRise-Lighting-Corridor-Sat | ApartmentHighRise | Lighting | Corridor | Sat | bar: 2 to 25
ApartmentHighRise | Lighting | Corridor | Sun | ApartmentHighRise-Lighting-Corridor-Sun | ApartmentHighRise | Lighting | Corridor | Sun | bar: 2 to 25
ApartmentHighRise | Electric Equipment | Apartment | Mon - Fri | ApartmentHighRise-Electric Equipment-Apartment-Mon - Fri | ApartmentHighRise | Electric Equipment | Apartment | Mon - Fri | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | Electric Equipment | Apartment | Sat | ApartmentHighRise-Electric Equipment-Apartment-Sat | ApartmentHighRise | Electric Equipment | Apartment | Sat | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | Electric Equipment | Apartment | Sun | ApartmentHighRise-Electric Equipment-Apartment-Sun | ApartmentHighRise | Electric Equipment | Apartment | Sun | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | Electric Equipment | Office | Mon - Fri | ApartmentHighRise-Electric Equipment-Office-Mon - Fri | ApartmentHighRise | Electric Equipment | Office | Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | Electric Equipment | Office | Sat | ApartmentHighRise-Electric Equipment-Office-Sat | ApartmentHighRise | Electric Equipment | Office | Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | Electric Equipment | Office | Sun | ApartmentHighRise-Electric Equipment-Office-Sun | ApartmentHighRise | Electric Equipment | Office | Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | HVAC | All | Mon - Fri | ApartmentHighRise-HVAC-All-Mon - Fri | ApartmentHighRise | HVAC | All | Mon - Fri | bar: 2 to 25
ApartmentHighRise | HVAC | All | Sat | ApartmentHighRise-HVAC-All-Sat | ApartmentHighRise | HVAC | All | Sat | bar: 2 to 25
ApartmentHighRise | HVAC | All | Sun | ApartmentHighRise-HVAC-All-Sun | ApartmentHighRise | HVAC | All | Sun | bar: 2 to 25
ApartmentHighRise | SWH | All | Mon - Fri | ApartmentHighRise-SWH-All-Mon - Fri | ApartmentHighRise | SWH | All | Mon - Fri | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | SWH | All | Sat | ApartmentHighRise-SWH-All-Sat | ApartmentHighRise | SWH | All | Sat | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | SWH | All | Sun | ApartmentHighRise-SWH-All-Sun | ApartmentHighRise | SWH | All | Sun | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | Elevator | All | Mon - Fri | ApartmentHighRise-Elevator-All-Mon - Fri | ApartmentHighRise | Elevator | All | Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | Elevator | All | Sat | ApartmentHighRise-Elevator-All-Sat | ApartmentHighRise | Elevator | All | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | Elevator | All | Sun | ApartmentHighRise-Elevator-All-Sun | ApartmentHighRise | Elevator | All | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | Infiltration | All | Mon - Fri | ApartmentHighRise-Infiltration-All-Mon - Fri | ApartmentHighRise | Infiltration | All | Mon - Fri | bar: 2 to 25
ApartmentHighRise | Infiltration | All | Sat | ApartmentHighRise-Infiltration-All-Sat | ApartmentHighRise | Infiltration | All | Sat | bar: 2 to 25
ApartmentHighRise | Infiltration | All | Sun | ApartmentHighRise-Infiltration-All-Sun | ApartmentHighRise | Infiltration | All | Sun | bar: 2 to 25
ApartmentHighRise | Cooling Set Point | Apartment | Mon - Fri | ApartmentHighRise-Cooling Set Point-Apartment-Mon - Fri | ApartmentHighRise | Cooling Set Point | Apartment | Mon - Fri | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | Cooling Set Point | Apartment | Sat | ApartmentHighRise-Cooling Set Point-Apartment-Sat | ApartmentHighRise | Cooling Set Point | Apartment | Sat | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | Cooling Set Point | Apartment | Sun | ApartmentHighRise-Cooling Set Point-Apartment-Sun | ApartmentHighRise | Cooling Set Point | Apartment | Sun | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | Cooling Set Point | Office | Mon - Fri | ApartmentHighRise-Cooling Set Point-Office-Mon - Fri | ApartmentHighRise | Cooling Set Point | Office | Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | Cooling Set Point | Office | Sat | ApartmentHighRise-Cooling Set Point-Office-Sat | ApartmentHighRise | Cooling Set Point | Office | Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | Cooling Set Point | Office | Sun | ApartmentHighRise-Cooling Set Point-Office-Sun | ApartmentHighRise | Cooling Set Point | Office | Sun | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | Heating Set Point | Apartment | Mon - Fri | ApartmentHighRise-Heating Set Point-Apartment-Mon - Fri | ApartmentHighRise | Heating Set Point | Apartment | Mon - Fri | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | Heating Set Point | Apartment | Sat | ApartmentHighRise-Heating Set Point-Apartment-Sat | ApartmentHighRise | Heating Set Point | Apartment | Sat | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | Heating Set Point | Apartment | Sun | ApartmentHighRise-Heating Set Point-Apartment-Sun | ApartmentHighRise | Heating Set Point | Apartment | Sun | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | Heating Set Point | Office | Mon - Fri | ApartmentHighRise-Heating Set Point-Office-Mon - Fri | ApartmentHighRise | Heating Set Point | Office | Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | Heating Set Point | Office | Sat | ApartmentHighRise-Heating Set Point-Office-Sat | ApartmentHighRise | Heating Set Point | Office | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | Heating Set Point | Office | Sun | ApartmentHighRise-Heating Set Point-Office-Sun | ApartmentHighRise | Heating Set Point | Office | Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6

## schedule_mapping (hidden)
Prototype | Schedule | Type | Through | Day of Week | Used? | Prototype | Schedule | Space Type | Day of Week |  | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00 | 0:00
ApartmentHighRise | OCC_APT_SCH_STAY_HOME_FAMILY | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Occupants | Apartment (Stay Home) | Mon - Fri | ApartmentHighRise-Occupants-Apartment (Stay Home)-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | OCC_APT_SCH_STAY_HOME_FAMILY | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Occupants | Apartment (Stay Home) | Sat | ApartmentHighRise-Occupants-Apartment (Stay Home)-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | OCC_APT_SCH_STAY_HOME_FAMILY | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Occupants | Apartment (Stay Home) | Sun | ApartmentHighRise-Occupants-Apartment (Stay Home)-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | OCC_APT_SCH_CORRIDOR | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | OCC_APT_SCH_CORRIDOR | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | OCC_APT_SCH_CORRIDOR | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentHighRise | OCC_APT_SCH_WORKING_FAMILY | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Occupants | Apartment (Working) | Mon - Fri | ApartmentHighRise-Occupants-Apartment (Working)-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | OCC_APT_SCH_WORKING_FAMILY | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Occupants | Apartment (Working) | Sat | ApartmentHighRise-Occupants-Apartment (Working)-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | OCC_APT_SCH_WORKING_FAMILY | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Occupants | Apartment (Working) | Sun | ApartmentHighRise-Occupants-Apartment (Working)-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | OCC_OFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | OCC_OFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | OCC_OFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | OCC_OFF_w_SB_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Occupants | Office | Mon - Fri | ApartmentHighRise-Occupants-Office-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | OCC_OFF_w_SB_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Occupants | Office | Sat | ApartmentHighRise-Occupants-Office-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | OCC_OFF_w_SB_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Occupants | Office | Sun | ApartmentHighRise-Occupants-Office-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Lighting | Office | Mon - Fri | ApartmentHighRise-Lighting-Office-Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | ltg_sch_office | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Lighting | Office | Sat | ApartmentHighRise-Lighting-Office-Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | ltg_sch_office | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Lighting | Office | Sun | ApartmentHighRise-Lighting-Office-Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentHighRise | ltg_sch_corridor | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Lighting | Corridor | Mon - Fri | ApartmentHighRise-Lighting-Corridor-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ltg_sch_corridor | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Lighting | Corridor | Sat | ApartmentHighRise-Lighting-Corridor-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ltg_sch_corridor | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Lighting | Corridor | Sun | ApartmentHighRise-Lighting-Corridor-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ltg_sch_apartment_hardwired | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Lighting | Apartment | Mon - Fri | ApartmentHighRise-Lighting-Apartment-Mon - Fri | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | ltg_sch_apartment_hardwired | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Lighting | Apartment | Sat | ApartmentHighRise-Lighting-Apartment-Sat | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | ltg_sch_apartment_hardwired | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Lighting | Apartment | Sun | ApartmentHighRise-Lighting-Apartment-Sun | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | ltg_sch_apartment_plugin | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_apartment_hardwired) |  |  |  |  | --- | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | ltg_sch_apartment_plugin | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_apartment_hardwired) |  |  |  |  | --- | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | ltg_sch_apartment_plugin | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_apartment_hardwired) |  |  |  |  | --- | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentHighRise | EQP_APT_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Electric Equipment | Apartment | Mon - Fri | ApartmentHighRise-Electric Equipment-Apartment-Mon - Fri | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | EQP_APT_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Electric Equipment | Apartment | Sat | ApartmentHighRise-Electric Equipment-Apartment-Sat | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | EQP_APT_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Electric Equipment | Apartment | Sun | ApartmentHighRise-Electric Equipment-Apartment-Sun | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentHighRise | EQP_OFF_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Electric Equipment | Office | Mon - Fri | ApartmentHighRise-Electric Equipment-Office-Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | EQP_OFF_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Electric Equipment | Office | Sat | ApartmentHighRise-Electric Equipment-Office-Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | EQP_OFF_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Electric Equipment | Office | Sun | ApartmentHighRise-Electric Equipment-Office-Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentHighRise | INF_APT_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Infiltration | All | Mon - Fri | ApartmentHighRise-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | INF_APT_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Infiltration | All | Sat | ApartmentHighRise-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | INF_APT_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Infiltration | All | Sun | ApartmentHighRise-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
ApartmentHighRise | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
ApartmentHighRise | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
ApartmentHighRise | HTGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | CLGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | S HTGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Heating Set Point | Apartment | Mon - Fri | ApartmentHighRise-Heating Set Point-Apartment-Mon - Fri | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | S HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | Yes | ApartmentHighRise | Heating Set Point | Apartment | Sat | ApartmentHighRise-Heating Set Point-Apartment-Sat | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | S HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | Yes | ApartmentHighRise | Heating Set Point | Apartment | Sun | ApartmentHighRise-Heating Set Point-Apartment-Sun | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | S CLGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Cooling Set Point | Apartment | Mon - Fri | ApartmentHighRise-Cooling Set Point-Apartment-Mon - Fri | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | S CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | Yes | ApartmentHighRise | Cooling Set Point | Apartment | Sat | ApartmentHighRise-Cooling Set Point-Apartment-Sat | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | S CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | Yes | ApartmentHighRise | Cooling Set Point | Apartment | Sun | ApartmentHighRise-Cooling Set Point-Apartment-Sun | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | N HTGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | No (the same as S HTGSETP_APT_SCH) |  |  |  |  | --- | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | N HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | No (the same as S HTGSETP_APT_SCH) |  |  |  |  | --- | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | N HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | No (the same as S HTGSETP_APT_SCH) |  |  |  |  | --- | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7 | 21.7
ApartmentHighRise | N CLGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | No (the same as S CLGSETP_APT_SCH) |  |  |  |  | --- | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | N CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | No (the same as S CLGSETP_APT_SCH) |  |  |  |  | --- | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | N CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | No (the same as S CLGSETP_APT_SCH) |  |  |  |  | --- | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 24.4
ApartmentHighRise | HTGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentHighRise | HTGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentHighRise | HTGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentHighRise | CLGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | CLGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | CLGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | HTGSETP_OFF_SCH_No_Optimum | Temperature | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Heating Set Point | Office | Mon - Fri | ApartmentHighRise-Heating Set Point-Office-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | HTGSETP_OFF_SCH_No_Optimum | Temperature | 2023-12-31 | Sat | Yes | ApartmentHighRise | Heating Set Point | Office | Sat | ApartmentHighRise-Heating Set Point-Office-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | HTGSETP_OFF_SCH_No_Optimum | Temperature | 2023-12-31 | Sun | Yes | ApartmentHighRise | Heating Set Point | Office | Sun | ApartmentHighRise-Heating Set Point-Office-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | HTGSETP_OFF_SCH_Yes_Optimum | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | HTGSETP_OFF_SCH_Yes_Optimum | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | HTGSETP_OFF_SCH_Yes_Optimum | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | HTGSETP_OFF_SCH_Yes_Optimum_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 20 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | HTGSETP_OFF_SCH_Yes_Optimum_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | HTGSETP_OFF_SCH_Yes_Optimum_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentHighRise | CLGSETP_OFF_SCH_Yes_Optimum | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 27.8 | 25.6 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise | CLGSETP_OFF_SCH_Yes_Optimum | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise | CLGSETP_OFF_SCH_Yes_Optimum | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise | CLGSETP_OFF_SCH_Yes_Optimum_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 27.8 | 25.6 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 25 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise | CLGSETP_OFF_SCH_Yes_Optimum_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise | CLGSETP_OFF_SCH_Yes_Optimum_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentHighRise | CLGSETP_OFF_SCH_No_Setback | Temperature | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Cooling Set Point | Office | Mon - Fri | ApartmentHighRise-Cooling Set Point-Office-Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | CLGSETP_OFF_SCH_No_Setback | Temperature | 2023-12-31 | Sat | Yes | ApartmentHighRise | Cooling Set Point | Office | Sat | ApartmentHighRise-Cooling Set Point-Office-Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | CLGSETP_OFF_SCH_No_Setback | Temperature | 2023-12-31 | Sun | Yes | ApartmentHighRise | Cooling Set Point | Office | Sun | ApartmentHighRise-Cooling Set Point-Office-Sun | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentHighRise | Activity Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
ApartmentHighRise | Activity Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
ApartmentHighRise | Activity Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
ApartmentHighRise | All Off | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | All Off | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | All Off | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentHighRise | All On | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | HVAC | All | Mon - Fri | ApartmentHighRise-HVAC-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | All On | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | HVAC | All | Sat | ApartmentHighRise-HVAC-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | All On | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | HVAC | All | Sun | ApartmentHighRise-HVAC-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | AllOn_Except_DD | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | AllOn_Except_DD | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | AllOn_Except_DD | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ZONE CONTROL TYPE SCHED | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
ApartmentHighRise | ZONE CONTROL TYPE SCHED | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
ApartmentHighRise | ZONE CONTROL TYPE SCHED | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
ApartmentHighRise | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHW TARGET TEMP SCHED | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHW TARGET TEMP SCHED | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHW TARGET TEMP SCHED | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentHighRise | SHW SUPPLY TEMP SCHED | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
ApartmentHighRise | SHW SUPPLY TEMP SCHED | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
ApartmentHighRise | SHW SUPPLY TEMP SCHED | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
ApartmentHighRise | SHW Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ApartmentHighRise | SHW Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ApartmentHighRise | SHW Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
ApartmentHighRise | SHW Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
ApartmentHighRise | SHW Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
ApartmentHighRise | SHW Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
ApartmentHighRise | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Ambient Temp Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ApartmentHighRise | Ambient Temp Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ApartmentHighRise | Ambient Temp Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
ApartmentHighRise | APT_DHW_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | SWH | All | Mon - Fri | ApartmentHighRise-SWH-All-Mon - Fri | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | APT_DHW_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | SWH | All | Sat | ApartmentHighRise-SWH-All-Sat | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | APT_DHW_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | SWH | All | Sun | ApartmentHighRise-SWH-All-Sun | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentHighRise | SupplyFanSch | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | SupplyFanSch | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | SupplyFanSch | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | PLANT LOOP HIGH TEMP SCHEDULE | TEMPERATURE | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
ApartmentHighRise | PLANT LOOP HIGH TEMP SCHEDULE | TEMPERATURE | 2023-12-31 | Sat | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
ApartmentHighRise | PLANT LOOP HIGH TEMP SCHEDULE | TEMPERATURE | 2023-12-31 | Sun | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
ApartmentHighRise | PLANT LOOP LOW TEMP SCHEDULE | TEMPERATURE | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
ApartmentHighRise | PLANT LOOP LOW TEMP SCHEDULE | TEMPERATURE | 2023-12-31 | Sat | No |  |  |  |  | --- | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
ApartmentHighRise | PLANT LOOP LOW TEMP SCHEDULE | TEMPERATURE | 2023-12-31 | Sun | No |  |  |  |  | --- | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
ApartmentHighRise | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentHighRise | Elevator | All | Mon - Fri | ApartmentHighRise-Elevator-All-Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | ApartmentHighRise | Elevator | All | Sat | ApartmentHighRise-Elevator-All-Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | ApartmentHighRise | Elevator | All | Sun | ApartmentHighRise-Elevator-All-Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentHighRise | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentHighRise | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
ApartmentHighRise | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
ApartmentHighRise | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
ApartmentMidRise | OCC_APT_SCH_STAY_HOME_FAMILY | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Occupants | Apartment (Stay Home) | Mon - Fri | ApartmentMidRise-Occupants-Apartment (Stay Home)-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | OCC_APT_SCH_STAY_HOME_FAMILY | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Occupants | Apartment (Stay Home) | Sat | ApartmentMidRise-Occupants-Apartment (Stay Home)-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | OCC_APT_SCH_STAY_HOME_FAMILY | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Occupants | Apartment (Stay Home) | Sun | ApartmentMidRise-Occupants-Apartment (Stay Home)-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | OCC_APT_SCH_CORRIDOR | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | OCC_APT_SCH_CORRIDOR | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | OCC_APT_SCH_CORRIDOR | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.85 | 0.39 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.3 | 0.52 | 0.87 | 0.87 | 0.87 | 1 | 1 | 1
ApartmentMidRise | OCC_APT_SCH_WORKING_FAMILY | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Occupants | Apartment (Working) | Mon - Fri | ApartmentMidRise-Occupants-Apartment (Working)-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | OCC_APT_SCH_WORKING_FAMILY | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Occupants | Apartment (Working) | Sat | ApartmentMidRise-Occupants-Apartment (Working)-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | OCC_APT_SCH_WORKING_FAMILY | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Occupants | Apartment (Working) | Sun | ApartmentMidRise-Occupants-Apartment (Working)-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | OCC_OFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | OCC_OFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | OCC_OFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | OCC_OFF_w_SB_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Occupants | Office | Mon - Fri | ApartmentMidRise-Occupants-Office-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | OCC_OFF_w_SB_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Occupants | Office | Sat | ApartmentMidRise-Occupants-Office-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | OCC_OFF_w_SB_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Occupants | Office | Sun | ApartmentMidRise-Occupants-Office-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Lighting | Office | Mon - Fri | ApartmentMidRise-Lighting-Office-Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | ltg_sch_office | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Lighting | Office | Sat | ApartmentMidRise-Lighting-Office-Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | ltg_sch_office | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Lighting | Office | Sun | ApartmentMidRise-Lighting-Office-Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
ApartmentMidRise | ltg_sch_corridor | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Lighting | Corridor | Mon - Fri | ApartmentMidRise-Lighting-Corridor-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | ltg_sch_corridor | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Lighting | Corridor | Sat | ApartmentMidRise-Lighting-Corridor-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | ltg_sch_corridor | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Lighting | Corridor | Sun | ApartmentMidRise-Lighting-Corridor-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | ltg_sch_apartment_hardwired | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Lighting | Apartment | Mon - Fri | ApartmentMidRise-Lighting-Apartment-Mon - Fri | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | ltg_sch_apartment_hardwired | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Lighting | Apartment | Sat | ApartmentMidRise-Lighting-Apartment-Sat | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | ltg_sch_apartment_hardwired | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Lighting | Apartment | Sun | ApartmentMidRise-Lighting-Apartment-Sun | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | ltg_sch_apartment_plugin | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_apartment_hardwired) |  |  |  |  | --- | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | ltg_sch_apartment_plugin | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_apartment_hardwired) |  |  |  |  | --- | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | ltg_sch_apartment_plugin | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_apartment_hardwired) |  |  |  |  | --- | 0.01132 | 0.01132 | 0.01132 | 0.01132 | 0.03395 | 0.07355 | 0.07921 | 0.07355 | 0.03395 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.02263 | 0.03961 | 0.07921 | 0.11316 | 0.15277 | 0.18106 | 0.18106 | 0.12448 | 0.0679 | 0.02829
ApartmentMidRise | EQP_APT_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Electric Equipment | Apartment | Mon - Fri | ApartmentMidRise-Electric Equipment-Apartment-Mon - Fri | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | EQP_APT_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Electric Equipment | Apartment | Sat | ApartmentMidRise-Electric Equipment-Apartment-Sat | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | EQP_APT_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Electric Equipment | Apartment | Sun | ApartmentMidRise-Electric Equipment-Apartment-Sun | 0.45 | 0.41 | 0.39 | 0.38 | 0.38 | 0.43 | 0.54 | 0.65 | 0.66 | 0.67 | 0.69 | 0.7 | 0.69 | 0.66 | 0.65 | 0.68 | 0.8 | 1 | 1 | 0.93 | 0.89 | 0.85 | 0.71 | 0.58
ApartmentMidRise | EQP_OFF_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Electric Equipment | Office | Mon - Fri | ApartmentMidRise-Electric Equipment-Office-Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | EQP_OFF_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Electric Equipment | Office | Sat | ApartmentMidRise-Electric Equipment-Office-Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | EQP_OFF_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Electric Equipment | Office | Sun | ApartmentMidRise-Electric Equipment-Office-Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
ApartmentMidRise | INF_APT_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Infiltration | All | Mon - Fri | ApartmentMidRise-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INF_APT_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Infiltration | All | Sat | ApartmentMidRise-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INF_APT_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Infiltration | All | Sun | ApartmentMidRise-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INF_OFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as INF_APT_SCH) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INF_OFF_SCH | Fraction | 2023-12-31 | Sat | No (the same as INF_APT_SCH) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INF_OFF_SCH | Fraction | 2023-12-31 | Sun | No (the same as INF_APT_SCH) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INF_COR_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INF_COR_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INF_COR_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
ApartmentMidRise | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
ApartmentMidRise | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
ApartmentMidRise | HTGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | CLGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | S HTGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Heating Set Point | Apartment | Mon - Fri | ApartmentMidRise-Heating Set Point-Apartment-Mon - Fri | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | S HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | Yes | ApartmentMidRise | Heating Set Point | Apartment | Sat | ApartmentMidRise-Heating Set Point-Apartment-Sat | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | S HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | Yes | ApartmentMidRise | Heating Set Point | Apartment | Sun | ApartmentMidRise-Heating Set Point-Apartment-Sun | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | S CLGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Cooling Set Point | Apartment | Mon - Fri | ApartmentMidRise-Cooling Set Point-Apartment-Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | S CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | Yes | ApartmentMidRise | Cooling Set Point | Apartment | Sat | ApartmentMidRise-Cooling Set Point-Apartment-Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | S CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | Yes | ApartmentMidRise | Cooling Set Point | Apartment | Sun | ApartmentMidRise-Cooling Set Point-Apartment-Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | N HTGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | No (the same as S HTGSETP_APT_SCH) |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | N HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | No (the same as S HTGSETP_APT_SCH) |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | N HTGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | No (the same as S HTGSETP_APT_SCH) |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | N CLGSETP_APT_SCH | Temperature | 2023-12-31 | Mon - Fri | No (the same as S CLGSETP_APT_SCH) |  |  |  |  | --- | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | N CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sat | No (the same as S CLGSETP_APT_SCH) |  |  |  |  | --- | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | N CLGSETP_APT_SCH | Temperature | 2023-12-31 | Sun | No (the same as S CLGSETP_APT_SCH) |  |  |  |  | --- | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
ApartmentMidRise | HTGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | HTGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | HTGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
ApartmentMidRise | CLGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | CLGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | CLGSETP_DESIGN_OFF_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | HTGSETP_OFF_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Heating Set Point | Office | Mon - Fri | ApartmentMidRise-Heating Set Point-Office-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | HTGSETP_OFF_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | ApartmentMidRise | Heating Set Point | Office | Sat | ApartmentMidRise-Heating Set Point-Office-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | HTGSETP_OFF_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | ApartmentMidRise | Heating Set Point | Office | Sun | ApartmentMidRise-Heating Set Point-Office-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | HTGSETP_OFF_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | HTGSETP_OFF_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | HTGSETP_OFF_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | HTGSETP_OFF_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 20 | 18.3 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | HTGSETP_OFF_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | HTGSETP_OFF_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
ApartmentMidRise | CLGSETP_OFF_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 26.7 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
ApartmentMidRise | CLGSETP_OFF_SCH_No_Setback | Temperature | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Cooling Set Point | Office | Mon - Fri | ApartmentMidRise-Cooling Set Point-Office-Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | CLGSETP_OFF_SCH_No_Setback | Temperature | 2023-12-31 | Sat | Yes | ApartmentMidRise | Cooling Set Point | Office | Sat | ApartmentMidRise-Cooling Set Point-Office-Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | CLGSETP_OFF_SCH_No_Setback | Temperature | 2023-12-31 | Sun | Yes | ApartmentMidRise | Cooling Set Point | Office | Sun | ApartmentMidRise-Cooling Set Point-Office-Sun | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
ApartmentMidRise | Activity Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
ApartmentMidRise | Activity Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
ApartmentMidRise | Activity Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
ApartmentMidRise | All Off | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | All Off | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | All Off | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ApartmentMidRise | All On | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | HVAC | All | Mon - Fri | ApartmentMidRise-HVAC-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | All On | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | HVAC | All | Sat | ApartmentMidRise-HVAC-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | All On | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | HVAC | All | Sun | ApartmentMidRise-HVAC-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Always_On | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Always_On | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Always_On | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | AllOn_Except_DD | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | AllOn_Except_DD | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | AllOn_Except_DD | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | ZONE CONTROL TYPE SCHED | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
ApartmentMidRise | ZONE CONTROL TYPE SCHED | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
ApartmentMidRise | ZONE CONTROL TYPE SCHED | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
ApartmentMidRise | APT_DHW_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | SWH | All | Mon - Fri | ApartmentMidRise-SWH-All-Mon - Fri | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | APT_DHW_SCH | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | SWH | All | Sat | ApartmentMidRise-SWH-All-Sat | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | APT_DHW_SCH | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | SWH | All | Sun | ApartmentMidRise-SWH-All-Sun | 0.08 | 0.04 | 0.01 | 0.01 | 0.04 | 0.27 | 0.94 | 1 | 0.96 | 0.84 | 0.76 | 0.61 | 0.53 | 0.47 | 0.41 | 0.47 | 0.55 | 0.73 | 0.86 | 0.82 | 0.75 | 0.61 | 0.53 | 0.29
ApartmentMidRise | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentMidRise | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentMidRise | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
ApartmentMidRise | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | ApartmentMidRise | Elevator | All | Mon - Fri | ApartmentMidRise-Elevator-All-Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | ApartmentMidRise | Elevator | All | Sat | ApartmentMidRise-Elevator-All-Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | ApartmentMidRise | Elevator | All | Sun | ApartmentMidRise-Elevator-All-Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
ApartmentMidRise | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
ApartmentMidRise | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
ApartmentMidRise | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
ApartmentMidRise | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
Hospital | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | HVACOperationSchd | on/off | 2023-12-31 | Mon - Fri | Yes | Hospital | HVAC | All | Mon - Fri | Hospital-HVAC-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | HVACOperationSchd | on/off | 2023-12-31 | Sat | Yes | Hospital | HVAC | All | Sat | Hospital-HVAC-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | HVACOperationSchd | on/off | 2023-12-31 | Sun | Yes | Hospital | HVAC | All | Sun | Hospital-HVAC-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | ltg_sch14_dining | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Mon - Fri | Hospital-Lighting-ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen-Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch14_dining | Fraction | 2023-12-31 | Sat | Yes | Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Sat | Hospital-Lighting-ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen-Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch14_dining | Fraction | 2023-12-31 | Sun | Yes | Hospital | Lighting | ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen | Sun | Hospital-Lighting-ER, Corridor, Patient Rm, Nurse Station, Nurse Station Lobby 2, Dining, Kitchen-Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch7_ic | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch7_ic | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch7_ic | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch3_record | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Mon - Fri | Hospital-Lighting-Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch3_record | Fraction | 2023-12-31 | Sat | Yes | Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Sat | Hospital-Lighting-Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch3_record | Fraction | 2023-12-31 | Sun | Yes | Hospital | Lighting | Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology | Sun | Hospital-Lighting-Basement, Office, Lobby, Nurse Station Lobby 1, OR, Physical Therapy, Lab, Radiology-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ltg_sch0_basement | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch0_basement | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch0_basement | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ltg_sch10_patient_room | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch10_patient_room | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch10_patient_room | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch4_corridor | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch4_corridor | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch4_corridor | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch11_physical_therapy | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch11_physical_therapy | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch11_physical_therapy | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ltg_sch13_radiology | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch13_radiology | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch13_radiology | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ltg_sch15_kitchen | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch15_kitchen | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch15_kitchen | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch_office1_flr_5 | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch_office1_flr_5 | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch_office1_flr_5 | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ltg_sch6_or | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch6_or | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch6_or | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ltg_sch1_office | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch1_office | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch1_office | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ltg_sch9_nursestn_lobby2 | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch9_nursestn_lobby2 | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch9_nursestn_lobby2 | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch12_lab | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch12_lab | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch12_lab | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ltg_sch8_nursstn | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch8_nursstn | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch8_nursstn | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch2_er | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch2_er | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch2_er | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch14_dining) |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | ltg_sch5_nursestn_lobby1 | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | ltg_sch5_nursestn_lobby1 | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | ltg_sch5_nursestn_lobby1 | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch3_record) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1
Hospital | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Hospital | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Mon - Fri | Hospital-Occupants-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0 | 0
Hospital | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sat | Hospital-Occupants-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hospital | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | Hospital | Occupants | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sun | Hospital-Occupants-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | BLDG_OCC_EXTD_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Mon - Fri | Hospital-Occupants-ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | BLDG_OCC_EXTD_SCH | Fraction | 2023-12-31 | Sat | Yes | Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sat | Hospital-Occupants-ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | BLDG_OCC_EXTD_SCH | Fraction | 2023-12-31 | Sun | Yes | Hospital | Occupants | ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sun | Hospital-Occupants-ER, Corridor, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Sun | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Mon - Fri | Hospital-Electric Equipment-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
Hospital | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sat | Hospital-Electric Equipment-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | Hospital | Electric Equipment | Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2 | Sun | Hospital-Electric Equipment-Basement, Office, Lobby, OR, Physical Therapy, Lab, Radiology, Nurse Station Lobby2-Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | BLDG_EQUIP_EXTD_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Mon - Fri | Hospital-Electric Equipment-ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4
Hospital | BLDG_EQUIP_EXTD_SCH | Fraction | 2023-12-31 | Sat | Yes | Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sat | Hospital-Electric Equipment-ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.5 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | BLDG_EQUIP_EXTD_SCH | Fraction | 2023-12-31 | Sun | Yes | Hospital | Electric Equipment | ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen | Sun | Hospital-Electric Equipment-ER, Patient Rm, ICU, Nurse Station Lobby1, Dinning, Kitchen-Sun | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
Hospital | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | Elevator | All | Mon - Fri | Hospital-Elevator-All-Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2
Hospital | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | Hospital | Elevator | All | Sat | Hospital-Elevator-All-Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | Hospital | Elevator | All | Sun | Hospital-Elevator-All-Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | Dishwashing Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Dishwashing Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Dishwashing Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Dishwashing Booster Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
Hospital | Dishwashing Booster Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
Hospital | Dishwashing Booster Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
Hospital | Laundry Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
Hospital | Laundry Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
Hospital | Laundry Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
Hospital | LAUNDRY_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | LAUNDRY_SWH_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | LAUNDRY_SWH_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | SWH | Office, Lobby, Clinic, OR | Mon - Fri | Hospital-SWH-Office, Lobby, Clinic, OR-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0 | 0
Hospital | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | Hospital | SWH | Office, Lobby, Clinic, OR | Sat | Hospital-SWH-Office, Lobby, Clinic, OR-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0
Hospital | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | Hospital | SWH | Office, Lobby, Clinic, OR | Sun | Hospital-SWH-Office, Lobby, Clinic, OR-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | BLDG_SWH_EXTD_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Mon - Fri | Hospital-SWH-ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen-Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3
Hospital | BLDG_SWH_EXTD_SCH | Fraction | 2023-12-31 | Sat | Yes | Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Sat | Hospital-SWH-ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen-Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | BLDG_SWH_EXTD_SCH | Fraction | 2023-12-31 | Sun | Yes | Hospital | SWH | ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen | Sun | Hospital-SWH-ER, Patient Rm, ICU, Nurse Station, Dinning, Kitchen-Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Hospital | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Hospital | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Hospital | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
Hospital | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Hospital | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | INFIL_SCH_PNNL | fraction | 2023-12-31 | Mon - Fri | Yes | Hospital | Infiltration | All | Mon - Fri | Hospital-Infiltration-All-Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sat | Yes | Hospital | Infiltration | All | Sat | Hospital-Infiltration-All-Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sun | Yes | Hospital | Infiltration | All | Sun | Hospital-Infiltration-All-Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Hospital | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | HTGSETP_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | Hospital | Heating Set Point | All | Mon - Fri | Hospital-Heating Set Point-All-Mon - Fri | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Hospital | HTGSETP_SCH | Temperature | 2023-12-31 | Sat | Yes | Hospital | Heating Set Point | All | Sat | Hospital-Heating Set Point-All-Sat | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Hospital | HTGSETP_SCH | Temperature | 2023-12-31 | Sun | Yes | Hospital | Heating Set Point | All | Sun | Hospital-Heating Set Point-All-Sun | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Hospital | CLGSETP_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | Hospital | Cooling Set Point | All | Mon - Fri | Hospital-Cooling Set Point-All-Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | CLGSETP_SCH | Temperature | 2023-12-31 | Sat | Yes | Hospital | Cooling Set Point | All | Sat | Hospital-Cooling Set Point-All-Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | CLGSETP_SCH | Temperature | 2023-12-31 | Sun | Yes | Hospital | Cooling Set Point | All | Sun | Hospital-Cooling Set Point-All-Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
Hospital | Humidity Setpoint Schedule | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Hospital | Humidity Setpoint Schedule | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Hospital | Humidity Setpoint Schedule | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
Hospital | MinOA_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | MinOA_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | MinOA_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | BLDG_OA_FRAC_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | BLDG_OA_FRAC_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | BLDG_OA_FRAC_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | VAV_ER_OAminOAFracSchedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_ER_OAminOAFracSchedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_ER_OAminOAFracSchedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_OR_OAminOAFracSchedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_OR_OAminOAFracSchedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_OR_OAminOAFracSchedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_ICU_OAminOAFracSchedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_ICU_OAminOAFracSchedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_ICU_OAminOAFracSchedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_PATRMS_OAminOAFracSchedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_PATRMS_OAminOAFracSchedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_PATRMS_OAminOAFracSchedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
Hospital | VAV_LABS_OAminOAFracSchedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | VAV_LABS_OAminOAFracSchedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | VAV_LABS_OAminOAFracSchedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Hospital | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Hospital | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Hospital | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | Heat-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | Heat-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | Heat-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
Hospital | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
Hospital | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
Hospital | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
Hospital | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
Hospital | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Exam1_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Exam1_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Exam1_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Exam1_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Trauma1_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Trauma1_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Trauma1_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Trauma1_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Trauma1_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Trauma1_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Trauma1_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Trauma1_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Trauma1_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Trauma1_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Trauma1_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Trauma1_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Exam3_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Exam3_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Exam3_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Exam3_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Trauma2_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Trauma2_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Trauma2_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Trauma2_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Trauma2_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Trauma2_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Trauma2_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Trauma2_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Trauma2_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Trauma2_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Trauma2_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Trauma2_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Triage_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Triage_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Triage_Mult4_Flr_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | ER_Triage_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Triage_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Triage_Mult4_Flr_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | ER_Triage_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Triage_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Triage_Mult4_Flr_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | ER_Triage_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Triage_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | ER_Triage_Mult4_Flr_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR1_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR1_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR1_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR1_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR1_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR1_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR1_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR1_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR1_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR1_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR1_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR1_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR2_Mult5_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR2_Mult5_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR2_Mult5_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR2_Mult5_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR2_Mult5_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR2_Mult5_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR2_Mult5_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR2_Mult5_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR2_Mult5_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR2_Mult5_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR2_Mult5_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR2_Mult5_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR3_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR3_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR3_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR3_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR3_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR3_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR3_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR3_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR3_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR3_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR3_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR3_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR4_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR4_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR4_Flr_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | OR4_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR4_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR4_Flr_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | OR4_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR4_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR4_Flr_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | OR4_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR4_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | OR4_Flr_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom1_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom1_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom1_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom1_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom1_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom1_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom1_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom1_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom1_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom1_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom1_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom1_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom2_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom2_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom2_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom2_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom2_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom2_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom2_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom2_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom2_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom2_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom2_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom2_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom3_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom3_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom3_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom3_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom3_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom3_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom3_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom3_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom3_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom3_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom3_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom3_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom4_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom4_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom4_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom4_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom4_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom4_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom4_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom4_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom4_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom4_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom4_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom4_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom5_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom5_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom5_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom5_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom5_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom5_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom5_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom5_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom5_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom5_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom5_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom5_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PhysTherapy_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PhysTherapy_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PhysTherapy_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PhysTherapy_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PhysTherapy_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PhysTherapy_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PhysTherapy_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PhysTherapy_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PhysTherapy_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PhysTherapy_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PhysTherapy_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PhysTherapy_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom6_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom6_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom6_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom6_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom6_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom6_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom6_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom6_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom6_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom6_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom6_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom6_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom7_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom7_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom7_Mult10_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom7_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom7_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom7_Mult10_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom7_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom7_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom7_Mult10_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom7_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom7_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom7_Mult10_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom8_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom8_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom8_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom8_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom8_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom8_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom8_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom8_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom8_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom8_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom8_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom8_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Lab_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Lab_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Lab_Flr_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Lab_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Lab_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Lab_Flr_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Lab_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Lab_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Lab_Flr_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Lab_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Lab_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Lab_Flr_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom1_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom1_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom1_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom1_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom1_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom1_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom1_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom1_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom1_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom1_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom1_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom1_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom2_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom2_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom2_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom2_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom2_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom2_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom2_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom2_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom2_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom2_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom2_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom2_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom3_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom3_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom3_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom3_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom3_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom3_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom3_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom3_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom3_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom3_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom3_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom3_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom4_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom4_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom4_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom4_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom4_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom4_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom4_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom4_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom4_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom4_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom4_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom4_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom5_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom5_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom5_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom5_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom5_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom5_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom5_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom5_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom5_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom5_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom5_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom5_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Radiology_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Radiology_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Radiology_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Radiology_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Radiology_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Radiology_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Radiology_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Radiology_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Radiology_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Radiology_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Radiology_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Radiology_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom6_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom6_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom6_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom6_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom6_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom6_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom6_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom6_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom6_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom6_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom6_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom6_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom7_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom7_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom7_Mult10_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom7_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom7_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom7_Mult10_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom7_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom7_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom7_Mult10_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom7_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom7_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom7_Mult10_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom8_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom8_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom8_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | PatRoom8_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom8_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom8_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | PatRoom8_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom8_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom8_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | PatRoom8_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom8_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | PatRoom8_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Lab_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Lab_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Lab_Flr_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Lab_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Lab_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Lab_Flr_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Lab_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Lab_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Lab_Flr_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Lab_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Lab_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Lab_Flr_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Kitchen_Flr_5 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Kitchen_Flr_5 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Kitchen_Flr_5 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
Hospital | Kitchen_Flr_5 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Kitchen_Flr_5 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Kitchen_Flr_5 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Hospital | Kitchen_Flr_5 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Kitchen_Flr_5 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Kitchen_Flr_5 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Kitchen_Flr_5 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Kitchen_Flr_5 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Kitchen_Flr_5 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | TuesdayFriday | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
Hospital | Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
Hospital | Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Hospital | Tower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
Hospital | Tower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
Hospital | Tower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
Hospital | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | VAV_SAT_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | VAV_SAT_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | VAV_SAT_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
Hospital | MinRelHumSetSch | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Hospital | MinRelHumSetSch | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Hospital | MinRelHumSetSch | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
Hospital | MinRelHumSetSch_addDI | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Hospital | MinRelHumSetSch_addDI | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Hospital | MinRelHumSetSch_addDI | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Hospital | MinRelHumSetSch_addDI_ICU | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Hospital | MinRelHumSetSch_addDI_ICU | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Hospital | MinRelHumSetSch_addDI_ICU | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
Hospital | MaxRelHumSetSch | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | MaxRelHumSetSch | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | MaxRelHumSetSch | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Hospital | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Hospital | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | ltg_sch_kitchen | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Lighting | Others | Mon - Fri | HotelLarge-Lighting-Others-Mon - Fri | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_kitchen | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Lighting | Others | Sat | HotelLarge-Lighting-Others-Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_kitchen | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Lighting | Others | Sun | HotelLarge-Lighting-Others-Sun | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | ltg_sch_dining | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_dining | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_dining | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | ltg_sch_basement | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_basement | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_basement | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | ltg_sch_lobby | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_lobby | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_lobby | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | ltg_sch_storage | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_storage | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_storage | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | ltg_sch_mechanic | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_mechanic | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_mechanic | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | ltg_sch_laundry | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_laundry | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_laundry | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | ltg_sch_guestroom | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Lighting | Guest Rooms | Mon - Fri | HotelLarge-Lighting-Guest Rooms-Mon - Fri | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
HotelLarge | ltg_sch_guestroom | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Lighting | Guest Rooms | Sat | HotelLarge-Lighting-Guest Rooms-Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelLarge | ltg_sch_guestroom | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Lighting | Guest Rooms | Sun | HotelLarge-Lighting-Guest Rooms-Sun | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelLarge | ltg_sch_corridor | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_corridor | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_corridor | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | ltg_sch_retail | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | ltg_sch_retail | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | ltg_sch_retail | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_kitchen) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3
HotelLarge | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3
HotelLarge | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3
HotelLarge | BASEMENT_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as BLDG_EQUIP_SCH) |  |  |  |  | --- | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
HotelLarge | BASEMENT_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No (the same as BLDG_EQUIP_SCH) |  |  |  |  | --- | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
HotelLarge | BASEMENT_EQUIP_SCH | Fraction | 2023-12-31 | Sun | No (the same as BLDG_EQUIP_SCH) |  |  |  |  | --- | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
HotelLarge | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Electric Equipment | Others | Mon - Fri | HotelLarge-Electric Equipment-Others-Mon - Fri | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4
HotelLarge | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Electric Equipment | Others | Sat | HotelLarge-Electric Equipment-Others-Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4
HotelLarge | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Electric Equipment | Others | Sun | HotelLarge-Electric Equipment-Others-Sun | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4
HotelLarge | GuestRoom_Eqp_Sch_Base | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Electric Equipment | Guest Rooms | Mon - Fri | HotelLarge-Electric Equipment-Guest Rooms-Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | GuestRoom_Eqp_Sch_Base | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Electric Equipment | Guest Rooms | Sat | HotelLarge-Electric Equipment-Guest Rooms-Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | GuestRoom_Eqp_Sch_Base | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Electric Equipment | Guest Rooms | Sun | HotelLarge-Electric Equipment-Guest Rooms-Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.2
HotelLarge | Kitchen_Elec_Equip_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Mon - Fri | HotelLarge-Electric Equipment-Kitchen, Dining, Banquet-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Kitchen_Elec_Equip_SCH | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Sat | HotelLarge-Electric Equipment-Kitchen, Dining, Banquet-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Kitchen_Elec_Equip_SCH | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Electric Equipment | Kitchen, Dining, Banquet | Sun | HotelLarge-Electric Equipment-Kitchen, Dining, Banquet-Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
HotelLarge | Kitchen_Gas_Equip_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Gas Equipment | Kitchen | Mon - Fri | HotelLarge-Gas Equipment-Kitchen-Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | Kitchen_Gas_Equip_SCH | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Gas Equipment | Kitchen | Sat | HotelLarge-Gas Equipment-Kitchen-Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | Kitchen_Gas_Equip_SCH | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Gas Equipment | Kitchen | Sun | HotelLarge-Gas Equipment-Kitchen-Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05
HotelLarge | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Elevator | All | Mon - Fri | HotelLarge-Elevator-All-Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Elevator | All | Sat | HotelLarge-Elevator-All-Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Elevator | All | Sun | HotelLarge-Elevator-All-Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelLarge | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Occupants | Others | Mon - Fri | HotelLarge-Occupants-Others-Mon - Fri | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9
HotelLarge | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Occupants | Others | Sat | HotelLarge-Occupants-Others-Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7
HotelLarge | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Occupants | Others | Sun | HotelLarge-Occupants-Others-Sun | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8
HotelLarge | GuestRoom_Occ_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Occupants | Guest Rooms | Mon - Fri | HotelLarge-Occupants-Guest Rooms-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1
HotelLarge | GuestRoom_Occ_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Occupants | Guest Rooms | Sat | HotelLarge-Occupants-Guest Rooms-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelLarge | GuestRoom_Occ_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Occupants | Guest Rooms | Sun | HotelLarge-Occupants-Guest Rooms-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelLarge | INFIL_QUARTER_ON_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Infiltration | All | Mon - Fri | HotelLarge-Infiltration-All-Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | INFIL_QUARTER_ON_SCH | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | Infiltration | All | Sat | HotelLarge-Infiltration-All-Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | INFIL_QUARTER_ON_SCH | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | Infiltration | All | Sun | HotelLarge-Infiltration-All-Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelLarge | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelLarge | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelLarge | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelLarge | Laundry Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelLarge | Laundry Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelLarge | Laundry Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelLarge | LAUNDRY_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | LAUNDRY_SWH_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | LAUNDRY_SWH_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | SWH | Kitchen | Mon - Fri | HotelLarge-SWH-Kitchen-Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
HotelLarge | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | SWH | Kitchen | Sat | HotelLarge-SWH-Kitchen-Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
HotelLarge | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | SWH | Kitchen | Sun | HotelLarge-SWH-Kitchen-Sun | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
HotelLarge | GuestRoom_SWH_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelLarge | SWH | Guest Rooms | Mon - Fri | HotelLarge-SWH-Guest Rooms-Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
HotelLarge | GuestRoom_SWH_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelLarge | SWH | Guest Rooms | Sat | HotelLarge-SWH-Guest Rooms-Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelLarge | GuestRoom_SWH_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelLarge | SWH | Guest Rooms | Sun | HotelLarge-SWH-Guest Rooms-Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelLarge | Hours_of_operation | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Hours_of_operation | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Hours_of_operation | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | ALWAYS_OFF | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | ALWAYS_OFF | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | ALWAYS_OFF | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | HVACOperationSchd | On/Off | 2023-12-31 | Mon - Fri | Yes | HotelLarge | HVAC | All | Mon - Fri | HotelLarge-HVAC-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | HVACOperationSchd | On/Off | 2023-12-31 | Sat | Yes | HotelLarge | HVAC | All | Sat | HotelLarge-HVAC-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | HVACOperationSchd | On/Off | 2023-12-31 | Sun | Yes | HotelLarge | HVAC | All | Sun | HotelLarge-HVAC-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | FAN_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | FAN_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | FAN_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | HTGSETP_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Heating Set Point | Common Areas | Mon - Fri | HotelLarge-Heating Set Point-Common Areas-Mon - Fri | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelLarge | HTGSETP_SCH | Temperature | 2023-12-31 | Sat | Yes | HotelLarge | Heating Set Point | Common Areas | Sat | HotelLarge-Heating Set Point-Common Areas-Sat | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelLarge | HTGSETP_SCH | Temperature | 2023-12-31 | Sun | Yes | HotelLarge | Heating Set Point | Common Areas | Sun | HotelLarge-Heating Set Point-Common Areas-Sun | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
HotelLarge | CLGSETP_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Cooling Set Point | Common Areas | Mon - Fri | HotelLarge-Cooling Set Point-Common Areas-Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | CLGSETP_SCH | Temperature | 2023-12-31 | Sat | Yes | HotelLarge | Cooling Set Point | Common Areas | Sat | HotelLarge-Cooling Set Point-Common Areas-Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | CLGSETP_SCH | Temperature | 2023-12-31 | Sun | Yes | HotelLarge | Cooling Set Point | Common Areas | Sun | HotelLarge-Cooling Set Point-Common Areas-Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
HotelLarge | VacGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889
HotelLarge | VacGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889
HotelLarge | VacGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889
HotelLarge | VacGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333
HotelLarge | VacGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333
HotelLarge | VacGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333
HotelLarge | Base_S_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Heating Set Point | Guest Rooms | Mon - Fri | HotelLarge-Heating Set Point-Guest Rooms-Mon - Fri | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_S_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sat | Yes | HotelLarge | Heating Set Point | Guest Rooms | Sat | HotelLarge-Heating Set Point-Guest Rooms-Sat | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_S_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sun | Yes | HotelLarge | Heating Set Point | Guest Rooms | Sun | HotelLarge-Heating Set Point-Guest Rooms-Sun | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_S_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | Yes | HotelLarge | Cooling Set Point | Guest Rooms | Mon - Fri | HotelLarge-Cooling Set Point-Guest Rooms-Mon - Fri | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_S_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sat | Yes | HotelLarge | Cooling Set Point | Guest Rooms | Sat | HotelLarge-Cooling Set Point-Guest Rooms-Sat | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_S_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sun | Yes | HotelLarge | Cooling Set Point | Guest Rooms | Sun | HotelLarge-Cooling Set Point-Guest Rooms-Sun | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_N_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No (the same as Base_S_OccGuestRoom_HtgSP_Sch) |  |  |  |  | --- | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_N_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sat | No (the same as Base_S_OccGuestRoom_HtgSP_Sch) |  |  |  |  | --- | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_N_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sun | No (the same as Base_S_OccGuestRoom_HtgSP_Sch) |  |  |  |  | --- | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_N_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No (the same as Base_S_OccGuestRoom_ClgSP_Sch) |  |  |  |  | --- | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_N_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sat | No (the same as Base_S_OccGuestRoom_ClgSP_Sch) |  |  |  |  | --- | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | Base_N_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sun | No (the same as Base_S_OccGuestRoom_ClgSP_Sch) |  |  |  |  | --- | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
HotelLarge | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | MinOA_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | MinOA_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | MinOA_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
HotelLarge | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
HotelLarge | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
HotelLarge | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
HotelLarge | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
HotelLarge | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
HotelLarge | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
HotelLarge | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
HotelLarge | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
HotelLarge | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
HotelLarge | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
HotelLarge | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
HotelLarge | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelLarge | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelLarge | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelLarge | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | Room_1_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_1_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_1_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_1_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_1_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_1_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_1_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_1_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_1_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_1_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_2_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_2_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_2_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_2_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_2_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_2_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_2_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_2_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_2_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_3_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_4_Mult19_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_5_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_5_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_5_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_5_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_5_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_5_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_5_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_5_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_5_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_5_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_6_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_6_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_6_Flr_3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_6_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_6_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_6_Flr_3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_6_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_6_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_6_Flr_3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_1_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_1_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_1_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_1_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_1_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_1_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_1_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_1_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_1_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_1_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_2_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_2_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_2_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_2_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_2_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_2_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_2_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_2_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_2_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_2_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Room_3_Mult9_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Kitchen_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Kitchen_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Kitchen_Flr_6 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelLarge | Kitchen_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Kitchen_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Kitchen_Flr_6 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelLarge | Kitchen_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Kitchen_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Kitchen_Flr_6 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Kitchen_Flr_6 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | TuesdayFriday | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
HotelLarge | Kitchen_Flr_6_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
HotelLarge | Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | FLR_3_DOAS_OAminOAFracSchedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | FLR_3_DOAS_OAminOAFracSchedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | FLR_3_DOAS_OAminOAFracSchedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelLarge | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelLarge | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Laundry_Flr_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Laundry_Flr_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Laundry_Flr_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelLarge | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
HotelLarge | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
HotelLarge | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
HotelSmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | AlwaysOn | On/Off | 2023-12-31 | Mon - Fri | Yes | HotelSmall | HVAC | All | Mon - Fri | HotelSmall-HVAC-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | AlwaysOn | On/Off | 2023-12-31 | Sat | Yes | HotelSmall | HVAC | All | Sat | HotelSmall-HVAC-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | AlwaysOn | On/Off | 2023-12-31 | Sun | Yes | HotelSmall | HVAC | All | Sun | HotelSmall-HVAC-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | AlwaysOff | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | AlwaysOff | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | AlwaysOff | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | COMPACT HVAC-ALWAYS 4 | COMPACT HVAC Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
HotelSmall | COMPACT HVAC-ALWAYS 4 | COMPACT HVAC Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
HotelSmall | COMPACT HVAC-ALWAYS 4 | COMPACT HVAC Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
HotelSmall | GuestRoom_Occ_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Occupants | Guest Rooms | Mon - Fri | HotelSmall-Occupants-Guest Rooms-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1
HotelSmall | GuestRoom_Occ_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Occupants | Guest Rooms | Sat | HotelSmall-Occupants-Guest Rooms-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelSmall | GuestRoom_Occ_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Occupants | Guest Rooms | Sun | HotelSmall-Occupants-Guest Rooms-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77
HotelSmall | Lobby_Occ_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Occupants | Front Lounge, Restroom | Mon - Fri | HotelSmall-Occupants-Front Lounge, Restroom-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Lobby_Occ_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Occupants | Front Lounge, Restroom | Sat | HotelSmall-Occupants-Front Lounge, Restroom-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Lobby_Occ_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Occupants | Front Lounge, Restroom | Sun | HotelSmall-Occupants-Front Lounge, Restroom-Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1
HotelSmall | Office_Occ_w_SB_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Occupants | Office | Mon - Fri | HotelSmall-Occupants-Office-Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0 | 1 | 0 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | Office_Occ_w_SB_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Occupants | Office | Sat | HotelSmall-Occupants-Office-Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | Office_Occ_w_SB_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Occupants | Office | Sun | HotelSmall-Occupants-Office-Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | EmployeeLounge_Occ_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Occupants | Employee Lounge | Mon - Fri | HotelSmall-Occupants-Employee Lounge-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0
HotelSmall | EmployeeLounge_Occ_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Occupants | Employee Lounge | Sat | HotelSmall-Occupants-Employee Lounge-Sat | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | EmployeeLounge_Occ_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Occupants | Employee Lounge | Sun | HotelSmall-Occupants-Employee Lounge-Sun | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | MeetingRoom_Occ_w_SB_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Occupants | Meeting Room | Mon - Fri | HotelSmall-Occupants-Meeting Room-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0 | 0 | 0.05 | 0.5 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | MeetingRoom_Occ_w_SB_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Occupants | Meeting Room | Sat | HotelSmall-Occupants-Meeting Room-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | MeetingRoom_Occ_w_SB_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Occupants | Meeting Room | Sun | HotelSmall-Occupants-Meeting Room-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_Occ_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Occupants | Laundry Room | Mon - Fri | HotelSmall-Occupants-Laundry Room-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_Occ_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Occupants | Laundry Room | Sat | HotelSmall-Occupants-Laundry Room-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_Occ_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Occupants | Laundry Room | Sun | HotelSmall-Occupants-Laundry Room-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | ExerciseCenter_Occ_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Occupants | Exercise Center | Mon - Fri | HotelSmall-Occupants-Exercise Center-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | ExerciseCenter_Occ_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Occupants | Exercise Center | Sat | HotelSmall-Occupants-Exercise Center-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | ExerciseCenter_Occ_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Occupants | Exercise Center | Sun | HotelSmall-Occupants-Exercise Center-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Lighting | Office | Mon - Fri | HotelSmall-Lighting-Office-Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | ltg_sch_office | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Lighting | Office | Sat | HotelSmall-Lighting-Office-Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | ltg_sch_office | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Lighting | Office | Sun | HotelSmall-Lighting-Office-Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
HotelSmall | ltg_sch_lobby | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Mon - Fri | HotelSmall-Lighting-Meeting Room, Employee Lounge, Front Lounge-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_lobby | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Sat | HotelSmall-Lighting-Meeting Room, Employee Lounge, Front Lounge-Sat | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_lobby | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Lighting | Meeting Room, Employee Lounge, Front Lounge | Sun | HotelSmall-Lighting-Meeting Room, Employee Lounge, Front Lounge-Sun | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_mechanical | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Lighting | Storage, Mechanical room | Mon - Fri | HotelSmall-Lighting-Storage, Mechanical room-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | ltg_sch_mechanical | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Lighting | Storage, Mechanical room | Sat | HotelSmall-Lighting-Storage, Mechanical room-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | ltg_sch_mechanical | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Lighting | Storage, Mechanical room | Sun | HotelSmall-Lighting-Storage, Mechanical room-Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | ltg_sch_storage | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_mechanical) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | ltg_sch_storage | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_mechanical) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | ltg_sch_storage | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_mechanical) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1
HotelSmall | ltg_sch_meeting | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_lobby) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_meeting | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_lobby) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_meeting | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_lobby) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_guestroom | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Lighting | Guest Rooms | Mon - Fri | HotelSmall-Lighting-Guest Rooms-Mon - Fri | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33
HotelSmall | ltg_sch_guestroom | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Lighting | Guest Rooms | Sat | HotelSmall-Lighting-Guest Rooms-Sat | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelSmall | ltg_sch_guestroom | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Lighting | Guest Rooms | Sun | HotelSmall-Lighting-Guest Rooms-Sun | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41
HotelSmall | ltg_sch_exercise | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Lighting | Exercise Center | Mon - Fri | HotelSmall-Lighting-Exercise Center-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | ltg_sch_exercise | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Lighting | Exercise Center | Sat | HotelSmall-Lighting-Exercise Center-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | ltg_sch_exercise | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Lighting | Exercise Center | Sun | HotelSmall-Lighting-Exercise Center-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0
HotelSmall | ltg_sch_stair | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Lighting | Corridors, Stairs, Restroom | Mon - Fri | HotelSmall-Lighting-Corridors, Stairs, Restroom-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ltg_sch_stair | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Lighting | Corridors, Stairs, Restroom | Sat | HotelSmall-Lighting-Corridors, Stairs, Restroom-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ltg_sch_stair | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Lighting | Corridors, Stairs, Restroom | Sun | HotelSmall-Lighting-Corridors, Stairs, Restroom-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ltg_sch_elevator | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | ltg_sch_elevator | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | ltg_sch_elevator | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | ltg_sch_laundry | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Lighting | Laundry Room | Mon - Fri | HotelSmall-Lighting-Laundry Room-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | ltg_sch_laundry | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Lighting | Laundry Room | Sat | HotelSmall-Lighting-Laundry Room-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | ltg_sch_laundry | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Lighting | Laundry Room | Sun | HotelSmall-Lighting-Laundry Room-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | ltg_sch_lounge | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_lobby) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_lounge | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_lobby) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_lounge | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_lobby) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0
HotelSmall | ltg_sch_corridor | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_stair) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ltg_sch_corridor | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_stair) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ltg_sch_corridor | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_stair) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ltg_sch_restroom | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_stair) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ltg_sch_restroom | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_stair) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ltg_sch_restroom | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_stair) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | GuestRoom_Eqp_Sch_Base | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Electric Equipment | Guest Rooms | Mon - Fri | HotelSmall-Electric Equipment-Guest Rooms-Mon - Fri | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | GuestRoom_Eqp_Sch_Base | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Electric Equipment | Guest Rooms | Sat | HotelSmall-Electric Equipment-Guest Rooms-Sat | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | GuestRoom_Eqp_Sch_Base | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Electric Equipment | Guest Rooms | Sun | HotelSmall-Electric Equipment-Guest Rooms-Sun | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11
HotelSmall | Lobby_Eqp_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Electric Equipment | Front Lounge | Mon - Fri | HotelSmall-Electric Equipment-Front Lounge-Mon - Fri | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | Lobby_Eqp_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Electric Equipment | Front Lounge | Sat | HotelSmall-Electric Equipment-Front Lounge-Sat | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | Lobby_Eqp_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Electric Equipment | Front Lounge | Sun | HotelSmall-Electric Equipment-Front Lounge-Sun | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21
HotelSmall | OFF_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Electric Equipment | Office | Mon - Fri | HotelSmall-Electric Equipment-Office-Mon - Fri | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | OFF_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Electric Equipment | Office | Sat | HotelSmall-Electric Equipment-Office-Sat | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | OFF_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Electric Equipment | Office | Sun | HotelSmall-Electric Equipment-Office-Sun | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33
HotelSmall | EmployeeLounge_Eqp_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Electric Equipment | Employee Lounge | Mon - Fri | HotelSmall-Electric Equipment-Employee Lounge-Mon - Fri | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | EmployeeLounge_Eqp_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Electric Equipment | Employee Lounge | Sat | HotelSmall-Electric Equipment-Employee Lounge-Sat | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | EmployeeLounge_Eqp_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Electric Equipment | Employee Lounge | Sun | HotelSmall-Electric Equipment-Employee Lounge-Sun | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11
HotelSmall | LaundryRoom_Eqp_Elec_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Electric Equipment | Laundry Room | Mon - Fri | HotelSmall-Electric Equipment-Laundry Room-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_Eqp_Elec_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Electric Equipment | Laundry Room | Sat | HotelSmall-Electric Equipment-Laundry Room-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_Eqp_Elec_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Electric Equipment | Laundry Room | Sun | HotelSmall-Electric Equipment-Laundry Room-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_Eqp_Gas_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Gas Equipment | Laundry Room | Mon - Fri | HotelSmall-Gas Equipment-Laundry Room-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_Eqp_Gas_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Gas Equipment | Laundry Room | Sat | HotelSmall-Gas Equipment-Laundry Room-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_Eqp_Gas_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Gas Equipment | Laundry Room | Sun | HotelSmall-Gas Equipment-Laundry Room-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | MeetingRoom_Eqp_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Electric Equipment | Meeting Room | Mon - Fri | HotelSmall-Electric Equipment-Meeting Room-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | MeetingRoom_Eqp_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Electric Equipment | Meeting Room | Sat | HotelSmall-Electric Equipment-Meeting Room-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | MeetingRoom_Eqp_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Electric Equipment | Meeting Room | Sun | HotelSmall-Electric Equipment-Meeting Room-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0
HotelSmall | ExerciseCenter_Eqp_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Electric Equipment | Exercise Center | Mon - Fri | HotelSmall-Electric Equipment-Exercise Center-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | ExerciseCenter_Eqp_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Electric Equipment | Exercise Center | Sat | HotelSmall-Electric Equipment-Exercise Center-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | ExerciseCenter_Eqp_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Electric Equipment | Exercise Center | Sun | HotelSmall-Electric Equipment-Exercise Center-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0
HotelSmall | SemiHeated_HtgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
HotelSmall | SemiHeated_HtgSP_Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
HotelSmall | SemiHeated_HtgSP_Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
HotelSmall | VacGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889
HotelSmall | VacGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889
HotelSmall | VacGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889 | 18.889
HotelSmall | VacGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333
HotelSmall | VacGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333
HotelSmall | VacGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333 | 23.333
HotelSmall | Base_S_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Heating Set Point | Guest Rooms | Mon - Fri | HotelSmall-Heating Set Point-Guest Rooms-Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_S_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sat | Yes | HotelSmall | Heating Set Point | Guest Rooms | Sat | HotelSmall-Heating Set Point-Guest Rooms-Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_S_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sun | Yes | HotelSmall | Heating Set Point | Guest Rooms | Sun | HotelSmall-Heating Set Point-Guest Rooms-Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_S_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Cooling Set Point | Guest Rooms | Mon - Fri | HotelSmall-Cooling Set Point-Guest Rooms-Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_S_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sat | Yes | HotelSmall | Cooling Set Point | Guest Rooms | Sat | HotelSmall-Cooling Set Point-Guest Rooms-Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_S_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sun | Yes | HotelSmall | Cooling Set Point | Guest Rooms | Sun | HotelSmall-Cooling Set Point-Guest Rooms-Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_N_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No (the same as Base_S_OccGuestRoom_HtgSP_Sch) |  |  |  |  | --- | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_N_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sat | No (the same as Base_S_OccGuestRoom_HtgSP_Sch) |  |  |  |  | --- | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_N_OccGuestRoom_HtgSP_Sch | Temperature | 2023-12-31 | Sun | No (the same as Base_S_OccGuestRoom_HtgSP_Sch) |  |  |  |  | --- | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_N_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | No (the same as Base_S_OccGuestRoom_ClgSP_Sch) |  |  |  |  | --- | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_N_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sat | No (the same as Base_S_OccGuestRoom_ClgSP_Sch) |  |  |  |  | --- | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | Base_N_OccGuestRoom_ClgSP_Sch | Temperature | 2023-12-31 | Sun | No (the same as Base_S_OccGuestRoom_ClgSP_Sch) |  |  |  |  | --- | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | CommonArea_HtgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Heating Set Point | Common Area | Mon - Fri | HotelSmall-Heating Set Point-Common Area-Mon - Fri | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | CommonArea_HtgSP_Sch | Temperature | 2023-12-31 | Sat | Yes | HotelSmall | Heating Set Point | Common Area | Sat | HotelSmall-Heating Set Point-Common Area-Sat | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | CommonArea_HtgSP_Sch | Temperature | 2023-12-31 | Sun | Yes | HotelSmall | Heating Set Point | Common Area | Sun | HotelSmall-Heating Set Point-Common Area-Sun | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111 | 21.111
HotelSmall | CommonArea_ClgSP_Sch | Temperature | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Cooling Set Point | Common Area | Mon - Fri | HotelSmall-Cooling Set Point-Common Area-Mon - Fri | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | CommonArea_ClgSP_Sch | Temperature | 2023-12-31 | Sat | Yes | HotelSmall | Cooling Set Point | Common Area | Sat | HotelSmall-Cooling Set Point-Common Area-Sat | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | CommonArea_ClgSP_Sch | Temperature | 2023-12-31 | Sun | Yes | HotelSmall | Cooling Set Point | Common Area | Sun | HotelSmall-Cooling Set Point-Common Area-Sun | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889 | 23.889
HotelSmall | Off During Unoccupied Period | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Off During Unoccupied Period | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | Off During Unoccupied Period | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | GuestRoom_Infil_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Infiltration | Guest Rooms | Mon - Fri | HotelSmall-Infiltration-Guest Rooms-Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | GuestRoom_Infil_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Infiltration | Guest Rooms | Sat | HotelSmall-Infiltration-Guest Rooms-Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | GuestRoom_Infil_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Infiltration | Guest Rooms | Sun | HotelSmall-Infiltration-Guest Rooms-Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | CommonArea_Infil_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Infiltration | Common Areas | Mon - Fri | HotelSmall-Infiltration-Common Areas-Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | CommonArea_Infil_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Infiltration | Common Areas | Sat | HotelSmall-Infiltration-Common Areas-Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | CommonArea_Infil_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Infiltration | Common Areas | Sun | HotelSmall-Infiltration-Common Areas-Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
HotelSmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
HotelSmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
HotelSmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0 | 0
HotelSmall | SHWSysShower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysShower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysShower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysLaundry-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysLaundry-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysLaundry-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysShower Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysShower Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysShower Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHWSysLaundry Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelSmall | SHWSysLaundry Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelSmall | SHWSysLaundry Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelSmall | GuestRoom_SHW_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | SWH | Guest Rooms | Mon - Fri | HotelSmall-SWH-Guest Rooms-Mon - Fri | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25
HotelSmall | GuestRoom_SHW_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | SWH | Guest Rooms | Sat | HotelSmall-SWH-Guest Rooms-Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelSmall | GuestRoom_SHW_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | SWH | Guest Rooms | Sun | HotelSmall-SWH-Guest Rooms-Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35
HotelSmall | LaundryRoom_SHW_Sch | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | SWH | Laundry Room | Mon - Fri | HotelSmall-SWH-Laundry Room-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_SHW_Sch | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | SWH | Laundry Room | Sat | HotelSmall-SWH-Laundry Room-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | LaundryRoom_SHW_Sch | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | SWH | Laundry Room | Sun | HotelSmall-SWH-Laundry Room-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HotelSmall | SHW Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelSmall | SHW Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelSmall | SHW Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
HotelSmall | SHW Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | SHW Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | SHW Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
HotelSmall | SHW Shower Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHW Shower Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHW Shower Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HotelSmall | SHW Laundry Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelSmall | SHW Laundry Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelSmall | SHW Laundry Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
HotelSmall | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | Activity_Sch | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
HotelSmall | Activity_Sch | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
HotelSmall | Activity_Sch | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
HotelSmall | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | HotelSmall | Elevator | All | Mon - Fri | HotelSmall-Elevator-All-Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | HotelSmall | Elevator | All | Sat | HotelSmall-Elevator-All-Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | HotelSmall | Elevator | All | Sun | HotelSmall-Elevator-All-Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
HotelSmall | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HotelSmall | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
HotelSmall | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
HotelSmall | Sliding_Doors_Ventilation_Availability_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeLarge | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | HVACOperationSchd | on/off | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | HVAC | All | Mon - Fri | OfficeLarge-HVAC-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeLarge | HVACOperationSchd | on/off | 2023-12-31 | Sat | Yes | OfficeLarge | HVAC | All | Sat | OfficeLarge-HVAC-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | HVACOperationSchd | on/off | 2023-12-31 | Sun | Yes | OfficeLarge | HVAC | All | Sun | OfficeLarge-HVAC-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | Lighting | All (Except Data Center) | Mon - Fri | OfficeLarge-Lighting-All (Except Data Center)-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OfficeLarge | ltg_sch_office | Fraction | 2023-12-31 | Sat | Yes | OfficeLarge | Lighting | All (Except Data Center) | Sat | OfficeLarge-Lighting-All (Except Data Center)-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | ltg_sch_office | Fraction | 2023-12-31 | Sun | Yes | OfficeLarge | Lighting | All (Except Data Center) | Sun | OfficeLarge-Lighting-All (Except Data Center)-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | ltg_sch_datacenter | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OfficeLarge | ltg_sch_datacenter | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | ltg_sch_datacenter | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Mon - Fri | OfficeLarge-Electric Equipment-All (Except Basement and Data Center)-Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
OfficeLarge | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Sat | OfficeLarge-Electric Equipment-All (Except Basement and Data Center)-Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeLarge | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | OfficeLarge | Electric Equipment | All (Except Basement and Data Center) | Sun | OfficeLarge-Electric Equipment-All (Except Basement and Data Center)-Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-01-31 | Mon - Fri | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-01-31 | Sat | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-01-31 | Sun | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-02-28 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-02-28 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-02-28 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-03-31 | Mon - Fri | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-03-31 | Sat | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-03-31 | Sun | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-05-31 | Mon - Fri | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-05-31 | Sat | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-05-31 | Sun | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-07-31 | Mon - Fri | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-07-31 | Sat | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-07-31 | Sun | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-08-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-08-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-08-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-10-31 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-10-31 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-10-31 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-11-30 | Mon - Fri | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-11-30 | Sat | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-11-30 | Sun | No |  |  |  |  | --- | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DataCenter_EQUIP_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeLarge | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeLarge | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeLarge | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0 | 0.3 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeLarge | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | OfficeLarge-Occupants-All (Except Perimeter_mid_ZN_2)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.99331 | 0.95 | 0.5228 | 0.95 | 0.99331 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeLarge | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Sat | Yes | OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | OfficeLarge-Occupants-All (Except Perimeter_mid_ZN_2)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.31368 | 0.3 | 0.10456 | 0.1 | 0.10456 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeLarge | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Sun | Yes | OfficeLarge | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | OfficeLarge-Occupants-All (Except Perimeter_mid_ZN_2)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | Elevator | All | Mon - Fri | OfficeLarge-Elevator-All-Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | OfficeLarge | Elevator | All | Sat | OfficeLarge-Elevator-All-Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | OfficeLarge | Elevator | All | Sun | OfficeLarge-Elevator-All-Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.12
OfficeLarge | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | SWH | All | Mon - Fri | OfficeLarge-SWH-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeLarge | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | OfficeLarge | SWH | All | Sat | OfficeLarge-SWH-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05
OfficeLarge | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | OfficeLarge | SWH | All | Sun | OfficeLarge-SWH-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04
OfficeLarge | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeLarge | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeLarge | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeLarge | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeLarge | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | INFIL_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
OfficeLarge | INFIL_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | INFIL_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | INFIL_SCH_PNNL | fraction | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | Infiltration | All | Mon - Fri | OfficeLarge-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeLarge | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sat | Yes | OfficeLarge | Infiltration | All | Sat | OfficeLarge-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sun | Yes | OfficeLarge | Infiltration | All | Sun | OfficeLarge-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | FAN_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | FAN_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | FAN_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Mon - Fri | OfficeLarge-Heating Set Point-All (Except Basement and Data Center)-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Sat | OfficeLarge-Heating Set Point-All (Except Basement and Data Center)-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | OfficeLarge | Heating Set Point | All (Except Basement and Data Center) | Sun | OfficeLarge-Heating Set Point-All (Except Basement and Data Center)-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_CAV_bas | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_CAV_bas | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | HTGSETP_SCH_CAV_bas | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | OfficeLarge | Cooling Set Point | All (Except Data Center) | Mon - Fri | OfficeLarge-Cooling Set Point-All (Except Data Center)-Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | OfficeLarge | Cooling Set Point | All (Except Data Center) | Sat | OfficeLarge-Cooling Set Point-All (Except Data Center)-Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | OfficeLarge | Cooling Set Point | All (Except Data Center) | Sun | OfficeLarge-Cooling Set Point-All (Except Data Center)-Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeLarge | CLGSETP_SCH_CAV_bas | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_CAV_bas | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | CLGSETP_SCH_CAV_bas | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeLarge | MinOA_MotorizedDamper_Sched | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeLarge | MinOA_MotorizedDamper_Sched | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | MinOA_MotorizedDamper_Sched | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeLarge | MinOA_Sched | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | MinOA_Sched | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | MinOA_Sched | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeLarge | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeLarge | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeLarge | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeLarge | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeLarge | Cool-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeLarge | Heat-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeLarge | Heat-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeLarge | Heat-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeLarge | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
OfficeLarge | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
OfficeLarge | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
OfficeLarge | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
OfficeLarge | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
OfficeLarge | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
OfficeLarge | Tower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
OfficeLarge | Tower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
OfficeLarge | Tower-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
OfficeLarge | Core_bottom sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_bottom sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_bottom sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_bottom sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_bottom sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_bottom sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_bottom sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_bottom sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_bottom sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_bottom sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | Core_bottom sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | Core_bottom sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | Core_mid sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_mid sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_mid sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_mid sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_mid sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_mid sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_mid sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_mid sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_mid sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_mid sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | Core_mid sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | Core_mid sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | Core_top sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_top sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_top sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeLarge | Core_top sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_top sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_top sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeLarge | Core_top sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_top sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_top sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | Core_top sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | Core_top sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | Core_top sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeLarge | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeLarge | CLGSETP_DC_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
OfficeLarge | CLGSETP_DC_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
OfficeLarge | CLGSETP_DC_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
OfficeLarge | HTGSETP_DC_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
OfficeLarge | HTGSETP_DC_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
OfficeLarge | HTGSETP_DC_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
OfficeLarge | PLANT LOOP HIGH TEMP SCHEDULE | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33
OfficeLarge | PLANT LOOP HIGH TEMP SCHEDULE | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33
OfficeLarge | PLANT LOOP HIGH TEMP SCHEDULE | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33 | 18.33
OfficeLarge | PLANT LOOP LOW TEMP SCHEDULE | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
OfficeLarge | PLANT LOOP LOW TEMP SCHEDULE | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
OfficeLarge | PLANT LOOP LOW TEMP SCHEDULE | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
OfficeLarge | SupplyFanSch | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | SupplyFanSch | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | SupplyFanSch | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeLarge | DC_MinRelHumSetSch | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OfficeLarge | DC_MinRelHumSetSch | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OfficeLarge | DC_MinRelHumSetSch | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OfficeMedium | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | HVACOperationSchd | on/off | 2023-12-31 | Mon - Fri | Yes | OfficeMedium | HVAC | All | Mon - Fri | OfficeMedium-HVAC-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeMedium | HVACOperationSchd | on/off | 2023-12-31 | Sat | Yes | OfficeMedium | HVAC | All | Sat | OfficeMedium-HVAC-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | HVACOperationSchd | on/off | 2023-12-31 | Sun | Yes | OfficeMedium | HVAC | All | Sun | OfficeMedium-HVAC-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeMedium | Lighting | All | Mon - Fri | OfficeMedium-Lighting-All-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05
OfficeMedium | ltg_sch_office | Fraction | 2023-12-31 | Sat | Yes | OfficeMedium | Lighting | All | Sat | OfficeMedium-Lighting-All-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | ltg_sch_office | Fraction | 2023-12-31 | Sun | Yes | OfficeMedium | Lighting | All | Sun | OfficeMedium-Lighting-All-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeMedium | Electric Equipment | All | Mon - Fri | OfficeMedium-Electric Equipment-All-Mon - Fri | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
OfficeMedium | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | OfficeMedium | Electric Equipment | All | Sat | OfficeMedium-Electric Equipment-All-Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeMedium | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | OfficeMedium | Electric Equipment | All | Sun | OfficeMedium-Electric Equipment-All-Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OfficeMedium | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeMedium | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeMedium | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeMedium | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0 | 0.3 | 0 | 0.1 | 0 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeMedium | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | OfficeMedium-Occupants-All (Except Perimeter_mid_ZN_2)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.9757 | 0.95 | 0.51353 | 0.95 | 0.9757 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
OfficeMedium | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Sat | Yes | OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | OfficeMedium-Occupants-All (Except Perimeter_mid_ZN_2)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.30812 | 0.3 | 0.10271 | 0.1 | 0.10271 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
OfficeMedium | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Sun | Yes | OfficeMedium | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | OfficeMedium-Occupants-All (Except Perimeter_mid_ZN_2)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeMedium | Elevator | All | Mon - Fri | OfficeMedium-Elevator-All-Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | OfficeMedium | Elevator | All | Sat | OfficeMedium-Elevator-All-Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | OfficeMedium | Elevator | All | Sun | OfficeMedium-Elevator-All-Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OfficeMedium | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeMedium | SWH | All | Mon - Fri | OfficeMedium-SWH-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05
OfficeMedium | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | OfficeMedium | SWH | All | Sat | OfficeMedium-SWH-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0 | 0 | 0 | 0 | 0
OfficeMedium | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | OfficeMedium | SWH | All | Sun | OfficeMedium-SWH-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeMedium | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeMedium | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeMedium | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeMedium | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeMedium | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OfficeMedium | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | FAN_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | FAN_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | FAN_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_bot | Temperature | 2023-12-31 | Mon - Fri | Yes (bot, mid, top schedules are the same) | OfficeMedium | Heating Set Point | All | Mon - Fri | OfficeMedium-Heating Set Point-All-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_bot | Temperature | 2023-12-31 | Sat | Yes (bot, mid, top schedules are the same) | OfficeMedium | Heating Set Point | All | Sat | OfficeMedium-Heating Set Point-All-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_bot | Temperature | 2023-12-31 | Sun | Yes (bot, mid, top schedules are the same) | OfficeMedium | Heating Set Point | All | Sun | OfficeMedium-Heating Set Point-All-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_mid | Temperature | 2023-12-31 | Mon - Fri | No (bot, mid, top schedules are the same) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_mid | Temperature | 2023-12-31 | Sat | No (bot, mid, top schedules are the same) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_mid | Temperature | 2023-12-31 | Sun | No (bot, mid, top schedules are the same) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_top | Temperature | 2023-12-31 | Mon - Fri | No (bot, mid, top schedules are the same) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_top | Temperature | 2023-12-31 | Sat | No (bot, mid, top schedules are the same) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | HTGSETP_SCH_PACU_VAV_top | Temperature | 2023-12-31 | Sun | No (bot, mid, top schedules are the same) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.7 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_bot | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_bot | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_bot | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_mid | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_mid | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_mid | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_top | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_top | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_PACU_VAV_top | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
OfficeMedium | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | OfficeMedium | Cooling Set Point | All | Mon - Fri | OfficeMedium-Cooling Set Point-All-Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | OfficeMedium | Cooling Set Point | All | Sat | OfficeMedium-Cooling Set Point-All-Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | OfficeMedium | Cooling Set Point | All | Sun | OfficeMedium-Cooling Set Point-All-Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
OfficeMedium | MinOA_MotorizedDamper_Sched | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
OfficeMedium | MinOA_MotorizedDamper_Sched | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | MinOA_MotorizedDamper_Sched | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | MinOA_Sched | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | MinOA_Sched | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | MinOA_Sched | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeMedium | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeMedium | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeMedium | Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeMedium | Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeMedium | Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OfficeMedium | Core_bottom sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_bottom sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_bottom sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_bottom sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_bottom sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_bottom sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_bottom sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_bottom sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_bottom sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_bottom sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Core_bottom sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Core_bottom sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Core_mid sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_mid sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_mid sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_mid sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_mid sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_mid sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_mid sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_mid sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_mid sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_mid sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Core_mid sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Core_mid sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Core_top sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_top sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_top sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Core_top sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_top sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_top sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Core_top sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_top sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_top sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Core_top sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Core_top sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Core_top sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_top_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_top_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_top_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_top_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_bot_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_bot_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_bot_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_bot_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_3 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_3 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_3 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_3 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_2 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_2 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_2 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_2 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_1 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_1 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_1 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_1 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_4 sub cat Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeMedium | Perimeter_mid_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_4 sub cat Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeMedium | Perimeter_mid_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_4 sub cat Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | Perimeter_mid_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | Perimeter_mid_ZN_4 sub catHot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeMedium | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeMedium | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
OfficeMedium | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeMedium | INFIL_SCH_PNNL | fraction | 2023-12-31 | Mon - Fri | Yes (not schedule:compact) | OfficeMedium | Infiltration | All | Mon - Fri | OfficeMedium-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
OfficeMedium | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sat | Yes (not schedule:compact) | OfficeMedium | Infiltration | All | Sat | OfficeMedium-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeMedium | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sun | Yes (not schedule:compact) | OfficeMedium | Infiltration | All | Sun | OfficeMedium-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeSmall | Lighting | All | Mon - Fri | OfficeSmall-Lighting-All-Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.23 | 0.42 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.42 | 0.42 | 0.32 | 0.32 | 0.23 | 0.18
OfficeSmall | ltg_sch_office | Fraction | 2023-12-31 | Sat | Yes | OfficeSmall | Lighting | All | Sat | OfficeSmall-Lighting-All-Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
OfficeSmall | ltg_sch_office | Fraction | 2023-12-31 | Sun | Yes | OfficeSmall | Lighting | All | Sun | OfficeSmall-Lighting-All-Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
OfficeSmall | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeSmall | Electric Equipment | All | Mon - Fri | OfficeSmall-Electric Equipment-All-Mon - Fri | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | OfficeSmall | Electric Equipment | All | Sat | OfficeSmall-Electric Equipment-All-Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | OfficeSmall | Electric Equipment | All | Sun | OfficeSmall-Electric Equipment-All-Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0
OfficeSmall | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0
OfficeSmall | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | BLDG_OCC_SCH_w_SB | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Mon - Fri | OfficeSmall-Occupants-All (Except Perimeter_mid_ZN_2)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.61039 | 1 | 1 | 1 | 1 | 0.32 | 0.11 | 0.11 | 0.11 | 0.11 | 0.05 | 0
OfficeSmall | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Sat | Yes | OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Sat | OfficeSmall-Occupants-All (Except Perimeter_mid_ZN_2)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | BLDG_OCC_SCH_wo_SB | Fraction | 2023-12-31 | Sun | Yes | OfficeSmall | Occupants | All (Except Perimeter_mid_ZN_2) | Sun | OfficeSmall-Occupants-All (Except Perimeter_mid_ZN_2)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | INFIL_QUARTER_ON_SCH | fraction | 2023-12-31 | Mon - Fri | Yes | OfficeSmall | Infiltration | All | Mon - Fri | OfficeSmall-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
OfficeSmall | INFIL_QUARTER_ON_SCH | fraction | 2023-12-31 | Sat | Yes | OfficeSmall | Infiltration | All | Sat | OfficeSmall-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | INFIL_QUARTER_ON_SCH | fraction | 2023-12-31 | Sun | Yes | OfficeSmall | Infiltration | All | Sun | OfficeSmall-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
OfficeSmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OfficeSmall | SWH | All | Mon - Fri | OfficeSmall-SWH-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27 | 0.55 | 0.64 | 0.64 | 0.82 | 1 | 0.91 | 0.55 | 0.55 | 0.73 | 0.37 | 0.37 | 0.18 | 0.27 | 0.09 | 0 | 0
OfficeSmall | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | OfficeSmall | SWH | All | Sat | OfficeSmall-SWH-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | OfficeSmall | SWH | All | Sun | OfficeSmall-SWH-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | HVACOperationSchd | on/off | 2023-12-31 | Mon - Fri | Yes | OfficeSmall | HVAC | All | Mon - Fri | OfficeSmall-HVAC-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
OfficeSmall | HVACOperationSchd | on/off | 2023-12-31 | Sat | Yes | OfficeSmall | HVAC | All | Sat | OfficeSmall-HVAC-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | HVACOperationSchd | on/off | 2023-12-31 | Sun | Yes | OfficeSmall | HVAC | All | Sun | OfficeSmall-HVAC-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OfficeSmall | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | OfficeSmall | Heating Set Point | All | Mon - Fri | OfficeSmall-Heating Set Point-All-Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | OfficeSmall | Heating Set Point | All | Sat | OfficeSmall-Heating Set Point-All-Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | OfficeSmall | Heating Set Point | All | Sun | OfficeSmall-Heating Set Point-All-Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 20 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
OfficeSmall | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 25 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
OfficeSmall | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | OfficeSmall | Cooling Set Point | All | Mon - Fri | OfficeSmall-Cooling Set Point-All-Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | OfficeSmall | Cooling Set Point | All | Sat | OfficeSmall-Cooling Set Point-All-Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | OfficeSmall | Cooling Set Point | All | Sun | OfficeSmall-Cooling Set Point-All-Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
OfficeSmall | MinOA_Sched | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | MinOA_Sched | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | MinOA_Sched | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeSmall | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeSmall | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OfficeSmall | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeSmall | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeSmall | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OfficeSmall | Core_ZN Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeSmall | Core_ZN Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeSmall | Core_ZN Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OfficeSmall | Core_ZN Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | Core_ZN Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | Core_ZN Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OfficeSmall | Core_ZN Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8
OfficeSmall | Core_ZN Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8
OfficeSmall | Core_ZN Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8
OfficeSmall | Core_ZN Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeSmall | Core_ZN Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeSmall | Core_ZN Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OfficeSmall | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeSmall | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeSmall | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeSmall | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeSmall | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeSmall | SHWSys1 Water Heater Setpoint Temperature Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OfficeSmall | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OfficeSmall | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 PACU Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 PACU Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 PACU Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 PACU Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 PACU Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 PACU Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 PACU Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 PACU Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 PACU Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 PACU Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 PACU Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 PACU Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Step Down Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Step Down Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Step Down Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 1 Step Down Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Step Down Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Step Down Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 1 Step Down Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Step Down Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Step Down Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
OutPatientHealthCare | AHU-1_OAminOAFracSchedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
OutPatientHealthCare | AHU-1_OAminOAFracSchedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
OutPatientHealthCare | AHU-1_OAminOAFracSchedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33
OutPatientHealthCare | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | HeatSys1 Loop Setpoint Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2
OutPatientHealthCare | HeatSys1 Loop Setpoint Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2
OutPatientHealthCare | HeatSys1 Loop Setpoint Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2
OutPatientHealthCare | Hours_of_operation | on/off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Hours_of_operation | on/off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Hours_of_operation | on/off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | HVACOperationSchd | on/off | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | HVAC | All | Mon - Fri | OutPatientHealthCare-HVAC-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | HVACOperationSchd | on/off | 2023-12-31 | Sat | Yes | OutPatientHealthCare | HVAC | All | Sat | OutPatientHealthCare-HVAC-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | HVACOperationSchd | on/off | 2023-12-31 | Sun | Yes | OutPatientHealthCare | HVAC | All | Sun | OutPatientHealthCare-HVAC-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Elevator | All | Mon - Fri | OutPatientHealthCare-Elevator-All-Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.12 | 0.12
OutPatientHealthCare | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Elevator | All | Sat | OutPatientHealthCare-Elevator-All-Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OutPatientHealthCare | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Elevator | All | Sun | OutPatientHealthCare-Elevator-All-Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
OutPatientHealthCare | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | SWH | All | Mon - Fri | OutPatientHealthCare-SWH-All-Mon - Fri | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01
OutPatientHealthCare | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | SWH | All | Sat | OutPatientHealthCare-SWH-All-Sat | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
OutPatientHealthCare | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | SWH | All | Sun | OutPatientHealthCare-SWH-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OutPatientHealthCare | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OutPatientHealthCare | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
OutPatientHealthCare | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | INFIL_SCH | fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Infiltration | All | Mon - Fri | OutPatientHealthCare-Infiltration-All-Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | INFIL_SCH | fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Infiltration | All | Sat | OutPatientHealthCare-Infiltration-All-Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | INFIL_SCH | fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Infiltration | All | Sun | OutPatientHealthCare-Infiltration-All-Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
OutPatientHealthCare | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | FAN_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | FAN_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | FAN_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Humidity Setpoint Schedule | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
OutPatientHealthCare | Humidity Setpoint Schedule | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
OutPatientHealthCare | Humidity Setpoint Schedule | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
OutPatientHealthCare | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
OutPatientHealthCare | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OutPatientHealthCare | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OutPatientHealthCare | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
OutPatientHealthCare | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Lighting | All | Mon - Fri | OutPatientHealthCare-Lighting-All-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_office | Fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Lighting | All | Sat | OutPatientHealthCare-Lighting-All-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_office | Fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Lighting | All | Sun | OutPatientHealthCare-Lighting-All-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_operation | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_operation | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_operation | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_floor_1_office | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_floor_1_office | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_floor_1_office | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_lounge | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_lounge | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_lounge | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_floor_1_sterile_storage | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_floor_1_sterile_storage | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_floor_1_sterile_storage | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_patient | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_patient | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_patient | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_nurse | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_nurse | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_nurse | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_exam | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_exam | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_exam | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_anesthesia | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_anesthesia | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_anesthesia | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_radiology | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_radiology | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_radiology | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_phy_therapy | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_phy_therapy | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_phy_therapy | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_utility | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_utility | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_utility | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_soiled | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_soiled | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_soiled | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_clean | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_clean | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_clean | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_dining | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_dining | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_dining | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_lobby | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_lobby | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_lobby | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_storage | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_storage | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_storage | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_recovery | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_recovery | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_recovery | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_corridor | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_corridor | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_corridor | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_toilet | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_toilet | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_toilet | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_procedure | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_procedure | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_procedure | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_conference | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_conference | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_conference | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | ltg_sch_reception | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_reception | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1
OutPatientHealthCare | ltg_sch_reception | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_office) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Electric Equipment | All | Mon - Fri | OutPatientHealthCare-Electric Equipment-All-Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Electric Equipment | All | Sat | OutPatientHealthCare-Electric Equipment-All-Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Electric Equipment | All | Sun | OutPatientHealthCare-Electric Equipment-All-Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_EQUIP_SCH_BASE | Fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Gas Equipment | Operating Room | Mon - Fri | OutPatientHealthCare-Gas Equipment-Operating Room-Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_EQUIP_SCH_BASE | Fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Gas Equipment | Operating Room | Sat | OutPatientHealthCare-Gas Equipment-Operating Room-Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_EQUIP_SCH_BASE | Fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Gas Equipment | Operating Room | Sun | OutPatientHealthCare-Gas Equipment-Operating Room-Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Occupants | Others | Mon - Fri | OutPatientHealthCare-Occupants-Others-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Occupants | Others | Sat | OutPatientHealthCare-Occupants-Others-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Occupants | Others | Sun | OutPatientHealthCare-Occupants-Others-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | MEETINGROOM_OCC_w_SB_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Occupants | Conference Room | Mon - Fri | OutPatientHealthCare-Occupants-Conference Room-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0 | 0 | 0.9 | 0.9 | 0 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | MEETINGROOM_OCC_w_SB_SCH | Fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Occupants | Conference Room | Sat | OutPatientHealthCare-Occupants-Conference Room-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | MEETINGROOM_OCC_w_SB_SCH | Fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Occupants | Conference Room | Sun | OutPatientHealthCare-Occupants-Conference Room-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | OFFICE_OCC_w_SB_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Mon - Fri | OutPatientHealthCare-Occupants-Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0 | 0.9 | 0 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05
OutPatientHealthCare | OFFICE_OCC_w_SB_SCH | Fraction | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Sat | OutPatientHealthCare-Occupants-Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0 | 0.3 | 0.3 | 0 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05
OutPatientHealthCare | OFFICE_OCC_w_SB_SCH | Fraction | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Occupants | Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work | Sun | OutPatientHealthCare-Occupants-Dictation, Dressing Room, Humid, IT Room, Office, Scheduling, Work-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Heating Set Point | Others | Mon - Fri | OutPatientHealthCare-Heating Set Point-Others-Mon - Fri | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Heating Set Point | Others | Sat | OutPatientHealthCare-Heating Set Point-Others-Sat | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Heating Set Point | Others | Sun | OutPatientHealthCare-Heating Set Point-Others-Sun | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 20 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 19.4 | 20 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 20.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3
OutPatientHealthCare | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 23.3 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 25 | 25 | 25 | 25 | 25 | 23.9 | 23.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 23.3 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
OutPatientHealthCare | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Cooling Set Point | Others | Mon - Fri | OutPatientHealthCare-Cooling Set Point-Others-Mon - Fri | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Cooling Set Point | Others | Sat | OutPatientHealthCare-Cooling Set Point-Others-Sat | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Cooling Set Point | Others | Sun | OutPatientHealthCare-Cooling Set Point-Others-Sun | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | OR_HTGSETP_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Heating Set Point | OR | Mon - Fri | OutPatientHealthCare-Heating Set Point-OR-Mon - Fri | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | OR_HTGSETP_SCH | Temperature | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Heating Set Point | OR | Sat | OutPatientHealthCare-Heating Set Point-OR-Sat | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | OR_HTGSETP_SCH | Temperature | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Heating Set Point | OR | Sun | OutPatientHealthCare-Heating Set Point-OR-Sun | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
OutPatientHealthCare | OR_CLGSETP_SCH | Temperature | 2023-12-31 | Mon - Fri | Yes | OutPatientHealthCare | Cooling Set Point | OR | Mon - Fri | OutPatientHealthCare-Cooling Set Point-OR-Mon - Fri | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | OR_CLGSETP_SCH | Temperature | 2023-12-31 | Sat | Yes | OutPatientHealthCare | Cooling Set Point | OR | Sat | OutPatientHealthCare-Cooling Set Point-OR-Sat | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | OR_CLGSETP_SCH | Temperature | 2023-12-31 | Sun | Yes | OutPatientHealthCare | Cooling Set Point | OR | Sun | OutPatientHealthCare-Cooling Set Point-OR-Sun | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
OutPatientHealthCare | MinRelHumSetSch | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
OutPatientHealthCare | MinRelHumSetSch | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
OutPatientHealthCare | MinRelHumSetSch | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
OutPatientHealthCare | MinRelHumSetSch_addDI | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OutPatientHealthCare | MinRelHumSetSch_addDI | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OutPatientHealthCare | MinRelHumSetSch_addDI | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
OutPatientHealthCare | MaxRelHumSetSch | Humidity | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | MaxRelHumSetSch | Humidity | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | MaxRelHumSetSch | Humidity | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OutPatientHealthCare | BLDG_OA_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | BLDG_OA_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | BLDG_OA_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | CAV_SAT_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
OutPatientHealthCare | CAV_SAT_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
OutPatientHealthCare | CAV_SAT_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
OutPatientHealthCare | VAV_SAT_SCH | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OutPatientHealthCare | VAV_SAT_SCH | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OutPatientHealthCare | VAV_SAT_SCH | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
OutPatientHealthCare | BLDG_CAV_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_CAV_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_CAV_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
OutPatientHealthCare | BLDG_OA_FRAC_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | BLDG_OA_FRAC_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | BLDG_OA_FRAC_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | AHU_1 Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | AHU_1 Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | AHU_1 Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | AHU_2 Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | AHU_2 Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OutPatientHealthCare | AHU_2 Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | ltg_sch_dining | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Lighting | All | Mon - Fri | RestaurantFastFood-Lighting-All-Mon - Fri | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | ltg_sch_dining | Fraction | 2023-12-31 | Sat | Yes | RestaurantFastFood | Lighting | All | Sat | RestaurantFastFood-Lighting-All-Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | ltg_sch_dining | Fraction | 2023-12-31 | Sun | Yes | RestaurantFastFood | Lighting | All | Sun | RestaurantFastFood-Lighting-All-Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantFastFood | ltg_sch_kitchen | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_dining) |  |  |  |  | --- | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | ltg_sch_kitchen | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_dining) |  |  |  |  | --- | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | ltg_sch_kitchen | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_dining) |  |  |  |  | --- | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantFastFood | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Electric Equipment | All | Mon - Fri | RestaurantFastFood-Electric Equipment-All-Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | RestaurantFastFood | Electric Equipment | All | Sat | RestaurantFastFood-Electric Equipment-All-Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | RestaurantFastFood | Electric Equipment | All | Sun | RestaurantFastFood-Electric Equipment-All-Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | FF_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Gas Equipment | Kitchen | Mon - Fri | RestaurantFastFood-Gas Equipment-Kitchen-Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | FF_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | RestaurantFastFood | Gas Equipment | Kitchen | Sat | RestaurantFastFood-Gas Equipment-Kitchen-Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | FF_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | RestaurantFastFood | Gas Equipment | Kitchen | Sun | RestaurantFastFood-Gas Equipment-Kitchen-Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantFastFood | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Occupants | All | Mon - Fri | RestaurantFastFood-Occupants-All-Mon - Fri | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
RestaurantFastFood | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | RestaurantFastFood | Occupants | All | Sat | RestaurantFastFood-Occupants-All-Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
RestaurantFastFood | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | RestaurantFastFood | Occupants | All | Sun | RestaurantFastFood-Occupants-All-Sun | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
RestaurantFastFood | INFIL_SCH_PNNL | fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Infiltration | All | Mon - Fri | RestaurantFastFood-Infiltration-All-Mon - Fri | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sat | Yes | RestaurantFastFood | Infiltration | All | Sat | RestaurantFastFood-Infiltration-All-Sat | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sun | Yes | RestaurantFastFood | Infiltration | All | Sun | RestaurantFastFood-Infiltration-All-Sun | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantFastFood | DOOR_INFIL_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258
RestaurantFastFood | DOOR_INFIL_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363
RestaurantFastFood | DOOR_INFIL_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258
RestaurantFastFood | VESTIBULE_DOOR_INFIL_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241
RestaurantFastFood | VESTIBULE_DOOR_INFIL_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345
RestaurantFastFood | VESTIBULE_DOOR_INFIL_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241
RestaurantFastFood | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | SWH | All | Mon - Fri | RestaurantFastFood-SWH-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.33 | 0.13 | 0.1 | 0.72 | 0.31 | 0.98 | 0.92 | 0.22 | 0.31 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0.15
RestaurantFastFood | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | RestaurantFastFood | SWH | All | Sat | RestaurantFastFood-SWH-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
RestaurantFastFood | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | RestaurantFastFood | SWH | All | Sun | RestaurantFastFood-SWH-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.1 | 0.72 | 0.6 | 0.98 | 0.92 | 0.25 | 0.25 | 0.23 | 0.16 | 0.1 | 0.4 | 0.42 | 0.43 | 0
RestaurantFastFood | Hours_of_operation | on/off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Hours_of_operation | on/off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Hours_of_operation | on/off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | HVACOperationSchd | on/off | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | HVAC | All | Mon - Fri | RestaurantFastFood-HVAC-All-Mon - Fri | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | HVACOperationSchd | on/off | 2023-12-31 | Sat | Yes | RestaurantFastFood | HVAC | All | Sat | RestaurantFastFood-HVAC-All-Sat | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | HVACOperationSchd | on/off | 2023-12-31 | Sun | Yes | RestaurantFastFood | HVAC | All | Sun | RestaurantFastFood-HVAC-All-Sun | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Heating Set Point | Dining | Mon - Fri | RestaurantFastFood-Heating Set Point-Dining-Mon - Fri | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | RestaurantFastFood | Heating Set Point | Dining | Sat | RestaurantFastFood-Heating Set Point-Dining-Sat | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | RestaurantFastFood | Heating Set Point | Dining | Sun | RestaurantFastFood-Heating Set Point-Dining-Sun | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RestaurantFastFood | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 30 | 30 | 30 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 30 | 30 | 30 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 30 | 30 | 30 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Cooling Set Point | Dining | Mon - Fri | RestaurantFastFood-Cooling Set Point-Dining-Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | RestaurantFastFood | Cooling Set Point | Dining | Sat | RestaurantFastFood-Cooling Set Point-Dining-Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | RestaurantFastFood | Cooling Set Point | Dining | Sun | RestaurantFastFood-Cooling Set Point-Dining-Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RestaurantFastFood | HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 16.7 | 17.8 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 16.7 | 17.8 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 16.7 | 17.8 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Heating Set Point | Kitchen | Mon - Fri | RestaurantFastFood-Heating Set Point-Kitchen-Mon - Fri | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | RestaurantFastFood | Heating Set Point | Kitchen | Sat | RestaurantFastFood-Heating Set Point-Kitchen-Sat | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | RestaurantFastFood | Heating Set Point | Kitchen | Sun | RestaurantFastFood-Heating Set Point-Kitchen-Sun | 15.56 | 15.56 | 15.56 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89 | 18.89
RestaurantFastFood | CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 30 | 30 | 30 | 28.9 | 27.8 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 30 | 30 | 30 | 28.9 | 27.8 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 30 | 30 | 30 | 28.9 | 27.8 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | CLGSETP_KITCHEN_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | RestaurantFastFood | Cooling Set Point | Kitchen | Mon - Fri | RestaurantFastFood-Cooling Set Point-Kitchen-Mon - Fri | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | CLGSETP_KITCHEN_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | RestaurantFastFood | Cooling Set Point | Kitchen | Sat | RestaurantFastFood-Cooling Set Point-Kitchen-Sat | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | CLGSETP_KITCHEN_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | RestaurantFastFood | Cooling Set Point | Kitchen | Sun | RestaurantFastFood-Cooling Set Point-Kitchen-Sun | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11 | 26.11
RestaurantFastFood | MinOA_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | MinOA_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | MinOA_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | MinOA_FFKitch_Sched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | MinOA_FFKitch_Sched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | MinOA_FFKitch_Sched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RestaurantFastFood | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RestaurantFastFood | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RestaurantFastFood | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RestaurantFastFood | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RestaurantFastFood | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RestaurantFastFood | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantFastFood | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantFastFood | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Kitchen Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RestaurantFastFood | Kitchen Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RestaurantFastFood | Kitchen Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RestaurantFastFood | Kitchen Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantFastFood | Kitchen Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantFastFood | Kitchen Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantFastFood | Kitchen Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | Kitchen Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | Kitchen Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | Kitchen Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
RestaurantFastFood | Kitchen Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
RestaurantFastFood | Kitchen Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | TuesdayFriday | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
RestaurantFastFood | Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
RestaurantFastFood | Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantFastFood | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantFastFood | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantFastFood | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantFastFood | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantFastFood | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.53054 | 0 | 0 | 0 | 0 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054
RestaurantFastFood | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.53054 | 0 | 0 | 0 | 0 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054
RestaurantFastFood | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.53054 | 0 | 0 | 0 | 0 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054 | 0.53054
RestaurantSitDown | ltg_sch_dining | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Lighting | All | Mon - Fri | RestaurantSitDown-Lighting-All-Mon - Fri | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | ltg_sch_dining | Fraction | 2023-12-31 | Sat | Yes | RestaurantSitDown | Lighting | All | Sat | RestaurantSitDown-Lighting-All-Sat | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | ltg_sch_dining | Fraction | 2023-12-31 | Sun | Yes | RestaurantSitDown | Lighting | All | Sun | RestaurantSitDown-Lighting-All-Sun | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantSitDown | ltg_sch_kitchen | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_dining) |  |  |  |  | --- | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | ltg_sch_kitchen | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_dining) |  |  |  |  | --- | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | ltg_sch_kitchen | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_dining) |  |  |  |  | --- | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantSitDown | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Electric Equipment | All | Mon - Fri | RestaurantSitDown-Electric Equipment-All-Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | RestaurantSitDown | Electric Equipment | All | Sat | RestaurantSitDown-Electric Equipment-All-Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | RestaurantSitDown | Electric Equipment | All | Sun | RestaurantSitDown-Electric Equipment-All-Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Rest_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Gas Equipment | Kitchen | Mon - Fri | RestaurantSitDown-Gas Equipment-Kitchen-Mon - Fri | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Rest_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | RestaurantSitDown | Gas Equipment | Kitchen | Sat | RestaurantSitDown-Gas Equipment-Kitchen-Sat | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | Rest_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | RestaurantSitDown | Gas Equipment | Kitchen | Sun | RestaurantSitDown-Gas Equipment-Kitchen-Sun | 0.03 | 0.02 | 0.03 | 0.02 | 0.05 | 0.12 | 0.13 | 0.15 | 0.18 | 0.21 | 0.26 | 0.29 | 0.27 | 0.25 | 0.23 | 0.23 | 0.26 | 0.26 | 0.24 | 0.22 | 0.2 | 0.18 | 0.09 | 0.03
RestaurantSitDown | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Occupants | All | Mon - Fri | RestaurantSitDown-Occupants-All-Mon - Fri | 0.05 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.4 | 0.4 | 0.4 | 0.2 | 0.5 | 0.8 | 0.7 | 0.4 | 0.2 | 0.25 | 0.5 | 0.8 | 0.8 | 0.8 | 0.5 | 0.35 | 0.2
RestaurantSitDown | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | RestaurantSitDown | Occupants | All | Sat | RestaurantSitDown-Occupants-All-Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.4 | 0.2 | 0.45 | 0.5 | 0.5 | 0.35 | 0.3 | 0.3 | 0.3 | 0.7 | 0.9 | 0.7 | 0.65 | 0.55 | 0.35
RestaurantSitDown | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | RestaurantSitDown | Occupants | All | Sun | RestaurantSitDown-Occupants-All-Sun | 0.05 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.3 | 0.2 | 0.25 | 0.35 | 0.55 | 0.65 | 0.7 | 0.35 | 0.2 | 0.2
RestaurantSitDown | INFIL_SCH_PNNL | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Infiltration | All | Mon - Fri | RestaurantSitDown-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | INFIL_SCH_PNNL | Fraction | 2023-12-31 | Sat | Yes | RestaurantSitDown | Infiltration | All | Sat | RestaurantSitDown-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | INFIL_SCH_PNNL | Fraction | 2023-12-31 | Sun | Yes | RestaurantSitDown | Infiltration | All | Sun | RestaurantSitDown-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RestaurantSitDown | DOOR_INFIL_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.462 | 0.462 | 0.462 | 0.258 | 0.558 | 0.829 | 0.74 | 0.462 | 0.258 | 0.363 | 0.558 | 0.829 | 0.829 | 0.829 | 0.558 | 0.363 | 0.258
RestaurantSitDown | DOOR_INFIL_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.462 | 0.258 | 0.462 | 0.558 | 0.558 | 0.462 | 0.363 | 0.363 | 0.363 | 0.74 | 0.915 | 0.74 | 0.65 | 0.558 | 0.363
RestaurantSitDown | DOOR_INFIL_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.558 | 0.558 | 0.258 | 0.258 | 0.363 | 0.558 | 0.558 | 0.363 | 0.258 | 0.363 | 0.462 | 0.558 | 0.65 | 0.74 | 0.462 | 0.258 | 0.258
RestaurantSitDown | VESTIBULE_DOOR_INFIL_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.445 | 0.445 | 0.445 | 0.241 | 0.542 | 0.821 | 0.73 | 0.445 | 0.241 | 0.345 | 0.542 | 0.821 | 0.821 | 0.821 | 0.542 | 0.345 | 0.241
RestaurantSitDown | VESTIBULE_DOOR_INFIL_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.445 | 0.241 | 0.445 | 0.542 | 0.542 | 0.445 | 0.345 | 0.345 | 0.345 | 0.73 | 0.911 | 0.73 | 0.637 | 0.542 | 0.345
RestaurantSitDown | VESTIBULE_DOOR_INFIL_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.131 | 0.542 | 0.542 | 0.241 | 0.241 | 0.345 | 0.542 | 0.542 | 0.345 | 0.241 | 0.345 | 0.445 | 0.542 | 0.637 | 0.73 | 0.445 | 0.241 | 0.241
RestaurantSitDown | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
RestaurantSitDown | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
RestaurantSitDown | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
RestaurantSitDown | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | SWH | All | Mon - Fri | RestaurantSitDown-SWH-All-Mon - Fri | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25
RestaurantSitDown | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | RestaurantSitDown | SWH | All | Sat | RestaurantSitDown-SWH-All-Sat | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3
RestaurantSitDown | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | RestaurantSitDown | SWH | All | Sun | RestaurantSitDown-SWH-All-Sun | 0.25 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2
RestaurantSitDown | Hours_of_operation | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Hours_of_operation | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Hours_of_operation | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | PlantOnSched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | PlantOnSched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | PlantOnSched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | HVACOperationSchd | On/Off | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | HVAC | All | Mon - Fri | RestaurantSitDown-HVAC-All-Mon - Fri | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | HVACOperationSchd | On/Off | 2023-12-31 | Sat | Yes | RestaurantSitDown | HVAC | All | Sat | RestaurantSitDown-HVAC-All-Sat | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | HVACOperationSchd | On/Off | 2023-12-31 | Sun | Yes | RestaurantSitDown | HVAC | All | Sun | RestaurantSitDown-HVAC-All-Sun | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Heating Set Point | Dining | Mon - Fri | RestaurantSitDown-Heating Set Point-Dining-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | RestaurantSitDown | Heating Set Point | Dining | Sat | RestaurantSitDown-Heating Set Point-Dining-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | RestaurantSitDown | Heating Set Point | Dining | Sun | RestaurantSitDown-Heating Set Point-Dining-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
RestaurantSitDown | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 30 | 30 | 30 | 30 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Cooling Set Point | Dining | Mon - Fri | RestaurantSitDown-Cooling Set Point-Dining-Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | RestaurantSitDown | Cooling Set Point | Dining | Sat | RestaurantSitDown-Cooling Set Point-Dining-Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | RestaurantSitDown | Cooling Set Point | Dining | Sun | RestaurantSitDown-Cooling Set Point-Dining-Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
RestaurantSitDown | HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 19 | 15.6 | 15.6 | 15.6 | 16.7 | 17.8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 19 | 15.6 | 15.6 | 15.6 | 16.7 | 17.8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | HTGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 19 | 15.6 | 15.6 | 15.6 | 16.7 | 17.8 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Heating Set Point | Kitchen | Mon - Fri | RestaurantSitDown-Heating Set Point-Kitchen-Mon - Fri | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | RestaurantSitDown | Heating Set Point | Kitchen | Sat | RestaurantSitDown-Heating Set Point-Kitchen-Sat | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | HTGSETP_KITCHEN_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | RestaurantSitDown | Heating Set Point | Kitchen | Sun | RestaurantSitDown-Heating Set Point-Kitchen-Sun | 19 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
RestaurantSitDown | CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26 | 30 | 30 | 30 | 28.9 | 27.8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26 | 30 | 30 | 30 | 28.9 | 27.8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | CLGSETP_KITCHEN_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26 | 30 | 30 | 30 | 28.9 | 27.8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | CLGSETP_KITCHEN_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | RestaurantSitDown | Cooling Set Point | Kitchen | Mon - Fri | RestaurantSitDown-Cooling Set Point-Kitchen-Mon - Fri | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | CLGSETP_KITCHEN_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | RestaurantSitDown | Cooling Set Point | Kitchen | Sat | RestaurantSitDown-Cooling Set Point-Kitchen-Sat | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | CLGSETP_KITCHEN_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | RestaurantSitDown | Cooling Set Point | Kitchen | Sun | RestaurantSitDown-Cooling Set Point-Kitchen-Sun | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
RestaurantSitDown | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | MinOA_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | MinOA_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | MinOA_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | MinOA_SDKitch_Sched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | MinOA_SDKitch_Sched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | MinOA_SDKitch_Sched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RestaurantSitDown | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RestaurantSitDown | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RestaurantSitDown | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RestaurantSitDown | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RestaurantSitDown | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RestaurantSitDown | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantSitDown | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantSitDown | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Kitchen Water Equipment Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RestaurantSitDown | Kitchen Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RestaurantSitDown | Kitchen Water Equipment Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RestaurantSitDown | Kitchen Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantSitDown | Kitchen Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantSitDown | Kitchen Water Equipment Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RestaurantSitDown | Kitchen Water Equipment Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | Kitchen Water Equipment Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | Kitchen Water Equipment Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | Kitchen Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
RestaurantSitDown | Kitchen Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
RestaurantSitDown | Kitchen Water Equipment Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | TuesdayFriday | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
RestaurantSitDown | Kitchen_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
RestaurantSitDown | Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RestaurantSitDown | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | SWHSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RestaurantSitDown | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.2 | 0.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3
RestaurantSitDown | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3
RestaurantSitDown | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RestaurantSitDown | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.93377 | 0 | 0 | 0 | 0 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377
RestaurantSitDown | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.93377 | 0 | 0 | 0 | 0 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377
RestaurantSitDown | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.93377 | 0 | 0 | 0 | 0 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377 | 0.93377
RetailStandalone | FrontEntry_CoilSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | FrontEntry_CoilSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | FrontEntry_CoilSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | FrontEntry_FanSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | FrontEntry_FanSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | FrontEntry_FanSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | ltg_sch_entry | Fraction | 2023-12-31 | Mon - Fri | Yes (all other spaces have the same schedules) | RetailStandalone | Lighting | All | Mon - Fri | RetailStandalone-Lighting-All-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone | ltg_sch_entry | Fraction | 2023-12-31 | Sat | Yes (all other spaces have the same schedules) | RetailStandalone | Lighting | All | Sat | RetailStandalone-Lighting-All-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone | ltg_sch_entry | Fraction | 2023-12-31 | Sun | Yes (all other spaces have the same schedules) | RetailStandalone | Lighting | All | Sun | RetailStandalone-Lighting-All-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone | ltg_sch_core | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone | ltg_sch_core | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone | ltg_sch_core | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone | ltg_sch_back | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone | ltg_sch_back | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone | ltg_sch_back | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone | ltg_sch_sale | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone | ltg_sch_sale | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone | ltg_sch_sale | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone | ltg_sch_front | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.5 | 0.2 | 0.05 | 0.05
RetailStandalone | ltg_sch_front | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05
RetailStandalone | ltg_sch_front | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_entry) |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStandalone | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStandalone | Occupants | All | Mon - Fri | RetailStandalone-Occupants-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0
RetailStandalone | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStandalone | Occupants | All | Sat | RetailStandalone-Occupants-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0
RetailStandalone | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStandalone | Occupants | All | Sun | RetailStandalone-Occupants-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0
RetailStandalone | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStandalone | Electric Equipment | All | Mon - Fri | RetailStandalone-Electric Equipment-All-Mon - Fri | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2
RetailStandalone | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStandalone | Electric Equipment | All | Sat | RetailStandalone-Electric Equipment-All-Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15
RetailStandalone | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStandalone | Electric Equipment | All | Sun | RetailStandalone-Electric Equipment-All-Sun | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
RetailStandalone | INFIL_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1
RetailStandalone | INFIL_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
RetailStandalone | INFIL_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0
RetailStandalone | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0
RetailStandalone | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0
RetailStandalone | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStandalone | SWH | All | Mon - Fri | RetailStandalone-SWH-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0 | 0 | 0
RetailStandalone | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStandalone | SWH | All | Sat | RetailStandalone-SWH-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0 | 0
RetailStandalone | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStandalone | SWH | All | Sun | RetailStandalone-SWH-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0 | 0 | 0 | 0 | 0
RetailStandalone | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RetailStandalone | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RetailStandalone | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RetailStandalone | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | HVACOperationSchd | on/off | 2023-12-31 | Mon - Fri | Yes | RetailStandalone | HVAC | All | Mon - Fri | RetailStandalone-HVAC-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStandalone | HVACOperationSchd | on/off | 2023-12-31 | Sat | Yes | RetailStandalone | HVAC | All | Sat | RetailStandalone-HVAC-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
RetailStandalone | HVACOperationSchd | on/off | 2023-12-31 | Sun | Yes | RetailStandalone | HVAC | All | Sun | RetailStandalone-HVAC-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStandalone | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 17.8 | 20 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | RetailStandalone | Heating Set Point | All (Except Core_Retail) | Mon - Fri | RetailStandalone-Heating Set Point-All (Except Core_Retail)-Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | RetailStandalone | Heating Set Point | All (Except Core_Retail) | Sat | RetailStandalone-Heating Set Point-All (Except Core_Retail)-Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | RetailStandalone | Heating Set Point | All (Except Core_Retail) | Sun | RetailStandalone-Heating Set Point-All (Except Core_Retail)-Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_PSZ_AC_2 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_PSZ_AC_2 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56
RetailStandalone | HTGSETP_SCH_PSZ_AC_2 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStandalone | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_YES_OPTIMUM_ORIGINAL | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_PSZ_AC_2 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_PSZ_AC_2 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_PSZ_AC_2 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStandalone | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Mon - Fri | RetailStandalone-Cooling Set Point-All (Except Front_Entry)-Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Sat | RetailStandalone-Cooling Set Point-All (Except Front_Entry)-Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | RetailStandalone | Cooling Set Point | All (Except Front_Entry) | Sun | RetailStandalone-Cooling Set Point-All (Except Front_Entry)-Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStandalone | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStandalone | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
RetailStandalone | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStandalone | MinOA_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | MinOA_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | MinOA_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RetailStandalone | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RetailStandalone | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RetailStandalone | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RetailStandalone | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RetailStandalone | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RetailStandalone | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RetailStandalone | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RetailStandalone | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RetailStandalone | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RetailStandalone | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RetailStandalone | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RetailStandalone | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RetailStandalone | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RetailStandalone | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RetailStandalone | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | FRONT_ENTRY_COOLING | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
RetailStandalone | FRONT_ENTRY_COOLING | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
RetailStandalone | FRONT_ENTRY_COOLING | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
RetailStandalone | INFIL_SCH_PNNL | fraction | 2023-12-31 | Mon - Fri | Yes | RetailStandalone | Infiltration | All | Mon - Fri | RetailStandalone-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStandalone | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sat | Yes | RetailStandalone | Infiltration | All | Sat | RetailStandalone-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1
RetailStandalone | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sun | Yes | RetailStandalone | Infiltration | All | Sun | RetailStandalone-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStandalone | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type1_OCC_SCH | Fraction | 2023-12-31 | MondayTuesdayWednesdayThursday | Yes | RetailStripmall | Occupants | Type 1 Store | Mon - Thu | RetailStripmall-Occupants-Type 1 Store-Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.05
RetailStripmall | Type1_OCC_SCH | Fraction | 2023-12-31 | FridaySaturday | Yes | RetailStripmall | Occupants | Type 1 Store | Fri, Sat | RetailStripmall-Occupants-Type 1 Store-Fri, Sat | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.6 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2
RetailStripmall | Type1_OCC_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.6 | 0.4 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.2
RetailStripmall | Type1_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Occupants | Type 1 Store | Sun | RetailStripmall-Occupants-Type 1 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.4 | 0.3 | 0.6 | 0.6 | 0.4 | 0.4 | 0.3 | 0.2 | 0.05
RetailStripmall | Type2_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Occupants | Type 2 Store | Mon - Fri | RetailStripmall-Occupants-Type 2 Store-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.3 | 0.2 | 0.2 | 0.5 | 0.5 | 0.2 | 0.05 | 0 | 0 | 0
RetailStripmall | Type2_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Occupants | Type 2 Store | Sat | RetailStripmall-Occupants-Type 2 Store-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.1 | 0.2 | 0.4 | 0.6 | 0.4 | 0.3 | 0.3 | 0.3 | 0.05 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type2_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Occupants | Type 2 Store | Sun | RetailStripmall-Occupants-Type 2 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.1 | 0.2 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type3_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Occupants | Type 3 Store | Mon - Fri | RetailStripmall-Occupants-Type 3 Store-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.71 | 0.5 | 0.69 | 0.54 | 0.71 | 0.34 | 0.26 | 0.11 | 0 | 0 | 0
RetailStripmall | Type3_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Occupants | Type 3 Store | Sat | RetailStripmall-Occupants-Type 3 Store-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.58 | 0.71 | 0.74 | 0.77 | 0.8 | 0.74 | 0.54 | 0.11 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type3_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Occupants | Type 3 Store | Sun | RetailStripmall-Occupants-Type 3 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.11 | 0.43 | 0.46 | 0.5 | 0.69 | 0.34 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | ltg_sch_display_lpd_type1_smstore | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_display_lpd_type1_smstore | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_display_lpd_type1_smstore | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_base_lpd2 | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Lighting | Type 2 Large Store | Mon - Fri | RetailStripmall-Lighting-Type 2 Large Store-Mon - Fri | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | ltg_sch_base_lpd2 | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Lighting | Type 2 Large Store | Sat | RetailStripmall-Lighting-Type 2 Large Store-Sat | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | ltg_sch_base_lpd2 | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Lighting | Type 2 Large Store | Sun | RetailStripmall-Lighting-Type 2 Large Store-Sun | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.49875 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.94763 | 0.49875 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988 | 0.04988
RetailStripmall | ltg_sch_base_small_lpd2_type3 | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Lighting | Type 3 Store | Mon - Fri | RetailStripmall-Lighting-Type 3 Store-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_base_small_lpd2_type3 | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Lighting | Type 3 Store | Sat | RetailStripmall-Lighting-Type 3 Store-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_base_small_lpd2_type3 | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Lighting | Type 3 Store | Sun | RetailStripmall-Lighting-Type 3 Store-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_display_lpd_type3_lgstore | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5
RetailStripmall | ltg_sch_display_lpd_type3_lgstore | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
RetailStripmall | ltg_sch_display_lpd_type3_lgstore | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5
RetailStripmall | ltg_sch_display_lpd_type3_smstore | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5
RetailStripmall | ltg_sch_display_lpd_type3_smstore | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
RetailStripmall | ltg_sch_display_lpd_type3_smstore | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5
RetailStripmall | ltg_sch_base_small_lpd1 | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Lighting | Type 1 Small Store | Mon - Fri | RetailStripmall-Lighting-Type 1 Small Store-Mon - Fri | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.502
RetailStripmall | ltg_sch_base_small_lpd1 | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Lighting | Type 1 Small Store | Sat | RetailStripmall-Lighting-Type 1 Small Store-Sat | 0.502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538
RetailStripmall | ltg_sch_base_small_lpd1 | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Lighting | Type 1 Small Store | Sun | RetailStripmall-Lighting-Type 1 Small Store-Sun | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.0502 | 0.502 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.9538 | 0.502
RetailStripmall | ltg_sch_base_lpd1 | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Lighting | Type 1 Large Store | Mon - Fri | RetailStripmall-Lighting-Type 1 Large Store-Mon - Fri | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.50075
RetailStripmall | ltg_sch_base_lpd1 | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Lighting | Type 1 Large Store | Sat | RetailStripmall-Lighting-Type 1 Large Store-Sat | 0.50075 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142
RetailStripmall | ltg_sch_base_lpd1 | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Lighting | Type 1 Large Store | Sun | RetailStripmall-Lighting-Type 1 Large Store-Sun | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.05008 | 0.50075 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.95142 | 0.50075
RetailStripmall | ltg_sch_display_lpd_type1_lgstore | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_display_lpd_type1_lgstore | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_display_lpd_type1_lgstore | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_base_small_lpd2_type2 | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Lighting | Type 2 Small Store | Mon - Fri | RetailStripmall-Lighting-Type 2 Small Store-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_base_small_lpd2_type2 | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Lighting | Type 2 Small Store | Sat | RetailStripmall-Lighting-Type 2 Small Store-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_base_small_lpd2_type2 | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Lighting | Type 2 Small Store | Sun | RetailStripmall-Lighting-Type 2 Small Store-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_display_lpd_type2_smstore | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_display_lpd_type2_smstore | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | ltg_sch_display_lpd_type2_smstore | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Type1_EQUIP_SCH | Fraction | 2023-12-31 | MondayTuesdayWednesdayThursday | Yes | RetailStripmall | Electric Equipment | Type 1 Store | Mon - Thu | RetailStripmall-Electric Equipment-Type 1 Store-Mon - Thu | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
RetailStripmall | Type1_EQUIP_SCH | Fraction | 2023-12-31 | FridaySaturday | Yes | RetailStripmall | Electric Equipment | Type 1 Store | Fri, Sat | RetailStripmall-Electric Equipment-Type 1 Store-Fri, Sat | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
RetailStripmall | Type1_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
RetailStripmall | Type1_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Electric Equipment | Type 1 Store | Sun | RetailStripmall-Electric Equipment-Type 1 Store-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5
RetailStripmall | Type2_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Electric Equipment | Type 2 Store | Mon - Fri | RetailStripmall-Electric Equipment-Type 2 Store-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Type2_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Electric Equipment | Type 2 Store | Sat | RetailStripmall-Electric Equipment-Type 2 Store-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Type2_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Electric Equipment | Type 2 Store | Sun | RetailStripmall-Electric Equipment-Type 2 Store-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Type3_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Electric Equipment | Type 3 Store | Mon - Fri | RetailStripmall-Electric Equipment-Type 3 Store-Mon - Fri | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05
RetailStripmall | Type3_EQUIP_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Electric Equipment | Type 3 Store | Sat | RetailStripmall-Electric Equipment-Type 3 Store-Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Type3_EQUIP_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Electric Equipment | Type 3 Store | Sun | RetailStripmall-Electric Equipment-Type 3 Store-Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
RetailStripmall | Type1_Infil_SCH | fraction | 2023-12-31 | MondayTuesdayWednesdayThursday | Yes | RetailStripmall | Infiltration | Type 1 Store | Mon - Thu | RetailStripmall-Infiltration-Type 1 Store-Mon - Thu | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Type1_Infil_SCH | fraction | 2023-12-31 | FridaySaturday | Yes | RetailStripmall | Infiltration | Type 1 Store | Fri, Sat | RetailStripmall-Infiltration-Type 1 Store-Fri, Sat | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Type1_Infil_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Type1_Infil_SCH | fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Infiltration | Type 1 Store | Sun | RetailStripmall-Infiltration-Type 1 Store-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
RetailStripmall | Type2_Infil_SCH | fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Infiltration | Type 2 Store | Mon - Fri | RetailStripmall-Infiltration-Type 2 Store-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStripmall | Type2_Infil_SCH | fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Infiltration | Type 2 Store | Sat | RetailStripmall-Infiltration-Type 2 Store-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type2_Infil_SCH | fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Infiltration | Type 2 Store | Sun | RetailStripmall-Infiltration-Type 2 Store-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type3_Infil_SCH | fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Infiltration | Type 3 Store | Mon - Fri | RetailStripmall-Infiltration-Type 3 Store-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
RetailStripmall | Type3_Infil_SCH | fraction | 2023-12-31 | Sat | Yes | RetailStripmall | Infiltration | Type 3 Store | Sat | RetailStripmall-Infiltration-Type 3 Store-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type3_Infil_SCH | fraction | 2023-12-31 | Sun | Yes | RetailStripmall | Infiltration | Type 3 Store | Sun | RetailStripmall-Infiltration-Type 3 Store-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0
RetailStripmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0
RetailStripmall | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 1 | 1 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0
RetailStripmall | Type1_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | MondayTuesdayWednesdayThursdayWinterDesignDay | No |  |  |  |  | --- | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Type1_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | FridaySaturday | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Type1_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Type1_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Type1_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | MondayTuesdayWednesdayThursday | Yes | RetailStripmall | Heating Set Point | Type 1 Store | Mon - Thu | RetailStripmall-Heating Set Point-Type 1 Store-Mon - Thu | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Type1_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | FridaySaturday | Yes | RetailStripmall | Heating Set Point | Type 1 Store | Fri, Sat | RetailStripmall-Heating Set Point-Type 1 Store-Fri, Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Type1_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Type1_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | RetailStripmall | Heating Set Point | Type 1 Store | Sun | RetailStripmall-Heating Set Point-Type 1 Store-Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11
RetailStripmall | Type2_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall | Type2_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Type2_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Type2_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Heating Set Point | Type 2 Store | Mon - Fri | RetailStripmall-Heating Set Point-Type 2 Store-Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall | Type2_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | RetailStripmall | Heating Set Point | Type 2 Store | Sat | RetailStripmall-Heating Set Point-Type 2 Store-Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Type2_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | RetailStripmall | Heating Set Point | Type 2 Store | Sun | RetailStripmall-Heating Set Point-Type 2 Store-Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Type3_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall | Type3_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Type3_HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 18.33 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Type3_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Heating Set Point | Type 3 Store | Mon - Fri | RetailStripmall-Heating Set Point-Type 3 Store-Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56
RetailStripmall | Type3_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | RetailStripmall | Heating Set Point | Type 3 Store | Sat | RetailStripmall-Heating Set Point-Type 3 Store-Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Type3_HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | RetailStripmall | Heating Set Point | Type 3 Store | Sun | RetailStripmall-Heating Set Point-Type 3 Store-Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 21.11 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
RetailStripmall | Type1_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | MondayTuesdayWednesdayThursdaySummerDesignDay | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type1_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | FridaySaturday | No |  |  |  |  | --- | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type1_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type1_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type1_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | MondayTuesdayWednesdayThursday | No (the same as Type2_CLGSETP_SCH_NO_SETBACK) |  |  |  |  | --- | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type1_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | FridaySaturday | No (the same as Type2_CLGSETP_SCH_NO_SETBACK) |  |  |  |  | --- | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type1_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | No (the same as Type2_CLGSETP_SCH_NO_SETBACK) |  |  |  |  | --- | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type1_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | No (the same as Type2_CLGSETP_SCH_NO_SETBACK) |  |  |  |  | --- | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type2_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall | Type2_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall | Type2_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall | Type2_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | Cooling Set Point | All | Mon - Fri | RetailStripmall-Cooling Set Point-All-Mon - Fri | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type2_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | RetailStripmall | Cooling Set Point | All | Sat | RetailStripmall-Cooling Set Point-All-Sat | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type2_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | RetailStripmall | Cooling Set Point | All | Sun | RetailStripmall-Cooling Set Point-All-Sun | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type3_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44
RetailStripmall | Type3_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall | Type3_CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 26.67 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
RetailStripmall | Type3_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | No (the same as Type2_CLGSETP_SCH_NO_SETBACK) |  |  |  |  | --- | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type3_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | No (the same as Type2_CLGSETP_SCH_NO_SETBACK) |  |  |  |  | --- | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type3_CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | No (the same as Type2_CLGSETP_SCH_NO_SETBACK) |  |  |  |  | --- | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89 | 23.89
RetailStripmall | Type1_FAN_SCH | on/off | 2023-12-31 | MondayTuesdayWednesdayThursdaySummerDesignDay | Yes | RetailStripmall | HVAC | Type 1 Store | Mon - Thu | RetailStripmall-HVAC-Type 1 Store-Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type1_FAN_SCH | on/off | 2023-12-31 | FridaySaturdayWinterDesignDay | Yes | RetailStripmall | HVAC | Type 1 Store | Fri, Sat | RetailStripmall-HVAC-Type 1 Store-Fri, Sat | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type1_FAN_SCH | on/off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type1_FAN_SCH | on/off | 2023-12-31 | Sun | Yes | RetailStripmall | HVAC | Type 1 Store | Sun | RetailStripmall-HVAC-Type 1 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type2_FAN_SCH | on/off | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | HVAC | Type 2 Store | Mon - Fri | RetailStripmall-HVAC-Type 2 Store-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall | Type2_FAN_SCH | on/off | 2023-12-31 | Sat | Yes | RetailStripmall | HVAC | Type 2 Store | Sat | RetailStripmall-HVAC-Type 2 Store-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type2_FAN_SCH | on/off | 2023-12-31 | Sun | Yes | RetailStripmall | HVAC | Type 2 Store | Sun | RetailStripmall-HVAC-Type 2 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type3_FAN_SCH | on/off | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | HVAC | Type 3 Store | Mon - Fri | RetailStripmall-HVAC-Type 3 Store-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall | Type3_FAN_SCH | on/off | 2023-12-31 | Sat | Yes | RetailStripmall | HVAC | Type 3 Store | Sat | RetailStripmall-HVAC-Type 3 Store-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type3_FAN_SCH | on/off | 2023-12-31 | Sun | Yes | RetailStripmall | HVAC | Type 3 Store | Sun | RetailStripmall-HVAC-Type 3 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type1_MinOA_MotorizedDamper_SCH | fraction | 2023-12-31 | MondayTuesdayWednesdayThursdaySummerDesignDay | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type1_MinOA_MotorizedDamper_SCH | fraction | 2023-12-31 | FridaySaturdayWinterDesignDay | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type1_MinOA_MotorizedDamper_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type1_MinOA_MotorizedDamper_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Type3_MinOA_MotorizedDamper_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
RetailStripmall | Type3_MinOA_MotorizedDamper_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type3_MinOA_MotorizedDamper_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type1_SWH_SCH | Fraction | 2023-12-31 | MondayTuesdayWednesdayThursdaySummerDesignDay | Yes | RetailStripmall | SWH | Type 1 Store | Mon - Thu | RetailStripmall-SWH-Type 1 Store-Mon - Thu | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.62 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall | Type1_SWH_SCH | Fraction | 2023-12-31 | FridaySaturdayWinterDesignDay | Yes | RetailStripmall | SWH | Type 1 Store | Fri, Sat | RetailStripmall-SWH-Type 1 Store-Fri, Sat | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0.32 | 0.41 | 0.65 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall | Type1_SWH_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.23 | 0.32 | 0.41 | 0.65 | 0.6 | 0.55 | 0.45 | 0.5 | 0.46 | 0.47 | 0.34 | 0.33 | 0.23 | 0.13
RetailStripmall | Type1_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | SWH | Type 1 Store | Sun | RetailStripmall-SWH-Type 1 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.16 | 0.1
RetailStripmall | Type2_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | SWH | Type 2 Store | Mon - Fri | RetailStripmall-SWH-Type 2 Store-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0
RetailStripmall | Type2_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | SWH | Type 2 Store | Sat | RetailStripmall-SWH-Type 2 Store-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.62 | 0.6 | 0.5 | 0.48 | 0.47 | 0.34 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type2_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | SWH | Type 2 Store | Sun | RetailStripmall-SWH-Type 2 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.14 | 0.29 | 0.33 | 0.4 | 0.36 | 0.37 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type3_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | RetailStripmall | SWH | Type 3 Store | Mon - Fri | RetailStripmall-SWH-Type 3 Store-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.25 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0 | 0 | 0
RetailStripmall | Type3_SWH_SCH | Fraction | 2023-12-31 | Sat | Yes | RetailStripmall | SWH | Type 3 Store | Sat | RetailStripmall-SWH-Type 3 Store-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0 | 0 | 0 | 0 | 0
RetailStripmall | Type3_SWH_SCH | Fraction | 2023-12-31 | Sun | Yes | RetailStripmall | SWH | Type 3 Store | Sun | RetailStripmall-SWH-Type 3 Store-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | MinOA_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | MinOA_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | MinOA_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RetailStripmall | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RetailStripmall | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
RetailStripmall | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RetailStripmall | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RetailStripmall | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
RetailStripmall | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RetailStripmall | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RetailStripmall | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RetailStripmall | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
RetailStripmall | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RetailStripmall | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RetailStripmall | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
RetailStripmall | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RetailStripmall | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RetailStripmall | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
RetailStripmall | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
RetailStripmall | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | ltg_sch_gym | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolPrimary | Lighting | All (Study Periods) | Mon - Fri | SchoolPrimary-Lighting-All (Study Periods)-Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_gym | Fraction | 2023-06-30 | Sat | Yes | SchoolPrimary | Lighting | All (Study Periods) | Sat | SchoolPrimary-Lighting-All (Study Periods)-Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_gym | Fraction | 2023-06-30 | Sun | Yes | SchoolPrimary | Lighting | All (Study Periods) | Sun | SchoolPrimary-Lighting-All (Study Periods)-Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_gym | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolPrimary | Lighting | All (Summer Holiday) | Mon - Fri | SchoolPrimary-Lighting-All (Summer Holiday)-Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_gym | Fraction | 2023-09-01 | Sat | Yes | SchoolPrimary | Lighting | All (Summer Holiday) | Sat | SchoolPrimary-Lighting-All (Summer Holiday)-Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_gym | Fraction | 2023-09-01 | Sun | Yes | SchoolPrimary | Lighting | All (Summer Holiday) | Sun | SchoolPrimary-Lighting-All (Summer Holiday)-Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_gym | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_gym | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_gym | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_classroom | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_library | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_bath | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_kitchen | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_office | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_lobby | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_mechanical | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_computer_room | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_cafeteria | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | ltg_sch_corridor | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolPrimary | Electric Equipment | Others (Study Periods) | Mon - Fri | SchoolPrimary-Electric Equipment-Others (Study Periods)-Mon - Fri | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-06-30 | Sat | Yes | SchoolPrimary | Electric Equipment | Others (Study Periods) | Sat | SchoolPrimary-Electric Equipment-Others (Study Periods)-Sat | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-06-30 | Sun | Yes | SchoolPrimary | Electric Equipment | Others (Study Periods) | Sun | SchoolPrimary-Electric Equipment-Others (Study Periods)-Sun | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Mon - Fri | SchoolPrimary-Electric Equipment-Others (Summer Holiday)-Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-09-01 | Sat | Yes | SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Sat | SchoolPrimary-Electric Equipment-Others (Summer Holiday)-Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-09-01 | Sun | Yes | SchoolPrimary | Electric Equipment | Others (Summer Holiday) | Sun | SchoolPrimary-Electric Equipment-Others (Summer Holiday)-Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-09-01 | Mon - Fri | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-09-01 | Sat | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-09-01 | Sun | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Mon - Fri | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-06-30 | Sat | Yes | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sat | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-06-30 | Sun | Yes | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sun | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Mon - Fri | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-09-01 | Sat | Yes | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sat | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-09-01 | Sun | Yes | SchoolPrimary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sun | SchoolPrimary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolPrimary | Gas Equipment | Kitchen | Mon - Fri | SchoolPrimary-Gas Equipment-Kitchen-Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-06-30 | Sat | Yes | SchoolPrimary | Gas Equipment | Kitchen | Sat | SchoolPrimary-Gas Equipment-Kitchen-Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-06-30 | Sun | Yes | SchoolPrimary | Gas Equipment | Kitchen | Sun | SchoolPrimary-Gas Equipment-Kitchen-Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-09-01 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-09-01 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-09-01 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-06-15 | Mon - Fri | Yes | SchoolPrimary | Occupants | Others (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Others (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-06-15 | Sat | Yes | SchoolPrimary | Occupants | Others (Study Periods) | Sat | SchoolPrimary-Occupants-Others (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-06-15 | Sun | Yes | SchoolPrimary | Occupants | Others (Study Periods) | Sun | SchoolPrimary-Occupants-Others (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-09-15 | Mon - Fri | Yes | SchoolPrimary | Occupants | Others (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Others (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-09-15 | Sat | Yes | SchoolPrimary | Occupants | Others (Summer Holiday) | Sat | SchoolPrimary-Occupants-Others (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-09-15 | Sun | Yes | SchoolPrimary | Occupants | Others (Summer Holiday) | Sun | SchoolPrimary-Occupants-Others (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Computer Classroom (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-06-30 | Sat | Yes | SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Sat | SchoolPrimary-Occupants-Computer Classroom (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-06-30 | Sun | Yes | SchoolPrimary | Occupants | Computer Classroom (Study Periods) | Sun | SchoolPrimary-Occupants-Computer Classroom (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Computer Classroom (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-09-01 | Sat | Yes | SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Sat | SchoolPrimary-Occupants-Computer Classroom (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-09-01 | Sun | Yes | SchoolPrimary | Occupants | Computer Classroom (Summer Holiday) | Sun | SchoolPrimary-Occupants-Computer Classroom (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Extend | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-09-01 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-09-01 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-09-01 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolPrimary | Occupants | Office (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Office (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-06-30 | Sat | Yes | SchoolPrimary | Occupants | Office (Study Periods) | Sat | SchoolPrimary-Occupants-Office (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-06-30 | Sun | Yes | SchoolPrimary | Occupants | Office (Study Periods) | Sun | SchoolPrimary-Occupants-Office (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolPrimary | Occupants | Office (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Office (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-09-01 | Sat | Yes | SchoolPrimary | Occupants | Office (Summer Holiday) | Sat | SchoolPrimary-Occupants-Office (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-09-01 | Sun | Yes | SchoolPrimary | Occupants | Office (Summer Holiday) | Sun | SchoolPrimary-Occupants-Office (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolPrimary | Occupants | Gym (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Gym (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-06-30 | Sat | Yes | SchoolPrimary | Occupants | Gym (Study Periods) | Sat | SchoolPrimary-Occupants-Gym (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-06-30 | Sun | Yes | SchoolPrimary | Occupants | Gym (Study Periods) | Sun | SchoolPrimary-Occupants-Gym (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolPrimary | Occupants | Gym (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Gym (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-09-01 | Sat | Yes | SchoolPrimary | Occupants | Gym (Summer Holiday) | Sat | SchoolPrimary-Occupants-Gym (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-09-01 | Sun | Yes | SchoolPrimary | Occupants | Gym (Summer Holiday) | Sun | SchoolPrimary-Occupants-Gym (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Gym | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolPrimary | Occupants | Cafeteria (Study Periods) | Mon - Fri | SchoolPrimary-Occupants-Cafeteria (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-06-30 | Sat | Yes | SchoolPrimary | Occupants | Cafeteria (Study Periods) | Sat | SchoolPrimary-Occupants-Cafeteria (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-06-30 | Sun | Yes | SchoolPrimary | Occupants | Cafeteria (Study Periods) | Sun | SchoolPrimary-Occupants-Cafeteria (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Mon - Fri | SchoolPrimary-Occupants-Cafeteria (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-09-01 | Sat | Yes | SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Sat | SchoolPrimary-Occupants-Cafeteria (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-09-01 | Sun | Yes | SchoolPrimary | Occupants | Cafeteria (Summer Holiday) | Sun | SchoolPrimary-Occupants-Cafeteria (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | INFIL_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
SchoolPrimary | INFIL_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
SchoolPrimary | INFIL_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1
SchoolPrimary | INFIL_SCH_PNNL | fraction | 2023-12-31 | Mon - Fri | Yes | SchoolPrimary | Infiltration | All | Mon - Fri | SchoolPrimary-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolPrimary | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sat | Yes | SchoolPrimary | Infiltration | All | Sat | SchoolPrimary-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sun | Yes | SchoolPrimary | Infiltration | All | Sun | SchoolPrimary-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
SchoolPrimary | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
SchoolPrimary | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-06-15 | Mon - Fri | Yes | SchoolPrimary | SWH | All (Study Periods) | Mon - Fri | SchoolPrimary-SWH-All (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-06-15 | Sat | Yes | SchoolPrimary | SWH | All (Study Periods) | Sat | SchoolPrimary-SWH-All (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-06-15 | Sun | Yes | SchoolPrimary | SWH | All (Study Periods) | Sun | SchoolPrimary-SWH-All (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-09-15 | Mon - Fri | Yes | SchoolPrimary | SWH | All (Summer Holiday) | Mon - Fri | SchoolPrimary-SWH-All (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-09-15 | Sat | Yes | SchoolPrimary | SWH | All (Summer Holiday) | Sat | SchoolPrimary-SWH-All (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-09-15 | Sun | Yes | SchoolPrimary | SWH | All (Summer Holiday) | Sun | SchoolPrimary-SWH-All (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | ALWAYS_ON | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | ALWAYS_ON | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | ALWAYS_ON | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolPrimary | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolPrimary | PlantOnSched | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | PlantOnSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | PlantOnSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SchoolPrimary | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SchoolPrimary | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-03-31 | Mon - Fri | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-03-31 | Sat | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-03-31 | Sun | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-09-30 | Sat | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-09-30 | Sun | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolPrimary | VAV-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
SchoolPrimary | VAV-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
SchoolPrimary | VAV-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
SchoolPrimary | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
SchoolPrimary | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
SchoolPrimary | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-09-01 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-09-01 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-09-01 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Hours_of_operation | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary | Hours_of_operation | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Hours_of_operation | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | HVACOperationSchd | On/Off | 2023-12-31 | Mon - Fri | Yes | SchoolPrimary | HVAC | All | Mon - Fri | SchoolPrimary-HVAC-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary | HVACOperationSchd | On/Off | 2023-12-31 | Sat | Yes | SchoolPrimary | HVAC | All | Sat | SchoolPrimary-HVAC-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | HVACOperationSchd | On/Off | 2023-12-31 | Sun | Yes | SchoolPrimary | HVAC | All | Sun | SchoolPrimary-HVAC-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolPrimary | Heating Set Point | Others | Mon - Fri | SchoolPrimary-Heating Set Point-Others-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | SchoolPrimary | Heating Set Point | Others | Sat | SchoolPrimary-Heating Set Point-Others-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | SchoolPrimary | Heating Set Point | Others | Sun | SchoolPrimary-Heating Set Point-Others-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_Setback | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Mon - Fri | SchoolPrimary-Heating Set Point-Mechanical Room, Bathroom-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_Setback | Temperature | 2023-12-31 | Sat | Yes | SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Sat | SchoolPrimary-Heating Set Point-Mechanical Room, Bathroom-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_Setback | Temperature | 2023-12-31 | Sun | Yes | SchoolPrimary | Heating Set Point | Mechanical Room, Bathroom | Sun | SchoolPrimary-Heating Set Point-Mechanical Room, Bathroom-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_1 | Temperature | 2023-12-31 | Mon - Fri | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_1 | Temperature | 2023-12-31 | Sat | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_1 | Temperature | 2023-12-31 | Sun | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_2 | Temperature | 2023-12-31 | Mon - Fri | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_2 | Temperature | 2023-12-31 | Sat | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_2 | Temperature | 2023-12-31 | Sun | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_3 | Temperature | 2023-12-31 | Mon - Fri | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_3 | Temperature | 2023-12-31 | Sat | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_POD_3 | Temperature | 2023-12-31 | Sun | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_OTHER | Temperature | 2023-12-31 | Mon - Fri | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_OTHER | Temperature | 2023-12-31 | Sat | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | HTGSETP_SCH_VAV_OTHER | Temperature | 2023-12-31 | Sun | No (the same as HTGSETP_SCH_NO_OPTIMUM) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolPrimary | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Mon - Fri | SchoolPrimary-Cooling Set Point-Gym, Kitchen, Cafeteria-Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Sat | SchoolPrimary-Cooling Set Point-Gym, Kitchen, Cafeteria-Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | SchoolPrimary | Cooling Set Point | Gym, Kitchen, Cafeteria | Sun | SchoolPrimary-Cooling Set Point-Gym, Kitchen, Cafeteria-Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 25.6 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_YES_OPTIMUM_original | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_1 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_1 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_1 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_2 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_2 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_2 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_3 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_3 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_POD_3 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_OTHER | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_OTHER | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_VAV_OTHER | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolPrimary | Cooling Set Point | Others | Mon - Fri | SchoolPrimary-Cooling Set Point-Others-Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | SchoolPrimary | Cooling Set Point | Others | Sat | SchoolPrimary-Cooling Set Point-Others-Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | SchoolPrimary | Cooling Set Point | Others | Sun | SchoolPrimary-Cooling Set Point-Others-Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolPrimary | CLGSETP_SCH_Setup | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Mon - Fri | SchoolPrimary-Cooling Set Point-Mechanical Room, Bathroom-Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_Setup | Temperature | 2023-12-31 | Sat | Yes | SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Sat | SchoolPrimary-Cooling Set Point-Mechanical Room, Bathroom-Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | CLGSETP_SCH_Setup | Temperature | 2023-12-31 | Sun | Yes | SchoolPrimary | Cooling Set Point | Mechanical Room, Bathroom | Sun | SchoolPrimary-Cooling Set Point-Mechanical Room, Bathroom-Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SchoolPrimary | MinOA_Sched | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | MinOA_Sched | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | MinOA_Sched | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | MinOA_MotorizedDamper_Sched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolPrimary | MinOA_MotorizedDamper_Sched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | MinOA_MotorizedDamper_Sched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | MinOA_Kitchen_Sched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | MinOA_Kitchen_Sched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | MinOA_Kitchen_Sched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SchoolPrimary | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SchoolPrimary | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolPrimary | Bath_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolPrimary | Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | TuesdayFriday | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolPrimary | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolPrimary | Bath_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Bath_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Bath_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-09-01 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-09-01 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-09-01 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolPrimary | Kitchen Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | ltg_sch_gym | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Lighting | All (Study Periods) | Mon - Fri | SchoolSecondary-Lighting-All (Study Periods)-Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_gym | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Lighting | All (Study Periods) | Sat | SchoolSecondary-Lighting-All (Study Periods)-Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_gym | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Lighting | All (Study Periods) | Sun | SchoolSecondary-Lighting-All (Study Periods)-Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_gym | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolSecondary | Lighting | All (Summer Holiday) | Mon - Fri | SchoolSecondary-Lighting-All (Summer Holiday)-Mon - Fri | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_gym | Fraction | 2023-09-01 | Sat | Yes | SchoolSecondary | Lighting | All (Summer Holiday) | Sat | SchoolSecondary-Lighting-All (Summer Holiday)-Sat | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_gym | Fraction | 2023-09-01 | Sun | Yes | SchoolSecondary | Lighting | All (Summer Holiday) | Sun | SchoolSecondary-Lighting-All (Summer Holiday)-Sun | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_gym | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_gym | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_gym | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_classroom | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_library | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_bath | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_auditorium | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_kitchen | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_office | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_lobby | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_cafeteria | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_mechanical | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-06-30 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-06-30 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-06-30 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-09-01 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-09-01 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-09-01 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | ltg_sch_corridor | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_gym) |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Electric Equipment | Others (Study Periods) | Mon - Fri | SchoolSecondary-Electric Equipment-Others (Study Periods)-Mon - Fri | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Electric Equipment | Others (Study Periods) | Sat | SchoolSecondary-Electric Equipment-Others (Study Periods)-Sat | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Electric Equipment | Others (Study Periods) | Sun | SchoolSecondary-Electric Equipment-Others (Study Periods)-Sun | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Mon - Fri | SchoolSecondary-Electric Equipment-Others (Summer Holiday)-Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-09-01 | Sat | Yes | SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Sat | SchoolSecondary-Electric Equipment-Others (Summer Holiday)-Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-09-01 | Sun | Yes | SchoolSecondary | Electric Equipment | Others (Summer Holiday) | Sun | SchoolSecondary-Electric Equipment-Others (Summer Holiday)-Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | BLDG_EQUIP_SCH | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Mon - Fri | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sat | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Study Periods) | Sun | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Study Periods)-Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Mon - Fri | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-09-01 | Sat | Yes | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sat | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-09-01 | Sun | Yes | SchoolSecondary | Electric Equipment | Kitchen, Cafeteria (Summer Holiday) | Sun | SchoolSecondary-Electric Equipment-Kitchen, Cafeteria (Summer Holiday)-Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.15 | 0.15 | 0.25 | 0.25 | 0.25 | 0.15 | 0.15 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_ELEC_EQUIP_SCH | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Gas Equipment | Kitchen | Mon - Fri | SchoolSecondary-Gas Equipment-Kitchen-Mon - Fri | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Gas Equipment | Kitchen | Sat | SchoolSecondary-Gas Equipment-Kitchen-Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Gas Equipment | Kitchen | Sun | SchoolSecondary-Gas Equipment-Kitchen-Sun | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-09-01 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-09-01 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-09-01 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.15 | 0.15 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Sat | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | KITCHEN_GAS_EQUIP_SCH | Fraction | 2023-12-31 | Sun | No (the same as 30-Jun) |  |  |  |  | --- | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
SchoolSecondary | BLDG_ELEVATORS | Fraction | 2023-12-31 | Mon - Fri | Yes | SchoolSecondary | Elevator | All | Mon - Fri | SchoolSecondary-Elevator-All-Mon - Fri | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sat | Yes | SchoolSecondary | Elevator | All | Sat | SchoolSecondary-Elevator-All-Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | BLDG_ELEVATORS | Fraction | 2023-12-31 | Sun | Yes | SchoolSecondary | Elevator | All | Sun | SchoolSecondary-Elevator-All-Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
SchoolSecondary | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | ELEV_LIGHT_FAN_SCH_24_7 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-06-15 | Mon - Fri | Yes | SchoolSecondary | Occupants | Others (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Others (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-06-15 | Sat | Yes | SchoolSecondary | Occupants | Others (Study Periods) | Sat | SchoolSecondary-Occupants-Others (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-06-15 | Sun | Yes | SchoolSecondary | Occupants | Others (Study Periods) | Sun | SchoolSecondary-Occupants-Others (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-09-15 | Mon - Fri | Yes | SchoolSecondary | Occupants | Others (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Others (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-09-15 | Sat | Yes | SchoolSecondary | Occupants | Others (Summer Holiday) | Sat | SchoolSecondary-Occupants-Others (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-09-15 | Sun | Yes | SchoolSecondary | Occupants | Others (Summer Holiday) | Sun | SchoolSecondary-Occupants-Others (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Sat | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods) | Sun | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-09-01 | Sat | Yes | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Sat | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-09-01 | Sun | Yes | SchoolSecondary | Occupants | Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday) | Sun | SchoolSecondary-Occupants-Mult_Class_1_Pod_3_ZN_1_FLR_2, Mult_Class_2_Pod_3_ZN_1_FLR_2 (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-12-31 | Mon - Fri | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-12-31 | Sat | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Extend | Fraction | 2023-12-31 | Sun | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-09-01 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-09-01 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-09-01 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Occupants | Office (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Office (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Occupants | Office (Study Periods) | Sat | SchoolSecondary-Occupants-Office (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Occupants | Office (Study Periods) | Sun | SchoolSecondary-Occupants-Office (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolSecondary | Occupants | Office (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Office (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-09-01 | Sat | Yes | SchoolSecondary | Occupants | Office (Summer Holiday) | Sat | SchoolSecondary-Occupants-Office (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-09-01 | Sun | Yes | SchoolSecondary | Occupants | Office (Summer Holiday) | Sun | SchoolSecondary-Occupants-Office (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-12-31 | Mon - Fri | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0.95 | 0 | 0.95 | 0.95 | 0.15 | 0.15 | 0.15 | 0.15 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-12-31 | Sat | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Offices_w_SB | Fraction | 2023-12-31 | Sun | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Occupants | Gym (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Gym (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Occupants | Gym (Study Periods) | Sat | SchoolSecondary-Occupants-Gym (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Occupants | Gym (Study Periods) | Sun | SchoolSecondary-Occupants-Gym (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolSecondary | Occupants | Gym (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Gym (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-09-01 | Sat | Yes | SchoolSecondary | Occupants | Gym (Summer Holiday) | Sat | SchoolSecondary-Occupants-Gym (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-09-01 | Sun | Yes | SchoolSecondary | Occupants | Gym (Summer Holiday) | Sun | SchoolSecondary-Occupants-Gym (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-12-31 | Mon - Fri | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-12-31 | Sat | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Gym | Fraction | 2023-12-31 | Sun | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Occupants | Auditorium (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Auditorium (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Occupants | Auditorium (Study Periods) | Sat | SchoolSecondary-Occupants-Auditorium (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Occupants | Auditorium (Study Periods) | Sun | SchoolSecondary-Occupants-Auditorium (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Auditorium (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-09-01 | Sat | Yes | SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Sat | SchoolSecondary-Occupants-Auditorium (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-09-01 | Sun | Yes | SchoolSecondary | Occupants | Auditorium (Summer Holiday) | Sun | SchoolSecondary-Occupants-Auditorium (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-12-31 | Mon - Fri | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-12-31 | Sat | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Auditorium | Fraction | 2023-12-31 | Sun | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-06-30 | Mon - Fri | Yes | SchoolSecondary | Occupants | Cafeteria (Study Periods) | Mon - Fri | SchoolSecondary-Occupants-Cafeteria (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-06-30 | Sat | Yes | SchoolSecondary | Occupants | Cafeteria (Study Periods) | Sat | SchoolSecondary-Occupants-Cafeteria (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-06-30 | Sun | Yes | SchoolSecondary | Occupants | Cafeteria (Study Periods) | Sun | SchoolSecondary-Occupants-Cafeteria (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-09-01 | Mon - Fri | Yes | SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Mon - Fri | SchoolSecondary-Occupants-Cafeteria (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.35 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-09-01 | Sat | Yes | SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Sat | SchoolSecondary-Occupants-Cafeteria (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-09-01 | Sun | Yes | SchoolSecondary | Occupants | Cafeteria (Summer Holiday) | Sun | SchoolSecondary-Occupants-Cafeteria (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-12-31 | Mon - Fri | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-12-31 | Sat | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_OCC_SCH_Cafeteria | Fraction | 2023-12-31 | Sun | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | INFIL_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolSecondary | INFIL_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolSecondary | INFIL_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolSecondary | INFIL_SCH_PNNL | fraction | 2023-12-31 | Mon - Fri | Yes | SchoolSecondary | Infiltration | All | Mon - Fri | SchoolSecondary-Infiltration-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
SchoolSecondary | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sat | Yes | SchoolSecondary | Infiltration | All | Sat | SchoolSecondary-Infiltration-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | INFIL_SCH_PNNL | fraction | 2023-12-31 | Sun | Yes | SchoolSecondary | Infiltration | All | Sun | SchoolSecondary-Infiltration-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 1 | 0.144 | 0.144 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Booster Water Inlet Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
SchoolSecondary | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
SchoolSecondary | Booster Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22 | 82.22
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-06-15 | Mon - Fri | Yes | SchoolSecondary | SWH | All (Study Periods) | Mon - Fri | SchoolSecondary-SWH-All (Study Periods)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-06-15 | Sat | Yes | SchoolSecondary | SWH | All (Study Periods) | Sat | SchoolSecondary-SWH-All (Study Periods)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-06-15 | Sun | Yes | SchoolSecondary | SWH | All (Study Periods) | Sun | SchoolSecondary-SWH-All (Study Periods)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-09-15 | Mon - Fri | Yes | SchoolSecondary | SWH | All (Summer Holiday) | Mon - Fri | SchoolSecondary-SWH-All (Summer Holiday)-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-09-15 | Sat | Yes | SchoolSecondary | SWH | All (Summer Holiday) | Sat | SchoolSecondary-SWH-All (Summer Holiday)-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-09-15 | Sun | Yes | SchoolSecondary | SWH | All (Summer Holiday) | Sun | SchoolSecondary-SWH-All (Summer Holiday)-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-12-31 | Mon - Fri | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34 | 0.6 | 0.63 | 0.72 | 0.79 | 0.83 | 0.61 | 0.65 | 0.1 | 0.1 | 0.19 | 0.25 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sat | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | BLDG_SWH_SCH | Fraction | 2023-12-31 | Sun | No (the same as 15-Jun) |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | ALWAYS_ON | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | ALWAYS_ON | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | ALWAYS_ON | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | WORK_EFF_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | WORK_EFF_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | WORK_EFF_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | AIR_VELO_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | AIR_VELO_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | AIR_VELO_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-04-30 | Mon - Fri | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-04-30 | Sat | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-04-30 | Sun | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-09-30 | Sat | No |  |  |  |  | --- | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-09-30 | Sun | No |  |  |  |  | --- | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolSecondary | CLOTHING_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
SchoolSecondary | PlantOnSched | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | PlantOnSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | PlantOnSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | FAN_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | FAN_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | FAN_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SchoolSecondary | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SchoolSecondary | Dual Zone Control Type Sched | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-03-31 | Mon - Fri | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-03-31 | Sat | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-03-31 | Sun | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-09-30 | Mon - Fri | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-09-30 | Sat | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-09-30 | Sun | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
SchoolSecondary | VAV-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
SchoolSecondary | VAV-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
SchoolSecondary | VAV-Supply-Air-Temp-Sch | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8
SchoolSecondary | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
SchoolSecondary | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
SchoolSecondary | CW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
SchoolSecondary | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
SchoolSecondary | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
SchoolSecondary | HW-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-09-01 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-09-01 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-09-01 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_Exhaust_SCH | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Hours_of_operation | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary | Hours_of_operation | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Hours_of_operation | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | HVACOperationSchd | On/Off | 2023-12-31 | Mon - Fri | Yes | SchoolSecondary | HVAC | All | Mon - Fri | SchoolSecondary-HVAC-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary | HVACOperationSchd | On/Off | 2023-12-31 | Sat | Yes | SchoolSecondary | HVAC | All | Sat | SchoolSecondary-HVAC-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | HVACOperationSchd | On/Off | 2023-12-31 | Sun | Yes | SchoolSecondary | HVAC | All | Sun | SchoolSecondary-HVAC-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolSecondary | Heating Set Point | Others | Mon - Fri | SchoolSecondary-Heating Set Point-Others-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | Yes | SchoolSecondary | Heating Set Point | Others | Sat | SchoolSecondary-Heating Set Point-Others-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | Yes | SchoolSecondary | Heating Set Point | Others | Sun | SchoolSecondary-Heating Set Point-Others-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_Yes_Optimum_Original | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 17.8 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_Yes_Optimum_Original | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_Yes_Optimum_Original | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_Setback | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Mon - Fri | SchoolSecondary-Heating Set Point-Bathrooms, Mechanical Rooms-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_Setback | Temperature | 2023-12-31 | Sat | Yes | SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Sat | SchoolSecondary-Heating Set Point-Bathrooms, Mechanical Rooms-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_Setback | Temperature | 2023-12-31 | Sun | Yes | SchoolSecondary | Heating Set Point | Bathrooms, Mechanical Rooms | Sun | SchoolSecondary-Heating Set Point-Bathrooms, Mechanical Rooms-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_5_9 | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Mon - Fri | SchoolSecondary-Heating Set Point-Gym, Auditorium, Kitchen, Cafeteria-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_5_9 | Temperature | 2023-12-31 | Sat | Yes | SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Sat | SchoolSecondary-Heating Set Point-Gym, Auditorium, Kitchen, Cafeteria-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_5_9 | Temperature | 2023-12-31 | Sun | Yes | SchoolSecondary | Heating Set Point | Gym, Auditorium, Kitchen, Cafeteria | Sun | SchoolSecondary-Heating Set Point-Gym, Auditorium, Kitchen, Cafeteria-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_4_8 | Temperature | 2023-12-31 | Mon - Fri | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_4_8 | Temperature | 2023-12-31 | Sat | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_4_8 | Temperature | 2023-12-31 | Sun | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_3_7 | Temperature | 2023-12-31 | Mon - Fri | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_3_7 | Temperature | 2023-12-31 | Sat | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_3_7 | Temperature | 2023-12-31 | Sun | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_2_6 | Temperature | 2023-12-31 | Mon - Fri | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_2_6 | Temperature | 2023-12-31 | Sat | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_2_6 | Temperature | 2023-12-31 | Sun | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_1_5 | Temperature | 2023-12-31 | Mon - Fri | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_1_5 | Temperature | 2023-12-31 | Sat | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | HTGSETP_SCH_PSZ_AC_1_5 | Temperature | 2023-12-31 | Sun | No (the same as HTGSETP_SCH_PSZ_AC_5_9) |  |  |  |  | --- | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
SchoolSecondary | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_NO_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_YES_OPTIMUM | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_YES_OPTIMUM_STARTSTOP | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_Yes_Optimum_Original | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 27.8 | 25.6 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_Yes_Optimum_Original | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_Yes_Optimum_Original | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolSecondary | Cooling Set Point | Others | Mon - Fri | SchoolSecondary-Cooling Set Point-Others-Mon - Fri | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sat | Yes | SchoolSecondary | Cooling Set Point | Others | Sat | SchoolSecondary-Cooling Set Point-Others-Sat | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | CLGSETP_SCH_NO_SETBACK | Temperature | 2023-12-31 | Sun | Yes | SchoolSecondary | Cooling Set Point | Others | Sun | SchoolSecondary-Cooling Set Point-Others-Sun | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
SchoolSecondary | CLGSETP_SCH_Setup | Temperature | 2023-12-31 | Mon - Fri | Yes | SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Mon - Fri | SchoolSecondary-Cooling Set Point-Bathrooms, Mechanical Rooms-Mon - Fri | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_Setup | Temperature | 2023-12-31 | Sat | Yes | SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Sat | SchoolSecondary-Cooling Set Point-Bathrooms, Mechanical Rooms-Sat | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_Setup | Temperature | 2023-12-31 | Sun | Yes | SchoolSecondary | Cooling Set Point | Bathrooms, Mechanical Rooms | Sun | SchoolSecondary-Cooling Set Point-Bathrooms, Mechanical Rooms-Sun | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_5_9 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_5_9 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_5_9 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_4_8 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_4_8 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_4_8 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_3_7 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_3_7 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_3_7 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_2_6 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_2_6 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_2_6 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_1_5 | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_1_5 | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | CLGSETP_SCH_PSZ_AC_1_5 | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44 | 29.44
SchoolSecondary | MinOA_Sched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | MinOA_Sched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | MinOA_Sched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | MinOA_MotorizedDamper_Sched | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
SchoolSecondary | MinOA_MotorizedDamper_Sched | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | MinOA_MotorizedDamper_Sched | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | ACTIVITY_SCH | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SchoolSecondary | ACTIVITY_SCH | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SchoolSecondary | ACTIVITY_SCH | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Bathrooms_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Bathrooms_ZN_1_FLR_2 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Latent fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Sensible fract sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Kitchen_ZN_1_FLR_1 SHW_default Hot Supply Temp Sched | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | ON/OFF | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | ON/OFF | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | TuesdayFriday | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | SHWSys1-Loop-Temp-Schedule | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-09-01 | Mon - Fri | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-09-01 | Sat | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-09-01 | Sun | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | walkin_occ_lght_SCH_1 | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773 | 0.1773
SchoolSecondary | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
SchoolSecondary | Bathrooms_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Bathrooms_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Bathrooms_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Bathrooms_ZN_1_FLR_2 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Bathrooms_ZN_1_FLR_2 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Bathrooms_ZN_1_FLR_2 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-06-30 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-06-30 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-06-30 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-09-01 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-09-01 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-09-01 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SchoolSecondary | Kitchen_ZN_1_FLR_1 Exhaust Fan Balanced Exhaust Fraction Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | ltg_sch_office | Fraction | 2023-12-31 | Mon - Fri | Yes | Warehouse | Lighting | Office | Mon - Fri | Warehouse-Lighting-Office-Mon - Fri | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | ltg_sch_office | Fraction | 2023-12-31 | Sat | Yes | Warehouse | Lighting | Office | Sat | Warehouse-Lighting-Office-Sat | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.23 | 0.42 | 0.77 | 0.77 | 0.77 | 0.77 | 0.68 | 0.77 | 0.77 | 0.77 | 0.77 | 0.61 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | ltg_sch_office | Fraction | 2023-12-31 | Sun | Yes | Warehouse | Lighting | Office | Sun | Warehouse-Lighting-Office-Sun | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18 | 0.18
Warehouse | ltg_sch_bulk_storage | Fraction | 2023-12-31 | Mon - Fri | Yes | Warehouse | Lighting | Fine Sorage, Bulk Storage | Mon - Fri | Warehouse-Lighting-Fine Sorage, Bulk Storage-Mon - Fri | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | ltg_sch_bulk_storage | Fraction | 2023-12-31 | Sat | Yes | Warehouse | Lighting | Fine Sorage, Bulk Storage | Sat | Warehouse-Lighting-Fine Sorage, Bulk Storage-Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | ltg_sch_bulk_storage | Fraction | 2023-12-31 | Sun | Yes | Warehouse | Lighting | Fine Sorage, Bulk Storage | Sun | Warehouse-Lighting-Fine Sorage, Bulk Storage-Sun | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | ltg_sch_fine_storage | Fraction | 2023-12-31 | Mon - Fri | No (the same as ltg_sch_bulk_storage) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | ltg_sch_fine_storage | Fraction | 2023-12-31 | Sat | No (the same as ltg_sch_bulk_storage) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.6 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.6 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | ltg_sch_fine_storage | Fraction | 2023-12-31 | Sun | No (the same as ltg_sch_bulk_storage) |  |  |  |  | --- | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Warehouse | Office_Plug_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | Warehouse | Electric Equipment | Office | Mon - Fri | Warehouse-Electric Equipment-Office-Mon - Fri | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Office_Plug_SCH | Fraction | 2023-12-31 | Sat | Yes | Warehouse | Electric Equipment | Office | Sat | Warehouse-Electric Equipment-Office-Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Office_Plug_SCH | Fraction | 2023-12-31 | Sun | Yes | Warehouse | Electric Equipment | Office | Sun | Warehouse-Electric Equipment-Office-Sun | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Warehouse | Bulk Storage Plug Schedule | Fraction | 2023-12-31 | Mon - Fri | Yes | Warehouse | Electric Equipment | Bulk Storage | Mon - Fri | Warehouse-Electric Equipment-Bulk Storage-Mon - Fri | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Warehouse | Bulk Storage Plug Schedule | Fraction | 2023-12-31 | Sat | Yes | Warehouse | Electric Equipment | Bulk Storage | Sat | Warehouse-Electric Equipment-Bulk Storage-Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Warehouse | Bulk Storage Plug Schedule | Fraction | 2023-12-31 | Sun | Yes | Warehouse | Electric Equipment | Bulk Storage | Sun | Warehouse-Electric Equipment-Bulk Storage-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | BLDG_OCC_SCH | Fraction | 2023-12-31 | Mon - Fri | Yes | Warehouse | Occupants | All | Mon - Fri | Warehouse-Occupants-All-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sat | Yes | Warehouse | Occupants | All | Sat | Warehouse-Occupants-All-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.21 | 1 | 1 | 1 | 1 | 0.53 | 1 | 1 | 1 | 1 | 0.32 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | BLDG_OCC_SCH | Fraction | 2023-12-31 | Sun | Yes | Warehouse | Occupants | All | Sun | Warehouse-Occupants-All-Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Office Activity Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | Office Activity Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | Office Activity Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | FanSched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | FanSched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | FanSched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | MinOA_MotorizedDamper_Sched | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Office Heating Schedule | Temperature | 2023-12-31 | Mon - Fri | Yes | Warehouse | Heating Set Point | Office | Mon - Fri | Warehouse-Heating Set Point-Office-Mon - Fri | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Office Heating Schedule | Temperature | 2023-12-31 | Sat | Yes | Warehouse | Heating Set Point | Office | Sat | Warehouse-Heating Set Point-Office-Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Office Heating Schedule | Temperature | 2023-12-31 | Sun | Yes | Warehouse | Heating Set Point | Office | Sun | Warehouse-Heating Set Point-Office-Sun | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
Warehouse | Office Cooling Schedule | Temperature | 2023-12-31 | Mon - Fri | Yes | Warehouse | Cooling Set Point | Office | Mon - Fri | Warehouse-Cooling Set Point-Office-Mon - Fri | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
Warehouse | Office Cooling Schedule | Temperature | 2023-12-31 | Sat | Yes | Warehouse | Cooling Set Point | Office | Sat | Warehouse-Cooling Set Point-Office-Sat | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9
Warehouse | Office Cooling Schedule | Temperature | 2023-12-31 | Sun | Yes | Warehouse | Cooling Set Point | Office | Sun | Warehouse-Cooling Set Point-Office-Sun | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
Warehouse | Bulk Storage Heating Setpoint Schedule | Temperature | 2023-12-31 | Mon - Fri | Yes | Warehouse | Heating Set Point | Bulk Storage | Mon - Fri | Warehouse-Heating Set Point-Bulk Storage-Mon - Fri | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Warehouse | Bulk Storage Heating Setpoint Schedule | Temperature | 2023-12-31 | Sat | Yes | Warehouse | Heating Set Point | Bulk Storage | Sat | Warehouse-Heating Set Point-Bulk Storage-Sat | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Warehouse | Bulk Storage Heating Setpoint Schedule | Temperature | 2023-12-31 | Sun | Yes | Warehouse | Heating Set Point | Bulk Storage | Sun | Warehouse-Heating Set Point-Bulk Storage-Sun | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Warehouse | ZoneControlSchedule | Control Type | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | ZoneControlSchedule | Control Type | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | ZoneControlSchedule | Control Type | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Office DHW Schedule | Fraction | 2023-12-31 | Mon - Fri | Yes | Warehouse | SWH | Office | Mon - Fri | Warehouse-SWH-Office-Mon - Fri | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.101 | 0.399 | 0.501 | 0.501 | 0.696 | 0.9 | 0.798 | 0.696 | 0.798 | 0.297 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Office DHW Schedule | Fraction | 2023-12-31 | Sat | Yes | Warehouse | SWH | Office | Sat | Warehouse-SWH-Office-Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.101 | 0.399 | 0.501 | 0.501 | 0.696 | 0.9 | 0.798 | 0.696 | 0.798 | 0.297 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Office DHW Schedule | Fraction | 2023-12-31 | Sun | Yes | Warehouse | SWH | Office | Sun | Warehouse-SWH-Office-Sun | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015
Warehouse | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Warehouse | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Warehouse | Hot Water Setpoint Temp Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Warehouse | ALWAYS_ON | On/Off | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | ALWAYS_ON | On/Off | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | ALWAYS_ON | On/Off | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Exterior_Lgt_ALWAYS_ON | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Always Off Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Always Off Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | Always Off Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Mon - Fri | Yes | Warehouse | HVAC | All | Mon - Fri | Warehouse-HVAC-All-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Sat | Yes | Warehouse | HVAC | All | Sat | Warehouse-HVAC-All-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | COMPACT HVAC-ALWAYS 1 | COMPACT HVAC Any Number | 2023-12-31 | Sun | Yes | Warehouse | HVAC | All | Sun | Warehouse-HVAC-All-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | COMPACT HVAC-ALWAYS 4 | COMPACT HVAC Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Warehouse | COMPACT HVAC-ALWAYS 4 | COMPACT HVAC Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Warehouse | COMPACT HVAC-ALWAYS 4 | COMPACT HVAC Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Warehouse | Fine Storage Heating Setpoint Schedule | Temperature | 2023-12-31 | Mon - Fri | Yes | Warehouse | Heating Set Point | Fine Sorage | Mon - Fri | Warehouse-Heating Set Point-Fine Sorage-Mon - Fri | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Fine Storage Heating Setpoint Schedule | Temperature | 2023-12-31 | Sat | Yes | Warehouse | Heating Set Point | Fine Sorage | Sat | Warehouse-Heating Set Point-Fine Sorage-Sat | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Fine Storage Heating Setpoint Schedule | Temperature | 2023-12-31 | Sun | Yes | Warehouse | Heating Set Point | Fine Sorage | Sun | Warehouse-Heating Set Point-Fine Sorage-Sun | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56 | 15.56
Warehouse | Fine Storage Cooling Setpoint Schedule | Temperature | 2023-12-31 | Mon - Fri | Yes | Warehouse | Cooling Set Point | Fine Sorage | Mon - Fri | Warehouse-Cooling Set Point-Fine Sorage-Mon - Fri | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | Fine Storage Cooling Setpoint Schedule | Temperature | 2023-12-31 | Sat | Yes | Warehouse | Cooling Set Point | Fine Sorage | Sat | Warehouse-Cooling Set Point-Fine Sorage-Sat | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | Fine Storage Cooling Setpoint Schedule | Temperature | 2023-12-31 | Sun | Yes | Warehouse | Cooling Set Point | Fine Sorage | Sun | Warehouse-Cooling Set Point-Fine Sorage-Sun | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
Warehouse | OA Damper Always ON Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | OA Damper Always ON Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | OA Damper Always ON Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | MinOA_Sched | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | MinOA_Sched | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | MinOA_Sched | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | UnitHeaterAvailability | Any Number | 2023-12-31 | Mon - Fri | No (the same as COMPACT HVAC-ALWAYS 1) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | UnitHeaterAvailability | Any Number | 2023-12-31 | Sat | No (the same as COMPACT HVAC-ALWAYS 1) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | UnitHeaterAvailability | Any Number | 2023-12-31 | Sun | No (the same as COMPACT HVAC-ALWAYS 1) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Zone3HeatingCoilAvailability | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Zone3HeatingCoilAvailability | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Zone3HeatingCoilAvailability | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Always On Schedule | Fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Always On Schedule | Fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Always On Schedule | Fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Office Infil Schedule | Any Number | 2023-12-31 | Mon - Fri | Yes | Warehouse | Infiltration | Office, Fine Sorage | Mon - Fri | Warehouse-Infiltration-Office, Fine Sorage-Mon - Fri | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Office Infil Schedule | Any Number | 2023-12-31 | Sat | Yes | Warehouse | Infiltration | Office, Fine Sorage | Sat | Warehouse-Infiltration-Office, Fine Sorage-Sat | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Office Infil Schedule | Any Number | 2023-12-31 | Sun | Yes | Warehouse | Infiltration | Office, Fine Sorage | Sun | Warehouse-Infiltration-Office, Fine Sorage-Sun | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Fine Sorage Infil Schedule | Any Number | 2023-12-31 | Mon - Fri | No (the same as Office Infil Schedule) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Fine Sorage Infil Schedule | Any Number | 2023-12-31 | Sat | No (the same as Office Infil Schedule) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.25 | 1.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1.25 | 1.25 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Fine Sorage Infil Schedule | Any Number | 2023-12-31 | Sun | No (the same as Office Infil Schedule) |  |  |  |  | --- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Bulk Storage Infil_Base Schedule | Any Number | 2023-12-31 | Mon - Fri | Yes | Warehouse | Infiltration | Bulk Storage | Mon - Fri | Warehouse-Infiltration-Bulk Storage-Mon - Fri | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | Bulk Storage Infil_Base Schedule | Any Number | 2023-12-31 | Sat | Yes | Warehouse | Infiltration | Bulk Storage | Sat | Warehouse-Infiltration-Bulk Storage-Sat | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 1 | 1 | 1 | 1 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | Bulk Storage Infil_Base Schedule | Any Number | 2023-12-31 | Sun | Yes | Warehouse | Infiltration | Bulk Storage | Sun | Warehouse-Infiltration-Bulk Storage-Sun | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765 | 0.765
Warehouse | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0.144 | 0.144 | 0.144 | 1 | 0.144 | 0 | 0 | 0 | 0 | 0
Warehouse | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | INFIL_Door_Opening_SCH | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Warehouse | ZONE3 BULK STORAGE Activity Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | ZONE3 BULK STORAGE Activity Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | ZONE3 BULK STORAGE Activity Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | ZONE2 FINE STORAGE Activity Schedule | Any Number | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | ZONE2 FINE STORAGE Activity Schedule | Any Number | 2023-12-31 | Sat | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | ZONE2 FINE STORAGE Activity Schedule | Any Number | 2023-12-31 | Sun | No |  |  |  |  | --- | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85 | 131.85
Warehouse | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Exterior_lighting_schedule_a | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Mon - Fri | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sat | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Warehouse | Exterior_lighting_schedule_b | fraction | 2023-12-31 | Sun | No |  |  |  |  | --- | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1

## raw_data (hidden)
| Code | Location | Prototype Building | Thermal Zone | Area [m2] | Multipliers | Conditioned (Y/N) | HVAC System Name | Above Ground Gross Wall Area [m2] | Window Glass Area [m2] | Lighting Power Density [W/m2] | Design Occupancy Density [m2/person] | Plug and Process [W/m2] | Gas Power [W] | Total OSA Ventilation [m3/s] | Exhaust Airflow [m3/s] | Envelope Infiltration (Flow/Exterior Wall Area) [m3/s-m2] | Envelope Infiltration (Flow/Zone) [m3/s] | Infiltration Through Entrances [m3/s]
ApartmentHighRiseG SW APARTMENT | STD2004 | Buffalo | ApartmentHighRise | G SW APARTMENT | 88.25 | 1 | Yes | AIRLOOP G SW | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseG NW APARTMENT | STD2004 | Buffalo | ApartmentHighRise | G NW APARTMENT | 88.25 | 1 | Yes | AIRLOOP G NW | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseOFFICE | STD2004 | Buffalo | ApartmentHighRise | OFFICE | 88.25 | 1 | Yes | AIRLOOP OFFICE | 58.52 | 17.56 | 11.8403 | 18.58 | 6.67 | 0 | 0.0448 |  | 0.0010252 | 0 | 0
ApartmentHighRiseG NE APARTMENT | STD2004 | Buffalo | ApartmentHighRise | G NE APARTMENT | 88.25 | 1 | Yes | AIRLOOP G NE | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseG N1 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | G N1 APARTMENT | 88.25 | 1 | Yes | AIRLOOP G N1 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseG N2 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | G N2 APARTMENT | 88.25 | 1 | Yes | AIRLOOP G N2 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseG S1 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | G S1 APARTMENT | 88.25 | 1 | Yes | AIRLOOP G S1 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseG S2 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | G S2 APARTMENT | 88.25 | 1 | Yes | AIRLOOP G S2 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseG CORRIDOR | STD2004 | Buffalo | ApartmentHighRise | G CORRIDOR | 77.66 | 1 | No |  | 10.22 | 4.47 | 5.651 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 1.5239
ApartmentHighRiseM SW APARTMENT | STD2004 | Buffalo | ApartmentHighRise | M SW APARTMENT | 88.25 | 8 | Yes | AIRLOOP M SW | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.2076 |  | 0.0010252 | 0 | 0
ApartmentHighRiseM NW APARTMENT | STD2004 | Buffalo | ApartmentHighRise | M NW APARTMENT | 88.25 | 8 | Yes | AIRLOOP M NW | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.2076 |  | 0.0010252 | 0 | 0
ApartmentHighRiseM SE APARTMENT | STD2004 | Buffalo | ApartmentHighRise | M SE APARTMENT | 88.25 | 8 | Yes | AIRLOOP M SE | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.2076 |  | 0.0010252 | 0 | 0
ApartmentHighRiseM NE APARTMENT | STD2004 | Buffalo | ApartmentHighRise | M NE APARTMENT | 88.25 | 8 | Yes | AIRLOOP M NE | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.2076 |  | 0.0010252 | 0 | 0
ApartmentHighRiseM N1 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | M N1 APARTMENT | 88.25 | 8 | Yes | AIRLOOP M N1 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.2076 |  | 0.0010252 | 0 | 0
ApartmentHighRiseM N2 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | M N2 APARTMENT | 88.25 | 8 | Yes | AIRLOOP M N2 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.2076 |  | 0.0010252 | 0 | 0
ApartmentHighRiseM S1 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | M S1 APARTMENT | 88.25 | 8 | Yes | AIRLOOP M S1 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.2076 |  | 0.0010252 | 0 | 0
ApartmentHighRiseM S2 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | M S2 APARTMENT | 88.25 | 8 | Yes | AIRLOOP M S2 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.2076 |  | 0.0010252 | 0 | 0
ApartmentHighRiseM CORRIDOR | STD2004 | Buffalo | ApartmentHighRise | M CORRIDOR | 77.66 | 8 | No |  | 10.22 | 2.23 | 5.651 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
ApartmentHighRiseT SW APARTMENT | STD2004 | Buffalo | ApartmentHighRise | T SW APARTMENT | 88.25 | 1 | Yes | AIRLOOP T SW | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseT NW APARTMENT | STD2004 | Buffalo | ApartmentHighRise | T NW APARTMENT | 88.25 | 1 | Yes | AIRLOOP T NW | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseT SE APARTMENT | STD2004 | Buffalo | ApartmentHighRise | T SE APARTMENT | 88.25 | 1 | Yes | AIRLOOP T SE | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseT NE APARTMENT | STD2004 | Buffalo | ApartmentHighRise | T NE APARTMENT | 88.25 | 1 | Yes | AIRLOOP T NE | 58.52 | 17.56 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseT N1 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | T N1 APARTMENT | 88.25 | 1 | Yes | AIRLOOP T N1 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseT N2 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | T N2 APARTMENT | 88.25 | 1 | Yes | AIRLOOP T N2 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseT S1 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | T S1 APARTMENT | 88.25 | 1 | Yes | AIRLOOP T S1 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseT S2 APARTMENT | STD2004 | Buffalo | ApartmentHighRise | T S2 APARTMENT | 88.25 | 1 | Yes | AIRLOOP T S2 | 35.3 | 10.59 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentHighRiseT CORRIDOR | STD2004 | Buffalo | ApartmentHighRise | T CORRIDOR | 77.66 | 1 | No |  | 10.22 | 2.23 | 5.651 | 18.58 | 223.7239 | 0 |  |  | 0.0010252 | 0 | 0
ApartmentHighRiseTotal | STD2004 | Buffalo | ApartmentHighRise | Total | 7836.48 |  |  |  | 3855.02 | 1150.39 | 16.2065 | 32.11 | 8.2261 | 0 |  |  | 0 | 0 | 0
ApartmentHighRiseConditioned Total | STD2004 | Buffalo | ApartmentHighRise | Conditioned Total | 7059.89 |  |  |  | 3752.84 | 1125.85 | 17.3676 | 34.91 | 6.67 | 0 |  |  | 0 | 0 | 0
ApartmentHighRiseUnconditioned Total | STD2004 | Buffalo | ApartmentHighRise | Unconditioned Total | 776.58 |  |  |  | 102.18 | 24.54 | 5.651 | 18.58 | 22.3724 | 0 |  |  | 0 | 0 | 0
ApartmentHighRiseNot Part of Total | STD2004 | Buffalo | ApartmentHighRise | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
ApartmentMidRiseG SW APARTMENT | STD2004 | Buffalo | ApartmentMidRise | G SW APARTMENT | 88.25 | 1 | Yes | SPLIT GSW | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseG NW APARTMENT | STD2004 | Buffalo | ApartmentMidRise | G NW APARTMENT | 88.25 | 1 | Yes | SPLIT GNW | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseOFFICE | STD2004 | Buffalo | ApartmentMidRise | OFFICE | 88.25 | 1 | Yes | SPLIT OFFICE | 58.52 | 11.71 | 11.8403 | 18.58 | 6.67 | 0 | 0.0448 |  | 0.0010252 | 0 | 0
ApartmentMidRiseG NE APARTMENT | STD2004 | Buffalo | ApartmentMidRise | G NE APARTMENT | 88.25 | 1 | Yes | SPLIT GNE | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseG N1 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | G N1 APARTMENT | 88.25 | 1 | Yes | SPLIT GN1 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseG N2 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | G N2 APARTMENT | 88.25 | 1 | Yes | SPLIT GN2 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseG S1 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | G S1 APARTMENT | 88.25 | 1 | Yes | SPLIT GS1 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseG S2 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | G S2 APARTMENT | 88.25 | 1 | Yes | SPLIT GS2 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseM SW APARTMENT | STD2004 | Buffalo | ApartmentMidRise | M SW APARTMENT | 88.25 | 2 | Yes | SPLIT MSW | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.0519 |  | 0.0010252 | 0 | 0
ApartmentMidRiseM NW APARTMENT | STD2004 | Buffalo | ApartmentMidRise | M NW APARTMENT | 88.25 | 2 | Yes | SPLIT MNW | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.0519 |  | 0.0010252 | 0 | 0
ApartmentMidRiseM SE APARTMENT | STD2004 | Buffalo | ApartmentMidRise | M SE APARTMENT | 88.25 | 2 | Yes | SPLIT MSE | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.0519 |  | 0.0010252 | 0 | 0
ApartmentMidRiseM NE APARTMENT | STD2004 | Buffalo | ApartmentMidRise | M NE APARTMENT | 88.25 | 2 | Yes | SPLIT MNE | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.0519 |  | 0.0010252 | 0 | 0
ApartmentMidRiseM N1 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | M N1 APARTMENT | 88.25 | 2 | Yes | SPLIT MN1 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.0519 |  | 0.0010252 | 0 | 0
ApartmentMidRiseM N2 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | M N2 APARTMENT | 88.25 | 2 | Yes | SPLIT MN2 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.0519 |  | 0.0010252 | 0 | 0
ApartmentMidRiseM S1 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | M S1 APARTMENT | 88.25 | 2 | Yes | SPLIT MS1 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.0519 |  | 0.0010252 | 0 | 0
ApartmentMidRiseM S2 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | M S2 APARTMENT | 88.25 | 2 | Yes | SPLIT MS2 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.0519 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT SW APARTMENT | STD2004 | Buffalo | ApartmentMidRise | T SW APARTMENT | 88.25 | 1 | Yes | SPLIT TSW | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT NW APARTMENT | STD2004 | Buffalo | ApartmentMidRise | T NW APARTMENT | 88.25 | 1 | Yes | SPLIT TNW | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT SE APARTMENT | STD2004 | Buffalo | ApartmentMidRise | T SE APARTMENT | 88.25 | 1 | Yes | SPLIT TSE | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT NE APARTMENT | STD2004 | Buffalo | ApartmentMidRise | T NE APARTMENT | 88.25 | 1 | Yes | SPLIT TNE | 58.52 | 11.71 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT N1 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | T N1 APARTMENT | 88.25 | 1 | Yes | SPLIT TN1 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT N2 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | T N2 APARTMENT | 88.25 | 1 | Yes | SPLIT TN2 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT S1 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | T S1 APARTMENT | 88.25 | 1 | Yes | SPLIT TS1 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT S2 APARTMENT | STD2004 | Buffalo | ApartmentMidRise | T S2 APARTMENT | 88.25 | 1 | Yes | SPLIT TS2 | 35.3 | 7.06 | 17.4375 | 35.3 | 6.67 | 0 | 0.026 |  | 0.0010252 | 0 | 0
ApartmentMidRiseT CORRIDOR | STD2004 | Buffalo | ApartmentMidRise | T CORRIDOR | 77.66 | 1 | No |  | 10.22 | 1.11 | 5.8183 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
ApartmentMidRiseG CORRIDOR | STD2004 | Buffalo | ApartmentMidRise | G CORRIDOR | 77.66 | 1 | No |  | 10.22 | 3.32 | 5.8183 | 18.58 | 105.2565 | 0 |  |  | 0.0010252 | 0 | 0.52056
ApartmentMidRiseM CORRIDOR | STD2004 | Buffalo | ApartmentMidRise | M CORRIDOR | 77.66 | 2 | No |  | 10.22 | 1.11 | 5.8183 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
ApartmentMidRiseTotal | STD2004 | Buffalo | ApartmentMidRise | Total | 3134.61 |  |  |  | 1542.04 | 306.92 | 16.1285 | 31.67 | 8.6167 | 0 |  |  | 0 | 0 | 0
ApartmentMidRiseConditioned Total | STD2004 | Buffalo | ApartmentMidRise | Conditioned Total | 2823.98 |  |  |  | 1501.17 | 300.26 | 17.2626 | 34.33 | 6.67 | 0 |  |  | 0 | 0 | 0
ApartmentMidRiseUnconditioned Total | STD2004 | Buffalo | ApartmentMidRise | Unconditioned Total | 310.64 |  |  |  | 40.87 | 6.66 | 5.8183 | 18.58 | 26.3141 | 0 |  |  | 0 | 0 | 0
ApartmentMidRiseNot Part of Total | STD2004 | Buffalo | ApartmentMidRise | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
HospitalBASEMENT | STD2004 | Buffalo | Hospital | BASEMENT | 3739.35 | 1 | Yes | VAV_1 | 0 | 0 | 11.5799 | 37.17 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalER_EXAM1_MULT4_FLR_1 | STD2004 | Buffalo | Hospital | ER_EXAM1_MULT4_FLR_1 | 27.87 | 4 | Yes | VAV_ER | 26.02 | 0 | 16.1458 | 4.65 | 16.14 | 0 | 0.2643 |  | 0.0010252 | 0 | 0
HospitalER_TRAUMA1_FLR_1 | STD2004 | Buffalo | Hospital | ER_TRAUMA1_FLR_1 | 27.87 | 1 | Yes | VAV_ER | 45.53 | 0 | 16.1458 | 4.65 | 43.04 | 0 | 0.0661 |  | 0.0010252 | 0 | 0
HospitalER_EXAM3_MULT4_FLR_1 | STD2004 | Buffalo | Hospital | ER_EXAM3_MULT4_FLR_1 | 27.87 | 4 | Yes | VAV_ER | 19.51 | 0 | 16.1458 | 4.65 | 16.14 | 0 | 0.2643 |  | 0.0010252 | 0 | 0
HospitalER_TRAUMA2_FLR_1 | STD2004 | Buffalo | Hospital | ER_TRAUMA2_FLR_1 | 27.87 | 1 | Yes | VAV_ER | 45.53 | 0 | 16.1458 | 4.65 | 43.04 | 0 | 0.0661 |  | 0.0010252 | 0 | 0
HospitalER_TRIAGE_MULT4_FLR_1 | STD2004 | Buffalo | Hospital | ER_TRIAGE_MULT4_FLR_1 | 27.87 | 4 | Yes | VAV_ER | 26.02 | 0 | 16.1458 | 4.65 | 21.5271 | 0 | 0.2643 |  | 0.0010252 | 0 | 0
HospitalOFFICE1_MULT4_FLR_1 | STD2004 | Buffalo | Hospital | OFFICE1_MULT4_FLR_1 | 13.94 | 5 | Yes | VAV_1 | 13.01 | 2.96 | 11.8403 | 13.27 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalLOBBY_RECORDS_FLR_1 | STD2004 | Buffalo | Hospital | LOBBY_RECORDS_FLR_1 | 1474.81 | 1 | Yes | VAV_1 | 409.78 | 62.6 | 13.7778 | 69.7 | 1.08 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalCORRIDOR_FLR_1 | STD2004 | Buffalo | Hospital | CORRIDOR_FLR_1 | 569.03 | 1 | Yes | VAV_1 | 91.07 | 0 | 10.3927 | 18.58 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalER_NURSESTN_LOBBY_FLR_1 | STD2004 | Buffalo | Hospital | ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | 1 | Yes | VAV_1 | 110.58 | 30.4 | 12.0556 | 69.7 | 14.63 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalOR1_FLR_2 | STD2004 | Buffalo | Hospital | OR1_FLR_2 | 55.74 | 1 | Yes | VAV_OR | 65.05 | 0 | 23.6806 | 18.59 | 43.04 | 0 | 0.1982 |  | 0.0010252 | 0 | 0
HospitalOR2_MULT5_FLR_2 | STD2004 | Buffalo | Hospital | OR2_MULT5_FLR_2 | 55.74 | 5 | Yes | VAV_OR | 26.02 | 0 | 23.6806 | 18.59 | 43.04 | 0 | 0.9911 |  | 0.0010252 | 0 | 0
HospitalOR3_FLR_2 | STD2004 | Buffalo | Hospital | OR3_FLR_2 | 55.74 | 1 | Yes | VAV_OR | 39.03 | 0 | 23.6806 | 18.59 | 43.04 | 0 | 0.1982 |  | 0.0010252 | 0 | 0
HospitalOR4_FLR_2 | STD2004 | Buffalo | Hospital | OR4_FLR_2 | 222.97 | 1 | Yes | VAV_OR | 0 | 0 | 23.6806 | 18.59 | 43.04 | 0 | 0.7929 |  | 0.0010252 | 0 | 0
HospitalIC_PATROOM1_MULT5_FLR_2 | STD2004 | Buffalo | Hospital | IC_PATROOM1_MULT5_FLR_2 | 20.9 | 5 | Yes | VAV_ICU | 19.51 | 4.91 | 8.6111 | 18.59 | 32.28 | 0 | 0.2478 |  | 0.0010252 | 0 | 0
HospitalIC_PATROOM2_FLR_2 | STD2004 | Buffalo | Hospital | IC_PATROOM2_FLR_2 | 27.87 | 1 | Yes | VAV_ICU | 45.53 | 11.45 | 8.6111 | 18.59 | 32.28 | 0 | 0.0661 |  | 0.0010252 | 0 | 0
HospitalIC_PATROOM3_MULT6_FLR_2 | STD2004 | Buffalo | Hospital | IC_PATROOM3_MULT6_FLR_2 | 20.9 | 6 | Yes | VAV_ICU | 19.51 | 4.91 | 8.6111 | 18.59 | 32.28 | 0 | 0.2973 |  | 0.0010252 | 0 | 0
HospitalICU_FLR_2 | STD2004 | Buffalo | Hospital | ICU_FLR_2 | 617.96 | 1 | Yes | VAV_ICU | 214.68 | 25.04 | 8.6111 | 18.59 | 32.28 | 0 | 1.465 |  | 0.0010252 | 0 | 0
HospitalICU_NURSESTN_LOBBY_FLR_2 | STD2004 | Buffalo | Hospital | ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | 1 | Yes | VAV_1 | 0 | 0 | 10.7639 | 69.7 | 21.52 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalCORRIDOR_FLR_2 | STD2004 | Buffalo | Hospital | CORRIDOR_FLR_2 | 569.03 | 1 | Yes | VAV_1 | 91.07 | 0 | 10.3927 | 92.94 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalOR_NURSESTN_LOBBY_FLR_2 | STD2004 | Buffalo | Hospital | OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | 1 | Yes | VAV_1 | 182.14 | 35.77 | 12.7014 | 69.7 | 11.19 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalPATROOM1_MULT10_FLR_3 | STD2004 | Buffalo | Hospital | PATROOM1_MULT10_FLR_3 | 20.9 | 10 | Yes | VAV_PATRMS | 19.51 | 4.91 | 7.5347 | 18.59 | 21.52 | 0 | 0.4955 |  | 0.0010252 | 0 | 0
HospitalPATROOM2_FLR_3 | STD2004 | Buffalo | Hospital | PATROOM2_FLR_3 | 34.84 | 1 | Yes | VAV_PATRMS | 52.04 | 13.08 | 7.5347 | 18.59 | 21.52 | 0 | 0.0826 |  | 0.0010252 | 0 | 0
HospitalPATROOM3_MULT10_FLR_3 | STD2004 | Buffalo | Hospital | PATROOM3_MULT10_FLR_3 | 20.21 | 10 | Yes | VAV_PATRMS | 18.87 | 4.74 | 7.5347 | 18.59 | 21.52 | 0 | 0.4791 |  | 0.0010252 | 0 | 0
HospitalPATROOM4_FLR_3 | STD2004 | Buffalo | Hospital | PATROOM4_FLR_3 | 34.84 | 1 | Yes | VAV_PATRMS | 52.04 | 13.08 | 7.5347 | 18.59 | 21.52 | 0 | 0.0826 |  | 0.0010252 | 0 | 0
HospitalPATROOM5_MULT10_FLR_3 | STD2004 | Buffalo | Hospital | PATROOM5_MULT10_FLR_3 | 20.9 | 10 | Yes | VAV_PATRMS | 19.51 | 4.91 | 7.5347 | 18.59 | 21.52 | 0 | 0.4955 |  | 0.0010252 | 0 | 0
HospitalPHYSTHERAPY_FLR_3 | STD2004 | Buffalo | Hospital | PHYSTHERAPY_FLR_3 | 487.74 | 1 | Yes | VAV_2 | 0 | 0 | 9.6875 | 18.59 | 16.14 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalPATROOM6_FLR_3 | STD2004 | Buffalo | Hospital | PATROOM6_FLR_3 | 27.87 | 1 | Yes | VAV_PATRMS | 45.53 | 11.45 | 7.5347 | 18.59 | 21.52 | 0 | 0.0661 |  | 0.0010252 | 0 | 0
HospitalPATROOM7_MULT10_FLR_3 | STD2004 | Buffalo | Hospital | PATROOM7_MULT10_FLR_3 | 20.21 | 10 | Yes | VAV_PATRMS | 18.87 | 4.74 | 7.5347 | 18.59 | 21.52 | 0 | 0.4791 |  | 0.0010252 | 0 | 0
HospitalPATROOM8_FLR_3 | STD2004 | Buffalo | Hospital | PATROOM8_FLR_3 | 27.87 | 1 | Yes | VAV_PATRMS | 45.53 | 11.45 | 7.5347 | 18.59 | 21.52 | 0 | 0.0661 |  | 0.0010252 | 0 | 0
HospitalNURSESTN_LOBBY_FLR_3 | STD2004 | Buffalo | Hospital | NURSESTN_LOBBY_FLR_3 | 905.8 | 1 | Yes | VAV_2 | 0 | 0 | 12.7014 | 69.7 | 11.19 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalLAB_FLR_3 | STD2004 | Buffalo | Hospital | LAB_FLR_3 | 264.77 | 1 | Yes | VAV_LABS | 0 | 0 | 15.0695 | 18.59 | 43.04 | 0 | 0.1345 |  | 0.0010252 | 0 | 0
HospitalCORRIDOR_SE_FLR_3 | STD2004 | Buffalo | Hospital | CORRIDOR_SE_FLR_3 | 566.71 | 1 | Yes | VAV_2 | 45.53 | 0 | 10.3927 | 92.94 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalCORRIDOR_NW_FLR_3 | STD2004 | Buffalo | Hospital | CORRIDOR_NW_FLR_3 | 566.71 | 1 | Yes | VAV_2 | 45.53 | 0 | 10.3927 | 92.94 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalPATROOM1_MULT10_FLR_4 | STD2004 | Buffalo | Hospital | PATROOM1_MULT10_FLR_4 | 20.9 | 10 | Yes | VAV_PATRMS | 19.51 | 4.91 | 7.5347 | 18.59 | 21.52 | 0 | 0.4955 |  | 0.0010252 | 0 | 0
HospitalPATROOM2_FLR_4 | STD2004 | Buffalo | Hospital | PATROOM2_FLR_4 | 34.84 | 1 | Yes | VAV_PATRMS | 52.04 | 13.08 | 7.5347 | 18.59 | 21.52 | 0 | 0.0826 |  | 0.0010252 | 0 | 0
HospitalPATROOM3_MULT10_FLR_4 | STD2004 | Buffalo | Hospital | PATROOM3_MULT10_FLR_4 | 20.21 | 10 | Yes | VAV_PATRMS | 18.87 | 4.74 | 7.5347 | 18.59 | 21.52 | 0 | 0.4791 |  | 0.0010252 | 0 | 0
HospitalPATROOM4_FLR_4 | STD2004 | Buffalo | Hospital | PATROOM4_FLR_4 | 34.84 | 1 | Yes | VAV_PATRMS | 52.04 | 13.08 | 7.5347 | 18.59 | 21.52 | 0 | 0.0826 |  | 0.0010252 | 0 | 0
HospitalPATROOM5_MULT10_FLR_4 | STD2004 | Buffalo | Hospital | PATROOM5_MULT10_FLR_4 | 20.9 | 10 | Yes | VAV_PATRMS | 19.51 | 4.91 | 7.5347 | 18.59 | 21.52 | 0 | 0.4955 |  | 0.0010252 | 0 | 0
HospitalRADIOLOGY_FLR_4 | STD2004 | Buffalo | Hospital | RADIOLOGY_FLR_4 | 487.74 | 1 | Yes | VAV_2 | 0 | 0 | 4.3056 | 18.59 | 107.6389 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalPATROOM6_FLR_4 | STD2004 | Buffalo | Hospital | PATROOM6_FLR_4 | 27.87 | 1 | Yes | VAV_PATRMS | 45.53 | 11.45 | 7.5347 | 18.59 | 21.52 | 0 | 0.0661 |  | 0.0010252 | 0 | 0
HospitalPATROOM7_MULT10_FLR_4 | STD2004 | Buffalo | Hospital | PATROOM7_MULT10_FLR_4 | 20.21 | 10 | Yes | VAV_PATRMS | 18.87 | 4.74 | 7.5347 | 18.59 | 21.52 | 0 | 0.4791 |  | 0.0010252 | 0 | 0
HospitalPATROOM8_FLR_4 | STD2004 | Buffalo | Hospital | PATROOM8_FLR_4 | 27.87 | 1 | Yes | VAV_PATRMS | 45.53 | 11.45 | 7.5347 | 18.59 | 21.52 | 0 | 0.0661 |  | 0.0010252 | 0 | 0
HospitalNURSESTN_LOBBY_FLR_4 | STD2004 | Buffalo | Hospital | NURSESTN_LOBBY_FLR_4 | 905.8 | 1 | Yes | VAV_2 | 0 | 0 | 12.7014 | 69.7 | 11.19 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalLAB_FLR_4 | STD2004 | Buffalo | Hospital | LAB_FLR_4 | 264.77 | 1 | Yes | VAV_LABS | 0 | 0 | 15.0695 | 18.59 | 43.04 | 0 | 0.1345 |  | 0.0010252 | 0 | 0
HospitalCORRIDOR_SE_FLR_4 | STD2004 | Buffalo | Hospital | CORRIDOR_SE_FLR_4 | 566.71 | 1 | Yes | VAV_2 | 45.53 | 0 | 10.3927 | 92.94 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalCORRIDOR_NW_FLR_4 | STD2004 | Buffalo | Hospital | CORRIDOR_NW_FLR_4 | 566.71 | 1 | Yes | VAV_2 | 45.53 | 0 | 10.3927 | 92.94 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HospitalDINING_FLR_5 | STD2004 | Buffalo | Hospital | DINING_FLR_5 | 696.77 | 1 | Yes | VAV_2 | 227.67 | 35.77 | 9.6875 | 9.29 | 10.76 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HospitalNURSESTN_LOBBY_FLR_5 | STD2004 | Buffalo | Hospital | NURSESTN_LOBBY_FLR_5 | 1040.51 | 1 | Yes | VAV_2 | 104.08 | 0 | 12.7014 | 69.7 | 11.19 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HospitalKITCHEN_FLR_5 | STD2004 | Buffalo | Hospital | KITCHEN_FLR_5 | 929.03 | 1 | Yes | CAV_KITCHEN | 260.2 | 0 | 12.9167 | 18.59 | 244.5857 | 149945.5066 | 0.354 | 3.78 | 0.0010252 | 0 | 0
HospitalOFFICE1_FLR_5 | STD2004 | Buffalo | Hospital | OFFICE1_FLR_5 | 69.7 | 1 | Yes | VAV_2 | 71.56 | 17.99 | 11.8403 | 13.28 | 10.76 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HospitalOFFICE2_MULT5_FLR_5 | STD2004 | Buffalo | Hospital | OFFICE2_MULT5_FLR_5 | 69.68 | 5 | Yes | VAV_2 | 32.52 | 8.18 | 11.8403 | 13.28 | 10.76 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HospitalOFFICE3_FLR_5 | STD2004 | Buffalo | Hospital | OFFICE3_FLR_5 | 69.68 | 1 | Yes | VAV_2 | 71.55 | 17.99 | 11.8403 | 13.28 | 10.76 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HospitalOFFICE4_MULT6_FLR_5 | STD2004 | Buffalo | Hospital | OFFICE4_MULT6_FLR_5 | 13.94 | 6 | Yes | VAV_2 | 13.01 | 2.96 | 11.8403 | 13.27 | 10.76 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HospitalCORRIDOR_FLR_5 | STD2004 | Buffalo | Hospital | CORRIDOR_FLR_5 | 501.68 | 1 | Yes | VAV_2 | 78.06 | 0 | 10.3927 | 92.94 | 0 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HospitalTotal | STD2004 | Buffalo | Hospital | Total | 22436.18 |  |  |  | 5197.44 | 848.5 | 11.5523 | 28.35 | 23.8985 | 0 |  |  | 0 | 0 | 0
HospitalConditioned Total | STD2004 | Buffalo | Hospital | Conditioned Total | 22436.18 |  |  |  | 5197.44 | 848.5 | 11.5523 | 28.35 | 23.8985 | 0 |  |  | 0 | 0 | 0
HospitalUnconditioned Total | STD2004 | Buffalo | Hospital | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
HospitalNot Part of Total | STD2004 | Buffalo | Hospital | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
HotelLargeBASEMENT | STD2004 | Buffalo | HotelLarge | BASEMENT | 1978.83 | 1 | Yes | VAV WITH REHEAT | 0 | 0 | 11.0679 | 18.58 | 5.38 | 0 | 0 |  | 0 | 0 | 0
HotelLargeRETAIL_1_FLR_1 | STD2004 | Buffalo | HotelLarge | RETAIL_1_FLR_1 | 67.07 | 1 | Yes | VAV WITH REHEAT | 68.84 | 23.26 | 16.1458 | 6.19 | 10.76 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeRETAIL_2_FLR_1 | STD2004 | Buffalo | HotelLarge | RETAIL_2_FLR_1 | 77.67 | 1 | Yes | VAV WITH REHEAT | 26.57 | 0 | 16.1458 | 6.19 | 10.76 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeMECH_FLR_1 | STD2004 | Buffalo | HotelLarge | MECH_FLR_1 | 164.24 | 1 | Yes | VAV WITH REHEAT | 62.8 | 0 | 16.1458 | 61.93 | 5.38 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeSTORAGE_FLR_1 | STD2004 | Buffalo | HotelLarge | STORAGE_FLR_1 | 94.76 | 1 | Yes | VAV WITH REHEAT | 36.23 | 0 | 8.6111 | 46.45 | 2.69 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeLAUNDRY_FLR_1 | STD2004 | Buffalo | HotelLarge | LAUNDRY_FLR_1 | 78.04 | 1 | Yes | VAV WITH REHEAT | 85.75 | 0 | 6.4583 | 9.29 | 597.53 | 41817.4489 | 0 | 0.24 | 0.0010252 | 0 | 0
HotelLargeCAFE_FLR_1 | STD2004 | Buffalo | HotelLarge | CAFE_FLR_1 | 188.86 | 1 | Yes | VAV WITH REHEAT | 152.17 | 65.5 | 15.0695 | 1.33 | 5.38 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeLOBBY_FLR_1 | STD2004 | Buffalo | HotelLarge | LOBBY_FLR_1 | 1308.19 | 1 | Yes | VAV WITH REHEAT | 434.79 | 85.08 | 13.9931 | 3.1 | 8.07 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HotelLargeROOM_1_FLR_3 | STD2004 | Buffalo | HotelLarge | ROOM_1_FLR_3 | 39.02 | 4 | Yes | FLR_3_DOAS | 39.95 | 13.18 | 11.8403 | 26.01 | 6.75 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeROOM_2_FLR_3 | STD2004 | Buffalo | HotelLarge | ROOM_2_FLR_3 | 39.02 | 4 | Yes | FLR_3_DOAS | 39.95 | 13.18 | 11.8403 | 26.01 | 6.75 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeROOM_3_MULT19_FLR_3 | STD2004 | Buffalo | HotelLarge | ROOM_3_MULT19_FLR_3 | 24.52 | 76 | Yes | FLR_3_DOAS | 11.15 | 3.68 | 11.8403 | 16.35 | 10.52 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeROOM_4_MULT19_FLR_3 | STD2004 | Buffalo | HotelLarge | ROOM_4_MULT19_FLR_3 | 24.53 | 76 | Yes | FLR_3_DOAS | 11.15 | 3.68 | 11.8403 | 16.35 | 10.52 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeROOM_5_FLR_3 | STD2004 | Buffalo | HotelLarge | ROOM_5_FLR_3 | 39.02 | 4 | Yes | FLR_3_DOAS | 39.95 | 13.18 | 11.8403 | 26.01 | 6.75 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeROOM_6_FLR_3 | STD2004 | Buffalo | HotelLarge | ROOM_6_FLR_3 | 39.02 | 4 | Yes | FLR_3_DOAS | 39.95 | 13.18 | 11.8403 | 26.01 | 6.75 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeCORRIDOR_FLR_3 | STD2004 | Buffalo | HotelLarge | CORRIDOR_FLR_3 | 389.4 | 4 | Yes | VAV WITH REHEAT | 48.31 | 15.94 | 5.3819 | 18.58 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeROOM_1_FLR_6 | STD2004 | Buffalo | HotelLarge | ROOM_1_FLR_6 | 39.02 | 1 | Yes | FLR_3_DOAS | 39.95 | 13.18 | 11.8403 | 26.01 | 6.75 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeROOM_2_FLR_6 | STD2004 | Buffalo | HotelLarge | ROOM_2_FLR_6 | 39.02 | 1 | Yes | FLR_3_DOAS | 39.95 | 13.18 | 11.8403 | 26.01 | 6.75 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeROOM_3_MULT9_FLR_6 | STD2004 | Buffalo | HotelLarge | ROOM_3_MULT9_FLR_6 | 24.53 | 9 | Yes | FLR_3_DOAS | 20.44 | 6.74 | 11.8403 | 16.35 | 10.52 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeBANQUET_FLR_6 | STD2004 | Buffalo | HotelLarge | BANQUET_FLR_6 | 331.66 | 1 | Yes | VAV WITH REHEAT | 97.55 | 32.19 | 15.0695 | 1.33 | 67.82 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HotelLargeDINING_FLR_6 | STD2004 | Buffalo | HotelLarge | DINING_FLR_6 | 331.66 | 1 | Yes | VAV WITH REHEAT | 97.55 | 32.19 | 15.0695 | 1.33 | 67.82 | 0 | 0 | 0 | 0.0010252 | 0 | 0
HotelLargeKITCHEN_FLR_6 | STD2004 | Buffalo | HotelLarge | KITCHEN_FLR_6 | 103.3 | 1 | Yes | VAV WITH REHEAT | 87.33 | 26.37 | 12.9167 | 4.65 | 2936.4163 | 249920.3527 | 0 | 1.89 | 0.0010252 | 0 | 0
HotelLargeCORRIDOR_FLR_6 | STD2004 | Buffalo | HotelLarge | CORRIDOR_FLR_6 | 412.12 | 1 | Yes | VAV WITH REHEAT | 85.47 | 28.2 | 5.3819 | 18.58 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelLargeTotal | STD2004 | Buffalo | HotelLarge | Total | 11345.29 |  |  |  | 4025.82 | 1213.79 | 11.1381 | 7.07 | 41.0885 | 0 |  |  | 0 | 0 | 0
HotelLargeConditioned Total | STD2004 | Buffalo | HotelLarge | Conditioned Total | 11345.29 |  |  |  | 4025.82 | 1213.79 | 11.1381 | 7.07 | 41.0885 | 0 |  |  | 0 | 0 | 0
HotelLargeUnconditioned Total | STD2004 | Buffalo | HotelLarge | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
HotelLargeNot Part of Total | STD2004 | Buffalo | HotelLarge | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
HotelSmallREARSTAIRSFLR1 | STD2004 | Buffalo | HotelSmall | REARSTAIRSFLR1 | 20.07 | 1 | Yes | RearStairsFlr1 Unit Heater | 35.77 | 0 | 6.4583 | 18.59 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallCORRIDORFLR1 | STD2004 | Buffalo | HotelSmall | CORRIDORFLR1 | 150.51 | 1 | Yes | CorridorFlr1 PTAC | 32.7 | 9.82 | 5.3819 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0.91558
HotelSmallREARSTORAGEFLR1 | STD2004 | Buffalo | HotelSmall | REARSTORAGEFLR1 | 20.07 | 1 | No |  | 35.77 | 0 | 8.6111 | 46.47 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallFRONTLOUNGEFLR1 | STD2004 | Buffalo | HotelSmall | FRONTLOUNGEFLR1 | 163.06 | 1 | Yes | SAC_FRONTLOUNGE | 94.02 | 14.83 | 13.9931 | 3.08 | 26.06 | 0 | 0.3727 |  | 0.0010252 | 0 | 0
HotelSmallRESTROOMFLR1 | STD2004 | Buffalo | HotelSmall | RESTROOMFLR1 | 32.61 | 1 | Yes | SAC_RESTROOM | 13.29 | 0 | 9.6875 | 18.58 | 0 | 0 | 0 |  | 0.0010252 | 0 | 0
HotelSmallMEETINGROOMFLR1 | STD2004 | Buffalo | HotelSmall | MEETINGROOMFLR1 | 80.27 | 1 | Yes | SAC_MEETINGROOM | 32.7 | 4.93 | 13.9931 | 1.87 | 6.18 | 0 | 0.4078 |  | 0.0010252 | 0 | 0
HotelSmallMECHANICALROOMFLR1 | STD2004 | Buffalo | HotelSmall | MECHANICALROOMFLR1 | 32.61 | 1 | Yes | MechanicalRoomFlr1 Unit Heater | 13.29 | 0 | 16.1458 | 61.88 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM101 | STD2004 | Buffalo | HotelSmall | GUESTROOM101 | 32.61 | 1 | Yes | 101 PTAC | 13.29 | 1.64 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM102 | STD2004 | Buffalo | HotelSmall | GUESTROOM102 | 32.61 | 1 | Yes | 102 PTAC | 13.29 | 1.64 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM103 | STD2004 | Buffalo | HotelSmall | GUESTROOM103 | 32.61 | 1 | Yes | 103 PTAC | 13.29 | 1.64 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM104 | STD2004 | Buffalo | HotelSmall | GUESTROOM104 | 32.61 | 1 | Yes | 104 PTAC | 13.29 | 1.64 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM105 | STD2004 | Buffalo | HotelSmall | GUESTROOM105 | 32.61 | 1 | Yes | 105 PTAC | 13.29 | 1.64 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallEMPLOYEELOUNGEFLR1 | STD2004 | Buffalo | HotelSmall | EMPLOYEELOUNGEFLR1 | 32.61 | 1 | Yes | SAC_EMPLOYEELOUNGE | 13.29 | 1.64 | 12.9167 | 1.81 | 21.51 | 0 | 0.1657 |  | 0.0010252 | 0 | 0
HotelSmallLAUNDRYROOMFLR1 | STD2004 | Buffalo | HotelSmall | LAUNDRYROOMFLR1 | 97.83 | 1 | No |  | 39.86 | 4.93 | 6.4583 | 9.29 | 437.5596 | 40096.0281 |  |  | 0.0010252 | 0 | 0
HotelSmallELEVATORCOREFLR1 | STD2004 | Buffalo | HotelSmall | ELEVATORCOREFLR1 | 15.05 | 1 | No |  | 6.13 | 0 | 0 | 61.94 | 1086.2447 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallEXERCISECENTERFLR1 | STD2004 | Buffalo | HotelSmall | EXERCISECENTERFLR1 | 32.61 | 1 | Yes | SAC_EXERCISECENTER | 13.29 | 1.64 | 9.6875 | 4.66 | 18.59 | 0 | 0.0248 |  | 0.0010252 | 0 | 0
HotelSmallFRONTOFFICEFLR1 | STD2004 | Buffalo | HotelSmall | FRONTOFFICEFLR1 | 130.44 | 1 | Yes | SAC_FRONTOFFICE | 53.14 | 6.57 | 11.8403 | 13.04 | 13.78 | 0 | 0.0663 |  | 0.0010252 | 0 | 0
HotelSmallFRONTSTAIRSFLR1 | STD2004 | Buffalo | HotelSmall | FRONTSTAIRSFLR1 | 20.07 | 1 | Yes | FrontStairsFlr1 Unit Heater | 35.77 | 0 | 6.4583 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallFRONTSTORAGEFLR1 | STD2004 | Buffalo | HotelSmall | FRONTSTORAGEFLR1 | 12.54 | 1 | No |  | 5.11 | 0 | 8.6111 | 46.45 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallREARSTAIRSFLR2 | STD2004 | Buffalo | HotelSmall | REARSTAIRSFLR2 | 20.07 | 1 | Yes | RearStairsFlr2 Unit Heater | 29.27 | 0 | 6.4583 | 18.59 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallCORRIDORFLR2 | STD2004 | Buffalo | HotelSmall | CORRIDORFLR2 | 125.42 | 1 | Yes | CorridorFlr2 PTAC | 18.39 | 2.62 | 5.3819 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallREARSTORAGEFLR2 | STD2004 | Buffalo | HotelSmall | REARSTORAGEFLR2 | 20.07 | 1 | No |  | 29.27 | 0 | 8.6111 | 46.47 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM201 | STD2004 | Buffalo | HotelSmall | GUESTROOM201 | 32.61 | 1 | Yes | 201 PTAC | 33.45 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM202_205 | STD2004 | Buffalo | HotelSmall | GUESTROOM202_205 | 130.45 | 1 | Yes | 202_205 PTAC | 43.48 | 6.6 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM206_208 | STD2004 | Buffalo | HotelSmall | GUESTROOM206_208 | 105.36 | 1 | Yes | 206_208 PTAC | 35.12 | 6.71 | 11.8403 | 23.41 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM209_212 | STD2004 | Buffalo | HotelSmall | GUESTROOM209_212 | 130.45 | 1 | Yes | 209_212 PTAC | 43.48 | 6.6 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM213 | STD2004 | Buffalo | HotelSmall | GUESTROOM213 | 32.61 | 1 | Yes | 213 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM214 | STD2004 | Buffalo | HotelSmall | GUESTROOM214 | 32.61 | 1 | Yes | 214 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM215_218 | STD2004 | Buffalo | HotelSmall | GUESTROOM215_218 | 130.44 | 1 | Yes | 215_218 PTAC | 43.48 | 6.6 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallELEVATORCOREFLR2 | STD2004 | Buffalo | HotelSmall | ELEVATORCOREFLR2 | 15.05 | 1 | No |  | 5.02 | 0 | 0 | 61.94 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM219 | STD2004 | Buffalo | HotelSmall | GUESTROOM219 | 32.61 | 1 | Yes | 219 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM220_223 | STD2004 | Buffalo | HotelSmall | GUESTROOM220_223 | 130.44 | 1 | Yes | 220_223 PTAC | 43.48 | 6.6 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM224 | STD2004 | Buffalo | HotelSmall | GUESTROOM224 | 32.61 | 1 | Yes | 224 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallFRONTSTORAGEFLR2 | STD2004 | Buffalo | HotelSmall | FRONTSTORAGEFLR2 | 12.54 | 1 | No |  | 4.18 | 0 | 8.6111 | 46.45 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallFRONTSTAIRSFLR2 | STD2004 | Buffalo | HotelSmall | FRONTSTAIRSFLR2 | 20.07 | 1 | Yes | FrontStairsFlr2 Unit Heater | 29.26 | 0 | 6.4583 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallREARSTAIRSFLR3 | STD2004 | Buffalo | HotelSmall | REARSTAIRSFLR3 | 20.07 | 1 | Yes | RearStairsFlr3 Unit Heater | 29.27 | 0 | 6.4583 | 18.59 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallCORRIDORFLR3 | STD2004 | Buffalo | HotelSmall | CORRIDORFLR3 | 125.42 | 1 | Yes | CorridorFlr3 PTAC | 18.39 | 2.62 | 5.3819 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallREARSTORAGEFLR3 | STD2004 | Buffalo | HotelSmall | REARSTORAGEFLR3 | 20.07 | 1 | No |  | 29.27 | 0 | 8.6111 | 46.47 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM301 | STD2004 | Buffalo | HotelSmall | GUESTROOM301 | 32.61 | 1 | Yes | 301 PTAC | 33.45 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM302_305 | STD2004 | Buffalo | HotelSmall | GUESTROOM302_305 | 130.45 | 1 | Yes | 302_305 PTAC | 43.48 | 6.58 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM306_308 | STD2004 | Buffalo | HotelSmall | GUESTROOM306_308 | 105.36 | 1 | Yes | 306_308 PTAC | 35.12 | 6.7 | 11.8403 | 23.41 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM309_312 | STD2004 | Buffalo | HotelSmall | GUESTROOM309_312 | 130.45 | 1 | Yes | 309_312 PTAC | 43.48 | 6.58 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM313 | STD2004 | Buffalo | HotelSmall | GUESTROOM313 | 32.61 | 1 | Yes | 313 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM314 | STD2004 | Buffalo | HotelSmall | GUESTROOM314 | 32.61 | 1 | Yes | 314 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM315_318 | STD2004 | Buffalo | HotelSmall | GUESTROOM315_318 | 130.44 | 1 | Yes | 315_318 PTAC | 43.48 | 6.58 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallELEVATORCOREFLR3 | STD2004 | Buffalo | HotelSmall | ELEVATORCOREFLR3 | 15.05 | 1 | No |  | 5.02 | 0 | 0 | 61.94 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM319 | STD2004 | Buffalo | HotelSmall | GUESTROOM319 | 32.61 | 1 | Yes | 319 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM320_323 | STD2004 | Buffalo | HotelSmall | GUESTROOM320_323 | 130.44 | 1 | Yes | 320_323 PTAC | 43.48 | 6.58 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM324 | STD2004 | Buffalo | HotelSmall | GUESTROOM324 | 32.61 | 1 | Yes | 324 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallFRONTSTORAGEFLR3 | STD2004 | Buffalo | HotelSmall | FRONTSTORAGEFLR3 | 12.54 | 1 | No |  | 4.18 | 0 | 8.6111 | 46.45 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallFRONTSTAIRSFLR3 | STD2004 | Buffalo | HotelSmall | FRONTSTAIRSFLR3 | 20.07 | 1 | Yes | FrontStairsFlr3 Unit Heater | 29.26 | 0 | 6.4583 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallREARSTAIRSFLR4 | STD2004 | Buffalo | HotelSmall | REARSTAIRSFLR4 | 20.07 | 1 | Yes | RearStairsFlr4 Unit Heater | 29.27 | 0 | 6.4583 | 18.59 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallCORRIDORFLR4 | STD2004 | Buffalo | HotelSmall | CORRIDORFLR4 | 125.42 | 1 | Yes | CorridorFlr4 PTAC | 18.39 | 2.62 | 5.3819 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallREARSTORAGEFLR4 | STD2004 | Buffalo | HotelSmall | REARSTORAGEFLR4 | 20.07 | 1 | No |  | 29.27 | 0 | 8.6111 | 46.47 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM401 | STD2004 | Buffalo | HotelSmall | GUESTROOM401 | 32.61 | 1 | Yes | 401 PTAC | 33.45 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM402_405 | STD2004 | Buffalo | HotelSmall | GUESTROOM402_405 | 130.45 | 1 | Yes | 402_405 PTAC | 43.48 | 6.58 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM406_408 | STD2004 | Buffalo | HotelSmall | GUESTROOM406_408 | 105.36 | 1 | Yes | 406_408 PTAC | 35.12 | 6.7 | 11.8403 | 23.41 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM409_412 | STD2004 | Buffalo | HotelSmall | GUESTROOM409_412 | 130.45 | 1 | Yes | 409_412 PTAC | 43.48 | 6.58 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM413 | STD2004 | Buffalo | HotelSmall | GUESTROOM413 | 32.61 | 1 | Yes | 413 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM414 | STD2004 | Buffalo | HotelSmall | GUESTROOM414 | 32.61 | 1 | Yes | 414 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM415_418 | STD2004 | Buffalo | HotelSmall | GUESTROOM415_418 | 130.44 | 1 | Yes | 415_418 PTAC | 43.48 | 6.58 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallELEVATORCOREFLR4 | STD2004 | Buffalo | HotelSmall | ELEVATORCOREFLR4 | 15.05 | 1 | No |  | 5.02 | 0 | 0 | 61.94 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM419 | STD2004 | Buffalo | HotelSmall | GUESTROOM419 | 32.61 | 1 | Yes | 419 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM420_423 | STD2004 | Buffalo | HotelSmall | GUESTROOM420_423 | 130.44 | 1 | Yes | 420_423 PTAC | 43.48 | 6.58 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallGUESTROOM424 | STD2004 | Buffalo | HotelSmall | GUESTROOM424 | 32.61 | 1 | Yes | 424 PTAC | 10.87 | 1.65 | 11.8403 | 21.74 | 11.8935 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallFRONTSTORAGEFLR4 | STD2004 | Buffalo | HotelSmall | FRONTSTORAGEFLR4 | 12.54 | 1 | No |  | 4.18 | 0 | 8.6111 | 46.45 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallFRONTSTAIRSFLR4 | STD2004 | Buffalo | HotelSmall | FRONTSTAIRSFLR4 | 20.07 | 1 | Yes | FrontStairsFlr4 Unit Heater | 29.26 | 0 | 6.4583 | 18.58 | 0 | 0 |  |  | 0.0010252 | 0 | 0
HotelSmallTotal | STD2004 | Buffalo | HotelSmall | Total | 4013.58 |  |  |  | 1694.58 | 184.3 | 10.5029 | 13.37 | 24.202 | 0 |  |  | 0 | 0 | 0
HotelSmallConditioned Total | STD2004 | Buffalo | HotelSmall | Conditioned Total | 3725.09 |  |  |  | 1492.32 | 179.37 | 10.8451 | 13.04 | 10.1966 | 0 |  |  | 0 | 0 | 0
HotelSmallUnconditioned Total | STD2004 | Buffalo | HotelSmall | Unconditioned Total | 288.49 |  |  |  | 202.26 | 4.93 | 6.0842 | 20.16 | 205.0457 | 0 |  |  | 0 | 0 | 0
HotelSmallNot Part of Total | STD2004 | Buffalo | HotelSmall | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
OfficeLargeBASEMENT | STD2004 | Buffalo | OfficeLarge | BASEMENT | 2779.43 | 1 | Yes | CAV_BAS | 0 | 0 | 11.6116 | 18.58 | 4.8418 | 0 | 1.4119 |  | 0 | 0 | 0
OfficeLargeCORE_BOTTOM | STD2004 | Buffalo | OfficeLarge | CORE_BOTTOM | 2496.12 | 1 | Yes | VAV_BOT WITH REHEAT | 0 | 0 | 11.6116 | 18.58 | 8.0697 | 0 | 0 |  | 0 | 0 | 0
OfficeLargeCORE_MID | STD2004 | Buffalo | OfficeLarge | CORE_MID | 2496.12 | 10 | Yes | VAV_MID WITH REHEAT | 0 | 0 | 11.6116 | 18.58 | 8.0696 | 0 | 0 |  | 0 | 0 | 0
OfficeLargeCORE_TOP | STD2004 | Buffalo | OfficeLarge | CORE_TOP | 2496.12 | 1 | Yes | VAV_TOP WITH REHEAT | 0 | 0 | 11.6116 | 18.58 | 8.0696 | 0 | 0 |  | 0 | 0 | 0
OfficeLargePERIMETER_BOT_ZN_3 | STD2004 | Buffalo | OfficeLarge | PERIMETER_BOT_ZN_3 | 313.41 | 1 | Yes | VAV_BOT WITH REHEAT | 200.61 | 115.9 | 11.6116 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_BOT_ZN_2 | STD2004 | Buffalo | OfficeLarge | PERIMETER_BOT_ZN_2 | 201.98 | 1 | Yes | VAV_BOT WITH REHEAT | 133.74 | 77.26 | 11.6116 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_BOT_ZN_1 | STD2004 | Buffalo | OfficeLarge | PERIMETER_BOT_ZN_1 | 313.42 | 1 | Yes | VAV_BOT WITH REHEAT | 200.61 | 115.9 | 11.6116 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_BOT_ZN_4 | STD2004 | Buffalo | OfficeLarge | PERIMETER_BOT_ZN_4 | 201.98 | 1 | Yes | VAV_BOT WITH REHEAT | 133.74 | 77.26 | 11.6116 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_MID_ZN_3 | STD2004 | Buffalo | OfficeLarge | PERIMETER_MID_ZN_3 | 313.41 | 10 | Yes | VAV_MID WITH REHEAT | 200.61 | 115.9 | 11.6116 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_MID_ZN_2 | STD2004 | Buffalo | OfficeLarge | PERIMETER_MID_ZN_2 | 201.98 | 10 | Yes | VAV_MID WITH REHEAT | 133.74 | 77.26 | 11.6116 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_MID_ZN_1 | STD2004 | Buffalo | OfficeLarge | PERIMETER_MID_ZN_1 | 313.42 | 10 | Yes | VAV_MID WITH REHEAT | 200.61 | 115.9 | 11.6116 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_MID_ZN_4 | STD2004 | Buffalo | OfficeLarge | PERIMETER_MID_ZN_4 | 201.98 | 10 | Yes | VAV_MID WITH REHEAT | 133.74 | 77.26 | 11.6116 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_TOP_ZN_3 | STD2004 | Buffalo | OfficeLarge | PERIMETER_TOP_ZN_3 | 313.41 | 1 | Yes | VAV_TOP WITH REHEAT | 200.61 | 115.9 | 11.6116 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_TOP_ZN_2 | STD2004 | Buffalo | OfficeLarge | PERIMETER_TOP_ZN_2 | 201.98 | 1 | Yes | VAV_TOP WITH REHEAT | 133.74 | 77.26 | 11.6116 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_TOP_ZN_1 | STD2004 | Buffalo | OfficeLarge | PERIMETER_TOP_ZN_1 | 313.42 | 1 | Yes | VAV_TOP WITH REHEAT | 200.61 | 115.9 | 11.6116 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargePERIMETER_TOP_ZN_4 | STD2004 | Buffalo | OfficeLarge | PERIMETER_TOP_ZN_4 | 201.98 | 1 | Yes | VAV_TOP WITH REHEAT | 133.74 | 77.26 | 11.6116 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeLargeGROUNDFLOOR_PLENUM | STD2004 | Buffalo | OfficeLarge | GROUNDFLOOR_PLENUM | 3563.11 | 1 | Yes |  | 297.11 | 0 | 0 |  | 0 | 0 |  |  | 0.0010252 | 0 | 0
OfficeLargeMIDFLOOR_PLENUM | STD2004 | Buffalo | OfficeLarge | MIDFLOOR_PLENUM | 3563.11 | 10 | Yes |  | 297.11 | 0 | 0 |  | 0 | 0 |  |  | 0.0010252 | 0 | 0
OfficeLargeTOPFLOOR_PLENUM | STD2004 | Buffalo | OfficeLarge | TOPFLOOR_PLENUM | 3563.11 | 1 | Yes |  | 297.11 | 0 | 0 |  | 0 | 0 |  |  | 0.0010252 | 0 | 0
OfficeLargeDATACENTER_BOT_ZN_6 | STD2004 | Buffalo | OfficeLarge | DATACENTER_BOT_ZN_6 | 36.2 | 1 | Yes | AIRLOOP DATACENTER BOT | 0 | 0 | 14.8542 | 18.58 | 215.2992 | 0 | 0.0184 |  | 0 | 0 | 0
OfficeLargeDATACENTER_MID_ZN_6 | STD2004 | Buffalo | OfficeLarge | DATACENTER_MID_ZN_6 | 36.2 | 10 | Yes | AIRLOOP DATACENTER MID | 0 | 0 | 14.8542 | 18.58 | 215.2992 | 0 | 0.1839 |  | 0 | 0 | 0
OfficeLargeDATACENTER_TOP_ZN_6 | STD2004 | Buffalo | OfficeLarge | DATACENTER_TOP_ZN_6 | 36.2 | 1 | Yes | AIRLOOP DATACENTER TOP | 0 | 0 | 14.8542 | 18.58 | 215.2992 | 0 | 0.0184 |  | 0 | 0 | 0
OfficeLargeDATACENTER_BASEMENT_ZN_6 | STD2004 | Buffalo | OfficeLarge | DATACENTER_BASEMENT_ZN_6 | 783.68 | 1 | Yes | AIRLOOP DATACENTER BASEMENT | 0 | 0 | 11.6116 | 18.58 | 484.4232 | 0 | 0.3981 |  | 0 | 0 | 0
OfficeLargeTotal | STD2004 | Buffalo | OfficeLarge | Total | 46320.38 |  |  |  | 8024.24 | 4635.8 | 11.642 | 18.58 | 17.8789 | 0 |  |  | 0 | 0 | 0
OfficeLargeConditioned Total | STD2004 | Buffalo | OfficeLarge | Conditioned Total | 46320.38 |  |  |  | 8024.24 | 4635.8 | 11.642 | 18.58 | 17.8789 | 0 |  |  | 0 | 0 | 0
OfficeLargeUnconditioned Total | STD2004 | Buffalo | OfficeLarge | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
OfficeLargeNot Part of Total | STD2004 | Buffalo | OfficeLarge | Not Part of Total | 42757.27 |  |  |  | 3565.29 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0
OfficeMediumCORE_BOTTOM | STD2004 | Buffalo | OfficeMedium | CORE_BOTTOM | 983.54 | 1 | Yes | PACU_VAV_BOT | 0 | 0 | 11.0267 | 18.58 | 25.0366 | 0 | 0 |  | 0 | 0 | 0
OfficeMediumTOPFLOOR_PLENUM | STD2004 | Buffalo | OfficeMedium | TOPFLOOR_PLENUM | 1660.73 | 1 | Yes |  | 202.84 | 0 | 0 |  | 0 | 0 |  |  | 0.0010252 | 0 | 0
OfficeMediumMIDFLOOR_PLENUM | STD2004 | Buffalo | OfficeMedium | MIDFLOOR_PLENUM | 1660.73 | 1 | Yes |  | 202.84 | 0 | 0 |  | 0 | 0 |  |  | 0.0010252 | 0 | 0
OfficeMediumFIRSTFLOOR_PLENUM | STD2004 | Buffalo | OfficeMedium | FIRSTFLOOR_PLENUM | 1660.73 | 1 | Yes |  | 202.84 | 0 | 0 |  | 0 | 0 |  |  | 0.0010252 | 0 | 0
OfficeMediumCORE_MID | STD2004 | Buffalo | OfficeMedium | CORE_MID | 983.54 | 1 | Yes | PACU_VAV_MID | 0 | 0 | 11.0267 | 18.58 | 8.07 | 0 | 0 |  | 0 | 0 | 0
OfficeMediumCORE_TOP | STD2004 | Buffalo | OfficeMedium | CORE_TOP | 983.54 | 1 | Yes | PACU_VAV_TOP | 0 | 0 | 11.0267 | 18.58 | 8.07 | 0 | 0 |  | 0 | 0 | 0
OfficeMediumPERIMETER_TOP_ZN_3 | STD2004 | Buffalo | OfficeMedium | PERIMETER_TOP_ZN_3 | 207.34 | 1 | Yes | PACU_VAV_TOP | 136.92 | 65.26 | 11.0267 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_TOP_ZN_2 | STD2004 | Buffalo | OfficeMedium | PERIMETER_TOP_ZN_2 | 131.26 | 1 | Yes | PACU_VAV_TOP | 91.28 | 43.51 | 11.0267 | 18.58 | 8.0695 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_TOP_ZN_1 | STD2004 | Buffalo | OfficeMedium | PERIMETER_TOP_ZN_1 | 207.34 | 1 | Yes | PACU_VAV_TOP | 136.92 | 65.26 | 11.0267 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_TOP_ZN_4 | STD2004 | Buffalo | OfficeMedium | PERIMETER_TOP_ZN_4 | 131.25 | 1 | Yes | PACU_VAV_TOP | 91.28 | 43.51 | 11.0267 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_BOT_ZN_3 | STD2004 | Buffalo | OfficeMedium | PERIMETER_BOT_ZN_3 | 207.34 | 1 | Yes | PACU_VAV_BOT | 136.92 | 65.26 | 11.0267 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_BOT_ZN_2 | STD2004 | Buffalo | OfficeMedium | PERIMETER_BOT_ZN_2 | 131.26 | 1 | Yes | PACU_VAV_BOT | 91.28 | 43.51 | 11.0267 | 18.58 | 8.0695 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_BOT_ZN_1 | STD2004 | Buffalo | OfficeMedium | PERIMETER_BOT_ZN_1 | 207.34 | 1 | Yes | PACU_VAV_BOT | 136.92 | 65.26 | 11.0267 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 1.043
OfficeMediumPERIMETER_BOT_ZN_4 | STD2004 | Buffalo | OfficeMedium | PERIMETER_BOT_ZN_4 | 131.25 | 1 | Yes | PACU_VAV_BOT | 91.28 | 43.51 | 11.0267 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_MID_ZN_3 | STD2004 | Buffalo | OfficeMedium | PERIMETER_MID_ZN_3 | 207.34 | 1 | Yes | PACU_VAV_MID | 136.92 | 65.26 | 11.0267 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_MID_ZN_2 | STD2004 | Buffalo | OfficeMedium | PERIMETER_MID_ZN_2 | 131.26 | 1 | Yes | PACU_VAV_MID | 91.28 | 43.51 | 11.0267 | 18.58 | 8.0695 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_MID_ZN_1 | STD2004 | Buffalo | OfficeMedium | PERIMETER_MID_ZN_1 | 207.34 | 1 | Yes | PACU_VAV_MID | 136.92 | 65.26 | 11.0267 | 18.58 | 8.0699 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumPERIMETER_MID_ZN_4 | STD2004 | Buffalo | OfficeMedium | PERIMETER_MID_ZN_4 | 131.25 | 1 | Yes | PACU_VAV_MID | 91.28 | 43.51 | 11.0267 | 18.58 | 8.07 | 0 | 0 |  | 0.0010252 | 0 | 0
OfficeMediumTotal | STD2004 | Buffalo | OfficeMedium | Total | 4982.19 |  |  |  | 1369.16 | 652.62 | 11.0267 | 18.58 | 11.4193 | 0 |  |  | 0 | 0 | 0
OfficeMediumConditioned Total | STD2004 | Buffalo | OfficeMedium | Conditioned Total | 4982.19 |  |  |  | 1369.16 | 652.62 | 11.0267 | 18.58 | 11.4193 | 0 |  |  | 0 | 0 | 0
OfficeMediumUnconditioned Total | STD2004 | Buffalo | OfficeMedium | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
OfficeMediumNot Part of Total | STD2004 | Buffalo | OfficeMedium | Not Part of Total | 4982.19 |  |  |  | 608.51 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0
OfficeSmallCORE_ZN | STD2004 | Buffalo | OfficeSmall | CORE_ZN | 149.66 | 1 | Yes | PSZ-AC:1 | 0 | 0 | 10.6713 | 18.58 | 6.78 | 0 | 0.076 |  | 0 | 0 | 0
OfficeSmallPERIMETER_ZN_1 | STD2004 | Buffalo | OfficeSmall | PERIMETER_ZN_1 | 113.45 | 1 | Yes | PSZ-AC:2 | 84.45 | 20.63 | 10.6713 | 18.58 | 6.78 | 0 | 0.0576 |  | 0.0010252 | 0 | 0.12979
OfficeSmallPERIMETER_ZN_2 | STD2004 | Buffalo | OfficeSmall | PERIMETER_ZN_2 | 67.3 | 1 | Yes | PSZ-AC:3 | 56.3 | 11.15 | 10.6713 | 18.58 | 6.78 | 0 | 0.0342 |  | 0.0010252 | 0 | 0
OfficeSmallPERIMETER_ZN_3 | STD2004 | Buffalo | OfficeSmall | PERIMETER_ZN_3 | 113.45 | 1 | Yes | PSZ-AC:4 | 84.45 | 16.72 | 10.6713 | 18.58 | 6.78 | 0 | 0.0576 |  | 0.0010252 | 0 | 0
OfficeSmallPERIMETER_ZN_4 | STD2004 | Buffalo | OfficeSmall | PERIMETER_ZN_4 | 67.3 | 1 | Yes | PSZ-AC:5 | 56.3 | 11.15 | 10.6713 | 18.58 | 6.78 | 0 | 0.0342 |  | 0.0010252 | 0 | 0
OfficeSmallATTIC | STD2004 | Buffalo | OfficeSmall | ATTIC | 567.98 | 1 | No |  | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0.2001 | 0
OfficeSmallTotal | STD2004 | Buffalo | OfficeSmall | Total | 511.16 |  |  |  | 281.51 | 59.65 | 10.6713 | 18.58 | 6.78 | 0 |  |  | 0 | 0 | 0
OfficeSmallConditioned Total | STD2004 | Buffalo | OfficeSmall | Conditioned Total | 511.16 |  |  |  | 281.51 | 59.65 | 10.6713 | 18.58 | 6.78 | 0 |  |  | 0 | 0 | 0
OfficeSmallUnconditioned Total | STD2004 | Buffalo | OfficeSmall | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
OfficeSmallNot Part of Total | STD2004 | Buffalo | OfficeSmall | Not Part of Total | 567.98 |  |  |  | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 ANESTHESIA | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 ANESTHESIA | 10.03 | 1 | Yes | AHU-1 | 8.36 | 2.23 | 16.1458 | 4.64 | 21.53 | 0 | 0.0153 | 0.07 | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 BIO HAZ | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 BIO HAZ | 5.2 | 1 | Yes | AHU-1 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0.004 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 CAFE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 CAFE | 39.02 | 1 | Yes | AHU-1 | 18.58 | 8.92 | 9.6875 | 0.93 | 10.76 | 0 | 0.3964 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 CLEAN | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 CLEAN | 11.71 | 1 | Yes | AHU-1 | 0 | 0 | 16.1458 | 4.64 | 21.53 | 0 | 0.0178 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 CLEAN WORK | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 CLEAN WORK | 15.33 | 1 | Yes | AHU-1 | 0 | 0 | 16.1458 | 4.64 | 21.53 | 0 | 0.0234 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 DICTATION | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 DICTATION | 11.71 | 1 | Yes | AHU-1 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0.0059 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 DRESSING ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 DRESSING ROOM | 4.18 | 1 | Yes | AHU-1 | 8.36 | 2.32 | 11.8403 | 18.58 | 11.84 | 0 | 0.0021 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 ELECTRICAL ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 ELECTRICAL ROOM | 9.1 | 1 | Yes | AHU-1 | 6.5 | 0 | 16.1458 | 61.94 | 53.82 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 ELEVATOR PUMP ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | 1 | Yes | AHU-1 | 18.58 | 0 | 16.1458 | 61.94 | 1674.7675 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 HUMID | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 HUMID | 5.02 | 1 | Yes | AHU-1 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0.0025 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 IT HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 IT HALL | 13.01 | 1 | Yes | AHU-1 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.0033 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 IT ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 IT ROOM | 10.41 | 1 | Yes | AHU-1 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0.0053 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 LOBBY | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 LOBBY | 57.79 | 1 | Yes | AHU-1 | 20.44 | 8.92 | 13.9931 | 9.29 | 11.84 | 0 | 0.044 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 LOBBY HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 LOBBY HALL | 22.3 | 1 | Yes | AHU-1 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.0057 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 LOBBY TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 LOBBY TOILET | 5.02 | 1 | Yes | AHU-1 | 5.57 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.04 | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 LOCKER ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 LOCKER ROOM | 61.32 | 1 | Yes | AHU-1 | 20.44 | 5.57 | 8.6111 | 6.19 | 32.29 | 0 | 0.0701 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 LOCKER ROOM HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 LOCKER ROOM HALL | 46.08 | 1 | Yes | AHU-1 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.0117 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 LOUNGE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 LOUNGE | 33.45 | 1 | Yes | AHU-1 | 0 | 0 | 8.6111 | 6.19 | 32.29 | 0 | 0.0382 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 MED GAS | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 MED GAS | 5.2 | 1 | Yes | AHU-1 | 13.94 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0.004 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 MRI CONTROL ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 MRI CONTROL ROOM | 15.61 | 1 | Yes | AHU-1 | 4.65 | 0 | 4.3056 | 4.64 | 107.64 | 0 | 0.0238 | 0.16 | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 MRI HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 MRI HALL | 13.66 | 1 | Yes | AHU-1 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.0035 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 MRI ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 MRI ROOM | 40.88 | 1 | Yes | AHU-1 | 0 | 0 | 4.3056 | 4.64 | 107.64 | 0 | 0.0623 | 0.42 | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 MRI TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 MRI TOILET | 5.02 | 1 | Yes | AHU-1 | 5.57 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.04 | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 NOURISHMENT | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 NOURISHMENT | 16.91 | 1 | Yes | AHU-1 | 0 | 0 | 10.7639 | 6.19 | 21.53 | 0 | 0.0258 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 NURSE HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 NURSE HALL | 46.08 | 1 | Yes | AHU-1 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.0117 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 NURSE JANITOR | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 NURSE JANITOR | 5.02 | 1 | Yes | AHU-1 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0.0038 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 NURSE STATION | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 NURSE STATION | 24.25 | 1 | Yes | AHU-1 | 0 | 0 | 10.7639 | 6.19 | 21.53 | 0 | 0.037 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 NURSE TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 NURSE TOILET | 5.02 | 1 | Yes | AHU-1 | 0 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.04 | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 OFFICE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 OFFICE | 44.87 | 1 | Yes | AHU-1 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0.0228 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 OPERATING ROOM 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 OPERATING ROOM 1 | 42.74 | 1 | Yes | AHU-1 | 39.95 | 8.92 | 23.6806 | 4.64 | 118.36 | 3217.9755 | 0.2388 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 OPERATING ROOM 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 OPERATING ROOM 2 | 44.59 | 1 | Yes | AHU-1 | 22.3 | 6.7 | 23.6806 | 4.64 | 118.36 | 3357.8875 | 0.2492 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 OPERATING ROOM 3 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 OPERATING ROOM 3 | 44.22 | 1 | Yes | AHU-1 | 0 | 0 | 23.6806 | 4.64 | 118.36 | 3329.9051 | 0.2471 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 PACU | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 PACU | 10.03 | 1 | Yes | AHU-1 | 0 | 0 | 8.6111 | 4.64 | 32.29 | 0 | 0.0323 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 PRE-OP HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 PRE-OP HALL | 49.05 | 1 | Yes | AHU-1 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.0125 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 PRE-OP ROOM 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 PRE-OP ROOM 1 | 17.56 | 1 | Yes | AHU-1 | 3.72 | 0 | 7.5347 | 9.29 | 21.53 | 0 | 0.052 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 PRE-OP ROOM 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 PRE-OP ROOM 2 | 31.4 | 1 | Yes | AHU-1 | 0 | 0 | 7.5347 | 9.29 | 21.53 | 0 | 0.0931 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 PRE-OP TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 PRE-OP TOILET | 5.02 | 1 | Yes | AHU-1 | 5.57 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.04 | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 PROCEDURE ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 PROCEDURE ROOM | 26.48 | 1 | Yes | AHU-1 | 17.65 | 5.57 | 16.1458 | 4.64 | 32.29 | 0 | 0.1076 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 RECEPTION | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 RECEPTION | 47.29 | 1 | Yes | AHU-1 | 12.08 | 3.34 | 13.9931 | 3.1 | 11.84 | 0 | 0.1081 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 RECEPTION HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 RECEPTION HALL | 11.89 | 1 | Yes | AHU-1 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.003 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 RECOVERY ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 RECOVERY ROOM | 50.17 | 1 | Yes | AHU-1 | 41.81 | 8.92 | 8.6111 | 4.64 | 32.29 | 0 | 0.1614 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 SCHEDULING | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 SCHEDULING | 11.06 | 1 | Yes | AHU-1 | 6.5 | 0.74 | 11.8403 | 18.58 | 11.84 | 0 | 0.0056 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 SCRUB | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 SCRUB | 7.8 | 1 | Yes | AHU-1 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.002 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 SOIL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 SOIL | 11.71 | 1 | Yes | AHU-1 | 0 | 0 | 16.1458 | 4.64 | 21.53 | 0 | 0.0178 | 0.1 | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 SOIL HOLD | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 SOIL HOLD | 5.2 | 1 | Yes | AHU-1 | 0 | 0 | 16.1458 | 4.64 | 21.53 | 0 | 0.0079 | 0.04 | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 SOIL WORK | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 SOIL WORK | 16.72 | 1 | Yes | AHU-1 | 0 | 0 | 16.1458 | 4.64 | 21.53 | 0 | 0.0255 | 0.14 | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 STEP DOWN | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 STEP DOWN | 27.87 | 1 | Yes | AHU-1 | 34.37 | 6.69 | 8.6111 | 4.64 | 32.29 | 0 | 0.0897 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 STERILE HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 STERILE HALL | 57.23 | 1 | Yes | AHU-1 | 7.43 | 2.23 | 10.3041 | 18.58 | 4.31 | 0 | 0.0145 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 STERILE STORAGE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 STERILE STORAGE | 36.79 | 1 | Yes | AHU-1 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0.028 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 STORAGE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 STORAGE | 85.47 | 1 | Yes | AHU-1 | 58.53 | 8.36 | 9.6875 | 46.45 | 1.08 | 0 | 0.0651 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 SUB-STERILE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 SUB-STERILE | 18.21 | 1 | Yes | AHU-1 | 13.01 | 2.98 | 10.3041 | 18.58 | 4.31 | 0 | 0.0046 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 UTILITY HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 UTILITY HALL | 23.78 | 1 | Yes | AHU-1 | 14.86 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.006 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 UTILITY JANITOR | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 UTILITY JANITOR | 3.9 | 1 | Yes | AHU-1 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0.003 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 1 UTILITY ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 UTILITY ROOM | 33.45 | 1 | Yes | AHU-1 | 16.72 | 2.23 | 9.6875 | 46.45 | 1.08 | 0 | 0.0255 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 1 VESTIBULE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 1 VESTIBULE | 6.69 | 1 | Yes | AHU-1 | 7.43 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0.0017 |  | 0.0010252 | 0 | 1.186
OutPatientHealthCareFLOOR 2 CONFERENCE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 CONFERENCE | 31.22 | 1 | Yes | AHU-2 | 37.16 | 8.92 | 13.9931 | 1.86 | 10.76 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 CONFERENCE TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 CONFERENCE TOILET | 5.95 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.05 | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 DICTATION | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 DICTATION | 6.5 | 1 | Yes | AHU-2 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 1 | 33.45 | 1 | Yes | AHU-2 | 39.02 | 8.92 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 2 | 50.17 | 1 | Yes | AHU-2 | 16.72 | 3.72 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 3 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 3 | 66.89 | 1 | Yes | AHU-2 | 22.3 | 5.95 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 4 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 4 | 7.8 | 1 | Yes | AHU-2 | 6.5 | 2.23 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 5 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 5 | 32.52 | 1 | Yes | AHU-2 | 23.23 | 5.95 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 6 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 6 | 20.9 | 1 | Yes | AHU-2 | 13.94 | 4.18 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 7 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 7 | 73.58 | 1 | Yes | AHU-2 | 22.3 | 5.57 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 8 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 8 | 25.08 | 1 | Yes | AHU-2 | 16.72 | 5.57 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM 9 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM 9 | 36.79 | 1 | Yes | AHU-2 | 11.15 | 2.79 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM HALL 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM HALL 1 | 16.72 | 1 | Yes | AHU-2 | 5.57 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM HALL 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM HALL 2 | 16.72 | 1 | Yes | AHU-2 | 5.57 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM HALL 3 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM HALL 3 | 16.72 | 1 | Yes | AHU-2 | 5.57 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM HALL 4 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM HALL 4 | 18.39 | 1 | Yes | AHU-2 | 5.57 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM HALL 5 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM HALL 5 | 18.39 | 1 | Yes | AHU-2 | 5.57 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 EXAM HALL 6 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 EXAM HALL 6 | 18.39 | 1 | Yes | AHU-2 | 5.57 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 JANITOR | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 JANITOR | 5.85 | 1 | Yes | AHU-2 | 14.86 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 LOUNGE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 LOUNGE | 7.43 | 1 | Yes | AHU-2 | 0 | 0 | 8.6111 | 6.19 | 32.29 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 NURSE STATION 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 NURSE STATION 1 | 13.94 | 1 | Yes | AHU-2 | 0 | 0 | 10.7639 | 6.19 | 21.53 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 NURSE STATION 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 NURSE STATION 2 | 16.72 | 1 | Yes | AHU-2 | 0 | 0 | 10.7639 | 6.19 | 21.53 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 OFFICE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 OFFICE | 52.03 | 1 | Yes | AHU-2 | 37.16 | 8.93 | 11.8403 | 18.58 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 OFFICE HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 OFFICE HALL | 41.25 | 1 | Yes | AHU-2 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 RECEPTION | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 RECEPTION | 91.42 | 1 | Yes | AHU-2 | 45.52 | 16.72 | 13.9931 | 3.1 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 RECEPTION HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 RECEPTION HALL | 52.4 | 1 | Yes | AHU-2 | 6.5 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 RECEPTION TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 RECEPTION TOILET | 11.71 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.1 | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 SCHEDULING 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 SCHEDULING 1 | 30.1 | 1 | Yes | AHU-2 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 SCHEDULING 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 SCHEDULING 2 | 31.77 | 1 | Yes | AHU-2 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 STORAGE 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 STORAGE 1 | 5.2 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 STORAGE 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 STORAGE 2 | 11.15 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 STORAGE 3 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 STORAGE 3 | 13.38 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 UTILITY | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 UTILITY | 11.71 | 1 | Yes | AHU-2 | 8.36 | 2.23 | 9.6875 | 46.45 | 1.08 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 WORK | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 WORK | 157.01 | 1 | Yes | AHU-2 | 24.15 | 5.57 | 11.8403 | 18.58 | 9.7803 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 WORK HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 WORK HALL | 77.48 | 1 | Yes | AHU-2 | 5.57 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0 | 0 | 0
OutPatientHealthCareFLOOR 2 WORK TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 WORK TOILET | 5.02 | 1 | Yes | AHU-2 | 5.57 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.04 | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 2 X-RAY | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 2 X-RAY | 83.61 | 1 | Yes | AHU-2 | 0 | 0 | 4.3056 | 4.64 | 107.64 | 0 | 0 | 0.85 | 0 | 0 | 0
OutPatientHealthCareFLOOR 3 DRESSING ROOM | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 DRESSING ROOM | 3.9 | 1 | Yes | AHU-2 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 ELEVATOR HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 ELEVATOR HALL | 34.37 | 1 | Yes | AHU-2 | 3.72 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 HUMID | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 HUMID | 10.03 | 1 | Yes | AHU-2 | 0 | 0 | 11.8403 | 18.58 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 JANITOR | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 JANITOR | 5.85 | 1 | Yes | AHU-2 | 14.86 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 LOCKER | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 LOCKER | 11.15 | 1 | Yes | AHU-2 | 0 | 0 | 8.6111 | 6.19 | 32.29 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 LOUNGE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 LOUNGE | 70.51 | 1 | Yes | AHU-2 | 21.37 | 5.57 | 8.6111 | 6.19 | 32.29 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 LOUNGE TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 LOUNGE TOILET | 17.84 | 1 | Yes | AHU-2 | 11.15 | 4.18 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.15 | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 MECHANICAL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 MECHANICAL | 32.52 | 1 | Yes | AHU-2 | 23.23 | 5.95 | 16.1458 | 61.94 | 53.82 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 MECHANICAL HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 MECHANICAL HALL | 27.87 | 1 | Yes | AHU-2 | 0 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 OFFICE | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 OFFICE | 282.05 | 1 | Yes | AHU-2 | 68.75 | 19.51 | 11.8403 | 18.58 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 OFFICE HALL | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 OFFICE HALL | 77.48 | 1 | Yes | AHU-2 | 5.57 | 0 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 OFFICE TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 OFFICE TOILET | 5.02 | 1 | Yes | AHU-2 | 5.57 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.04 | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 PHYSICAL THERAPY 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | 1 | Yes | AHU-2 | 78.97 | 28.99 | 9.6875 | 4.64 | 16.15 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 PHYSICAL THERAPY 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 PHYSICAL THERAPY 2 | 55 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 4.64 | 16.15 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 PHYSICAL THERAPY TOILET | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 18.58 | 4.31 | 0 | 0 | 0.07 | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 STORAGE 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 STORAGE 1 | 10.03 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 STORAGE 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 STORAGE 2 | 7.8 | 1 | Yes | AHU-2 | 0 | 0 | 9.6875 | 46.45 | 1.08 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 TREATMENT | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 TREATMENT | 44.22 | 1 | Yes | AHU-2 | 0 | 0 | 16.1458 | 4.64 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 UNDEVELOPED 1 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 UNDEVELOPED 1 | 210.7 | 1 | Yes | AHU-2 | 66.89 | 25.64 | 9.6875 | 46.45 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 UNDEVELOPED 2 | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 UNDEVELOPED 2 | 107.02 | 1 | Yes | AHU-2 | 52.03 | 13.38 | 9.6875 | 46.45 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 UTILITY | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 UTILITY | 20.07 | 1 | Yes | AHU-2 | 0 | 0 | 16.1458 | 46.45 | 1.08 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareFLOOR 3 WORK | STD2004 | Buffalo | OutPatientHealthCare | FLOOR 3 WORK | 53.33 | 1 | Yes | AHU-2 | 38.09 | 8.93 | 11.8403 | 18.58 | 11.84 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareNE STAIR | STD2004 | Buffalo | OutPatientHealthCare | NE STAIR | 15.61 | 1 | Yes | AHU-2 | 97.55 | 12.03 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareNW ELEVATOR | STD2004 | Buffalo | OutPatientHealthCare | NW ELEVATOR | 13.01 | 1 | Yes | AHU-2 | 75.25 | 0 | 10.3041 | 61.94 | 4.31 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareNW STAIR | STD2004 | Buffalo | OutPatientHealthCare | NW STAIR | 17.84 | 1 | Yes | AHU-2 | 111.48 | 11.15 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareSW STAIR | STD2004 | Buffalo | OutPatientHealthCare | SW STAIR | 8.92 | 1 | Yes | AHU-2 | 55.74 | 1.11 | 10.3041 | 18.58 | 4.31 | 0 | 0 |  | 0.0010252 | 0 | 0
OutPatientHealthCareTotal | STD2004 | Buffalo | OutPatientHealthCare | Total | 3804.01 |  |  |  | 1553.34 | 308.36 | 11.6268 | 8.02 | 22.9367 | 0 |  |  | 0 | 0 | 0
OutPatientHealthCareConditioned Total | STD2004 | Buffalo | OutPatientHealthCare | Conditioned Total | 3804.01 |  |  |  | 1553.34 | 308.36 | 11.6268 | 8.02 | 22.9367 | 0 |  |  | 0 | 0 | 0
OutPatientHealthCareUnconditioned Total | STD2004 | Buffalo | OutPatientHealthCare | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
OutPatientHealthCareNot Part of Total | STD2004 | Buffalo | OutPatientHealthCare | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
RestaurantFastFoodDINING | STD2004 | Buffalo | RestaurantFastFood | DINING | 116.17 | 1 | Yes | PSZ-AC_1:1 | 92.94 | 26.02 | 9.2637 | 1.33 | 116.7869 | 0 | 0.8262 | 0.83 | 0.0010252 | 0 | 0.90283
RestaurantFastFoodKITCHEN | STD2004 | Buffalo | RestaurantFastFood | KITCHEN | 116.17 | 1 | Yes | PSZ-AC_2:2 | 92.94 | 0 | 11.9458 | 18.52 | 1074.0064 | 91932.6006 | 0.1017 | 1.56 | 0.0010252 | 0 | 0
RestaurantFastFoodATTIC | STD2004 | Buffalo | RestaurantFastFood | ATTIC | 232.34 | 1 | No |  | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0.0729 | 0
RestaurantFastFoodTotal | STD2004 | Buffalo | RestaurantFastFood | Total | 232.34 |  |  |  | 185.89 | 26.02 | 10.6047 | 2.48 | 595.3967 | 0 |  |  | 0 | 0 | 0
RestaurantFastFoodConditioned Total | STD2004 | Buffalo | RestaurantFastFood | Conditioned Total | 232.34 |  |  |  | 185.89 | 26.02 | 10.6047 | 2.48 | 595.3967 | 0 |  |  | 0 | 0 | 0
RestaurantFastFoodUnconditioned Total | STD2004 | Buffalo | RestaurantFastFood | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
RestaurantFastFoodNot Part of Total | STD2004 | Buffalo | RestaurantFastFood | Not Part of Total | 232.34 |  |  |  | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0
RestaurantSitDownDINING | STD2004 | Buffalo | RestaurantSitDown | DINING | 371.75 | 1 | Yes | PSZ-AC_1:1 | 169.19 | 47.17 | 20.6319 | 1.33 | 64.9275 | 0 | 2.6439 | 2.64 | 0.0010252 | 0 | 0.61447
RestaurantSitDownKITCHEN | STD2004 | Buffalo | RestaurantSitDown | KITCHEN | 139.41 | 1 | Yes | PSZ-AC_2:2 | 106.53 | 0 | 11.3949 | 18.52 | 1063.0801 | 90512.4824 | 0.1242 | 2.83 | 0.0010252 | 0 | 0
RestaurantSitDownATTIC | STD2004 | Buffalo | RestaurantSitDown | ATTIC | 511.15 | 1 | No |  | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0.2378 | 0
RestaurantSitDownTotal | STD2004 | Buffalo | RestaurantSitDown | Total | 511.15 |  |  |  | 275.72 | 47.17 | 18.1127 | 1.78 | 337.1505 | 0 |  |  | 0 | 0 | 0
RestaurantSitDownConditioned Total | STD2004 | Buffalo | RestaurantSitDown | Conditioned Total | 511.15 |  |  |  | 275.72 | 47.17 | 18.1127 | 1.78 | 337.1505 | 0 |  |  | 0 | 0 | 0
RestaurantSitDownUnconditioned Total | STD2004 | Buffalo | RestaurantSitDown | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
RestaurantSitDownNot Part of Total | STD2004 | Buffalo | RestaurantSitDown | Not Part of Total | 511.15 |  |  |  | 0 | 0 | 0 |  | 0 | 0 |  |  | 0 | 0 | 0
RetailStandaloneBACK_SPACE | STD2004 | Buffalo | RetailStandalone | BACK_SPACE | 379.89 | 1 | Yes | PSZ-AC:1 | 416.17 | 0 | 9.0271 | 46.45 | 8.07 | 0 | 0.2895 |  | 0.0010252 | 0 | 0
RetailStandaloneCORE_RETAIL | STD2004 | Buffalo | RetailStandalone | CORE_RETAIL | 1600.48 | 1 | Yes | PSZ-AC:2 | 356.86 | 0 | 18.2986 | 6.19 | 3.23 | 0 | 2.4391 |  | 0.0010252 | 0 | 0
RetailStandalonePOINT_OF_SALE | STD2004 | Buffalo | RetailStandalone | POINT_OF_SALE | 150.81 | 1 | Yes | PSZ-AC:3 | 189.8 | 38.06 | 18.2986 | 6.19 | 21.52 | 0 | 0.2298 |  | 0.0010252 | 0 | 0
RetailStandaloneFRONT_RETAIL | STD2004 | Buffalo | RetailStandalone | FRONT_RETAIL | 150.81 | 1 | Yes | PSZ-AC:4 | 189.8 | 38.06 | 18.2986 | 6.19 | 3.23 | 0 | 0.2298 |  | 0.0010252 | 0 | 0
RetailStandaloneFRONT_ENTRY | STD2004 | Buffalo | RetailStandalone | FRONT_ENTRY | 12 | 1 | Yes | Front_Entry Unit Heater | 24.38 | 7.83 | 10.9792 | 6.19 | 0 | 0 |  |  | 0.0010252 | 0 | 1.4187
RetailStandaloneTotal | STD2004 | Buffalo | RetailStandalone | Total | 2293.99 |  |  |  | 1177.02 | 83.95 | 16.725 | 7.23 | 5.217 | 0 |  |  | 0 | 0 | 0
RetailStandaloneConditioned Total | STD2004 | Buffalo | RetailStandalone | Conditioned Total | 2293.99 |  |  |  | 1177.02 | 83.95 | 16.725 | 7.23 | 5.217 | 0 |  |  | 0 | 0 | 0
RetailStandaloneUnconditioned Total | STD2004 | Buffalo | RetailStandalone | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
RetailStandaloneNot Part of Total | STD2004 | Buffalo | RetailStandalone | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
RetailStripmallLGSTORE1 | STD2004 | Buffalo | RetailStripmall | LGSTORE1 | 348.39 | 1 | Yes | PSZ-AC_1:1 | 276.3 | 20.77 | 26.4001 | 6.19 | 4.3 | 0 | 0.5309 |  | 0.0010252 | 0 | 0.38888
RetailStripmallSMSTORE1 | STD2004 | Buffalo | RetailStripmall | SMSTORE1 | 174.19 | 1 | Yes | PSZ-AC_2:2 | 78.94 | 10.38 | 26.6665 | 6.19 | 4.3 | 0 | 0.2655 |  | 0.0010252 | 0 | 0.22229
RetailStripmallSMSTORE2 | STD2004 | Buffalo | RetailStripmall | SMSTORE2 | 174.19 | 1 | Yes | PSZ-AC_3:3 | 78.94 | 10.36 | 20.4514 | 6.19 | 4.3 | 0 | 0.2655 |  | 0.0010252 | 0 | 0.22229
RetailStripmallSMSTORE3 | STD2004 | Buffalo | RetailStripmall | SMSTORE3 | 174.19 | 1 | Yes | PSZ-AC_4:4 | 78.94 | 10.36 | 20.4514 | 6.19 | 4.3 | 0 | 0.2655 |  | 0.0010252 | 0 | 0.22229
RetailStripmallSMSTORE4 | STD2004 | Buffalo | RetailStripmall | SMSTORE4 | 174.19 | 1 | Yes | PSZ-AC_5:5 | 78.94 | 10.36 | 20.4514 | 6.19 | 4.3 | 0 | 0.2655 |  | 0.0010252 | 0 | 0.22229
RetailStripmallLGSTORE2 | STD2004 | Buffalo | RetailStripmall | LGSTORE2 | 348.39 | 1 | Yes | PSZ-AC_6:6 | 157.89 | 20.72 | 15.8794 | 6.19 | 4.3 | 0 | 0.5309 |  | 0.0010252 | 0 | 0.38888
RetailStripmallSMSTORE5 | STD2004 | Buffalo | RetailStripmall | SMSTORE5 | 174.19 | 1 | Yes | PSZ-AC_7:7 | 78.94 | 10.36 | 16.1458 | 6.19 | 4.3 | 0 | 0.2655 |  | 0.0010252 | 0 | 0.22229
RetailStripmallSMSTORE6 | STD2004 | Buffalo | RetailStripmall | SMSTORE6 | 174.19 | 1 | Yes | PSZ-AC_8:8 | 78.94 | 10.36 | 16.1458 | 6.19 | 4.3 | 0 | 0.2655 |  | 0.0010252 | 0 | 0.22229
RetailStripmallSMSTORE7 | STD2004 | Buffalo | RetailStripmall | SMSTORE7 | 174.19 | 1 | Yes | PSZ-AC_9:9 | 78.94 | 10.36 | 16.1458 | 6.19 | 4.3 | 0 | 0.2655 |  | 0.0010252 | 0 | 0.22229
RetailStripmallSMSTORE8 | STD2004 | Buffalo | RetailStripmall | SMSTORE8 | 174.19 | 1 | Yes | PSZ-AC_10:10 | 197.36 | 10.36 | 16.1458 | 6.19 | 4.3 | 0 | 0.2655 |  | 0.0010252 | 0 | 0.22229
RetailStripmallTotal | STD2004 | Buffalo | RetailStripmall | Total | 2090.32 |  |  |  | 1184.15 | 124.4 | 19.7636 | 6.19 | 4.3 | 0 |  |  | 0 | 0 | 0
RetailStripmallConditioned Total | STD2004 | Buffalo | RetailStripmall | Conditioned Total | 2090.32 |  |  |  | 1184.15 | 124.4 | 19.7636 | 6.19 | 4.3 | 0 |  |  | 0 | 0 | 0
RetailStripmallUnconditioned Total | STD2004 | Buffalo | RetailStripmall | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
RetailStripmallNot Part of Total | STD2004 | Buffalo | RetailStripmall | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
SchoolPrimaryCORNER_CLASS_1_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_1 | 80 | 28 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryMULT_CLASS_1_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_1 | 212 | 74.2 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCORRIDOR_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORRIDOR_POD_1_ZN_1_FLR_1 | 192 | 1 | Yes | VAV_POD_1 | 12 | 4.2 | 5.481 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCORNER_CLASS_2_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_1 | 80 | 28 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryMULT_CLASS_2_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_1 | 212 | 74.2 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCORNER_CLASS_1_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_2 | 80 | 28 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryMULT_CLASS_1_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_2 | 212 | 74.2 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCORRIDOR_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORRIDOR_POD_2_ZN_1_FLR_1 | 192 | 1 | Yes | VAV_POD_2 | 12 | 4.2 | 5.481 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCORNER_CLASS_2_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_2 | 80 | 28 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryMULT_CLASS_2_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_2 | 212 | 74.2 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCORNER_CLASS_1_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_3 | 80 | 28 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryMULT_CLASS_1_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_3 | 212 | 74.2 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCORRIDOR_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORRIDOR_POD_3_ZN_1_FLR_1 | 192 | 1 | Yes | VAV_POD_3 | 12 | 4.2 | 5.481 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCORNER_CLASS_2_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_3 | 80 | 27.95 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryMULT_CLASS_2_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 315 | 1 | Yes | VAV_POD_3 | 140 | 49 | 15.0695 | 3.72 | 15 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryCOMPUTER_CLASS_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | COMPUTER_CLASS_ZN_1_FLR_1 | 162 | 1 | Yes | VAV_OTHER | 72 | 25.2 | 15.0695 | 3.72 | 20 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryMAIN_CORRIDOR_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | MAIN_CORRIDOR_ZN_1_FLR_1 | 546 | 1 | Yes | VAV_OTHER | 36 | 12.6 | 5.481 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryLOBBY_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | LOBBY_ZN_1_FLR_1 | 171 | 1 | Yes | VAV_OTHER | 76 | 26.6 | 13.9931 | 9.29 | 4 | 0 | 0 |  | 0.0010252 | 0 | 4.3443
SchoolPrimaryMECH_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | MECH_ZN_1_FLR_1 | 252 | 1 | Yes | VAV_OTHER | 0 | 0 | 16.1458 | 61.93 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryBATH_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | BATH_ZN_1_FLR_1 | 190 | 1 | Yes | VAV_OTHER | 40 | 14 | 9.6875 | 18.58 | 4 | 0 | 0 | 0.28 | 0.0010252 | 0 | 0
SchoolPrimaryOFFICES_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | OFFICES_ZN_1_FLR_1 | 441 | 1 | Yes | VAV_OTHER | 168 | 58.8 | 11.8403 | 18.58 | 10.8 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolPrimaryGYM_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | GYM_ZN_1_FLR_1 | 357 | 1 | Yes | PSZ-AC_2:5 | 68 | 23.8 | 13.3472 | 3.1 | 5 | 0 | 1.0881 | 0 | 0.0010252 | 0 | 0
SchoolPrimaryKITCHEN_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | KITCHEN_ZN_1_FLR_1 | 168 | 1 | Yes | PSZ-AC_1:6 | 32 | 11.2 | 12.9167 | 6.22 | 1632.7613 | 240424.8 | 0.446 | 2.36 | 0.0010252 | 0 | 0
SchoolPrimaryCAFETERIA_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | CAFETERIA_ZN_1_FLR_1 | 315 | 1 | Yes | PSZ-AC_2:7 | 144 | 50.4 | 9.6875 | 0.93 | 25.39 | 0 | 3.2004 | 0 | 0.0010252 | 0 | 0
SchoolPrimaryLIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolPrimary | LIBRARY_MEDIA_CENTER_ZN_1_FLR_1 | 399 | 1 | Yes | VAV_OTHER | 160 | 56 | 16.684 | 9.29 | 15 | 0 | 0 | 0 | 0.0010252 | 0 | 0
SchoolPrimaryTotal | STD2004 | Buffalo | SchoolPrimary | Total | 6871 |  |  |  | 2512 | 879.14 | 12.8652 | 4.37 | 51.8027 | 0 |  |  | 0 | 0 | 0
SchoolPrimaryConditioned Total | STD2004 | Buffalo | SchoolPrimary | Conditioned Total | 6871 |  |  |  | 2512 | 879.14 | 12.8652 | 4.37 | 51.8027 | 0 |  |  | 0 | 0 | 0
SchoolPrimaryUnconditioned Total | STD2004 | Buffalo | SchoolPrimary | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
SchoolPrimaryNot Part of Total | STD2004 | Buffalo | SchoolPrimary | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
SchoolSecondaryCORNER_CLASS_1_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_1_POD_1_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_1 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_1_POD_1_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_1_POD_1_ZN_1_FLR_2 | 99 | 1 | Yes | VAV_POD_1 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_1_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_1_POD_1_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_1 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_1_POD_1_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_1_POD_1_ZN_1_FLR_2 | 477 | 1 | Yes | VAV_POD_1 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORRIDOR_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORRIDOR_POD_1_ZN_1_FLR_1 | 320 | 1 | Yes | VAV_POD_1 | 20 | 7 | 5.5178 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORRIDOR_POD_1_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORRIDOR_POD_1_ZN_1_FLR_2 | 320 | 1 | Yes | VAV_POD_1 | 20 | 7 | 5.5178 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_2_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_2_POD_1_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_1 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_2_POD_1_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_2_POD_1_ZN_1_FLR_2 | 99 | 1 | Yes | VAV_POD_1 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_2_POD_1_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_2_POD_1_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_1 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_2_POD_1_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_2_POD_1_ZN_1_FLR_2 | 477 | 1 | Yes | VAV_POD_1 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_1_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_1_POD_2_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_2 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_1_POD_2_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_1_POD_2_ZN_1_FLR_2 | 99 | 1 | Yes | VAV_POD_2 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_1_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_1_POD_2_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_2 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_1_POD_2_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_1_POD_2_ZN_1_FLR_2 | 477 | 1 | Yes | VAV_POD_2 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORRIDOR_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORRIDOR_POD_2_ZN_1_FLR_1 | 320 | 1 | Yes | VAV_POD_2 | 20 | 7 | 5.5178 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORRIDOR_POD_2_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORRIDOR_POD_2_ZN_1_FLR_2 | 320 | 1 | Yes | VAV_POD_2 | 20 | 7 | 5.5178 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_2_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_2_POD_2_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_2 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_2_POD_2_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_2_POD_2_ZN_1_FLR_2 | 99 | 1 | Yes | VAV_POD_2 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_2_POD_2_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_2_POD_2_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_2 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_2_POD_2_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_2_POD_2_ZN_1_FLR_2 | 477 | 1 | Yes | VAV_POD_2 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_1_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_1_POD_3_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_3 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_1_POD_3_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_1_POD_3_ZN_1_FLR_2 | 99 | 1 | Yes | VAV_POD_3 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_1_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_1_POD_3_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_3 | 212 | 74.2 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_1_POD_3_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_1_POD_3_ZN_1_FLR_2 | 477 | 1 | Yes | VAV_POD_3 | 212 | 74.2 | 15.0695 | 2.65 | 20 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORRIDOR_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORRIDOR_POD_3_ZN_1_FLR_1 | 320 | 1 | Yes | VAV_POD_3 | 20 | 7 | 5.5178 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORRIDOR_POD_3_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORRIDOR_POD_3_ZN_1_FLR_2 | 320 | 1 | Yes | VAV_POD_3 | 20 | 7 | 5.5178 | 18.58 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_2_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_2_POD_3_ZN_1_FLR_1 | 99 | 1 | Yes | VAV_POD_3 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCORNER_CLASS_2_POD_3_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | CORNER_CLASS_2_POD_3_ZN_1_FLR_2 | 99 | 1 | Yes | VAV_POD_3 | 80 | 28 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_2_POD_3_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_2_POD_3_ZN_1_FLR_1 | 477 | 1 | Yes | VAV_POD_3 | 212 | 74.19 | 15.0695 | 2.65 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMULT_CLASS_2_POD_3_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | MULT_CLASS_2_POD_3_ZN_1_FLR_2 | 477 | 1 | Yes | VAV_POD_3 | 212 | 74.2 | 15.0695 | 2.65 | 20 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryMAIN_CORRIDOR_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | MAIN_CORRIDOR_ZN_1_FLR_1 | 1140 | 1 | Yes | VAV_OTHER | 140 | 49 | 5.5178 | 18.58 | 4 | 0 | 0 | 0 | 0.0010252 | 0 | 0
SchoolSecondaryMAIN_CORRIDOR_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | MAIN_CORRIDOR_ZN_1_FLR_2 | 1140 | 1 | Yes | VAV_OTHER | 140 | 49 | 5.5178 | 18.58 | 4 | 0 | 0 | 0 | 0.0010252 | 0 | 0
SchoolSecondaryLOBBY_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | LOBBY_ZN_1_FLR_1 | 210 | 1 | Yes | VAV_OTHER | 60 | 21 | 13.9931 | 9.29 | 4 | 0 | 0 |  | 0.0010252 | 0 | 7.1552
SchoolSecondaryLOBBY_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | LOBBY_ZN_1_FLR_2 | 210 | 1 | Yes | VAV_OTHER | 60 | 21 | 13.9931 | 9.29 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryBATHROOMS_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | BATHROOMS_ZN_1_FLR_1 | 210 | 1 | Yes | VAV_OTHER | 72 | 25.2 | 9.6875 | 18.58 | 4 | 0 | 0 | 0.28 | 0.0010252 | 0 | 0
SchoolSecondaryBATHROOMS_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | BATHROOMS_ZN_1_FLR_2 | 210 | 1 | Yes | VAV_OTHER | 72 | 25.2 | 9.6875 | 18.58 | 4 | 0 | 0 | 0.28 | 0.0010252 | 0 | 0
SchoolSecondaryOFFICES_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | OFFICES_ZN_1_FLR_1 | 532 | 1 | Yes | VAV_OTHER | 208 | 72.8 | 11.8403 | 18.58 | 10.8 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryOFFICES_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | OFFICES_ZN_1_FLR_2 | 532 | 1 | Yes | VAV_OTHER | 208 | 72.8 | 11.8403 | 18.58 | 10.8 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryGYM_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | GYM_ZN_1_FLR_1 | 1976 | 1 | Yes | PSZ-AC_1:5 | 0 | 0 | 13.3472 | 3.1 | 5 | 0 | 6.0228 | 0 | 0.0010252 | 0 | 0
SchoolSecondaryAUX_GYM_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | AUX_GYM_ZN_1_FLR_1 | 1248 | 1 | Yes | PSZ-AC_2:6 | 608 | 212.8 | 13.3472 | 3.1 | 5 | 0 | 3.8039 |  | 0.0010252 | 0 | 0
SchoolSecondaryAUDITORIUM_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | AUDITORIUM_ZN_1_FLR_1 | 988 | 1 | Yes | PSZ-AC_3:7 | 304 | 106.4 | 9.6875 | 0.62 | 5 | 0 | 11.2928 |  | 0.0010252 | 0 | 0
SchoolSecondaryKITCHEN_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | KITCHEN_ZN_1_FLR_1 | 216 | 1 | Yes | PSZ-AC_4:8 | 36 | 12.6 | 12.9167 | 4.64 | 1909.5199 | 362577.6 | 0.6848 | 2.83 | 0.0010252 | 0 | 0
SchoolSecondaryLIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | LIBRARY_MEDIA_CENTER_ZN_1_FLR_2 | 840 | 1 | Yes | VAV_OTHER | 236 | 82.6 | 16.684 | 9.29 | 10 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryCAFETERIA_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | CAFETERIA_ZN_1_FLR_1 | 624 | 1 | Yes | PSZ-AC_5:9 | 200 | 70 | 9.6875 | 0.93 | 76.93 | 0 | 6.3398 |  | 0.0010252 | 0 | 0
SchoolSecondaryMECH_ZN_1_FLR_1 | STD2004 | Buffalo | SchoolSecondary | MECH_ZN_1_FLR_1 | 342 | 1 | Yes | VAV_OTHER | 0 | 0 | 16.1458 | 61.6 | 71.2028 | 0 | 0 |  | 0 | 0 | 0
SchoolSecondaryMECH_ZN_1_FLR_2 | STD2004 | Buffalo | SchoolSecondary | MECH_ZN_1_FLR_2 | 342 | 1 | Yes | VAV_OTHER | 0 | 0 | 16.1458 | 61.6 | 4 | 0 | 0 |  | 0.0010252 | 0 | 0
SchoolSecondaryTotal | STD2004 | Buffalo | SchoolSecondary | Total | 19592 |  |  |  | 5968 | 2088.8 | 12.0649 | 3.06 | 31.9493 | 0 |  |  | 0 | 0 | 0
SchoolSecondaryConditioned Total | STD2004 | Buffalo | SchoolSecondary | Conditioned Total | 19592 |  |  |  | 5968 | 2088.8 | 12.0649 | 3.06 | 31.9493 | 0 |  |  | 0 | 0 | 0
SchoolSecondaryUnconditioned Total | STD2004 | Buffalo | SchoolSecondary | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
SchoolSecondaryNot Part of Total | STD2004 | Buffalo | SchoolSecondary | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
WarehouseZONE1 OFFICE | STD2004 | Buffalo | Warehouse | ZONE1 OFFICE | 236.88 | 1 | Yes | PSZ-OFFICE | 149.56 | 17.66 | 10.7186 | 18.58 | 8.0737 | 0 | 0.1203 |  | 0.0010252 | 0 | 0.28883
WarehouseZONE2 FINE STORAGE | STD2004 | Buffalo | Warehouse | ZONE2 FINE STORAGE | 1393.41 | 1 | Yes | PSZ-FINE STORAGE | 760.8 | 0 | 15.0695 | 46.45 | 0 | 0 | 0.3539 |  | 0.0010252 | 0 | 0
WarehouseZONE3 BULK STORAGE | STD2004 | Buffalo | Warehouse | ZONE3 BULK STORAGE | 3204.84 | 1 | Yes | Zone3 Bulk Storage Unit Heater | 1586.63 | 0 | 9.6875 | 46.45 | 2.5587 | 0 |  |  | 0.0021635 | 0 | 0
WarehouseTotal | STD2004 | Buffalo | Warehouse | Total | 4835.13 |  |  |  | 2496.99 | 17.66 | 11.289 | 43.27 | 2.0915 | 0 |  |  | 0 | 0 | 0
WarehouseConditioned Total | STD2004 | Buffalo | Warehouse | Conditioned Total | 4835.13 |  |  |  | 2496.99 | 17.66 | 11.289 | 43.27 | 2.0915 | 0 |  |  | 0 | 0 | 0
WarehouseUnconditioned Total | STD2004 | Buffalo | Warehouse | Unconditioned Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0
WarehouseNot Part of Total | STD2004 | Buffalo | Warehouse | Not Part of Total | 0 |  |  |  | 0 | 0 |  |  |  | 0 |  |  | 0 | 0 | 0